## Informe FP 15 min Abr-2009
RESUMEN FACTOR DE POTENCIA ARTÍCULO 6-17 NORMA TÉCNICA MES DE ABRIL DE 2009
|  |  |  | INDUCTIVO | [5 empty] | CAPACITIVO | [5 empty] | Carga de Datos
Empresa | Clave | Retiro | Tensión | Máximo | Mínimo | Permitido | Intervalos Fuera de | Total de | Fuera de | Máximo | Mínimo | Permitido | Intervalos Fuera de | Total de | Fuera de | Fecha | Hora
|  |  | Nominal |  |  |  | Rango | Intervalos | Rango |  |  |  | Rango | Intervalos | Rango
|  |  | [kV] | [p.u.] | [p.u.] | [p.u.] |  |  | [%] | [p.u.] | [p.u.] | [p.u.] |  |  | [%]
C. MIN. C. DE ANDACOLLO | RET001L059SE001L059 | MIN. C. DE ANDACOLLO - S/E Minera Carmen de Andacollo | 110 | 0.97 | 0.66 | 0.98 | 2875 | 2875 | 100% | 0 | 0 | 1 | 0 | 0 | 0% | 2012-01-19 | 14:35
C. MIN. C. DE ANDACOLLO | RET002L059SE001L059 | S/E Minera Carmen de Andacollo 220 kV | 220
C. Min. Cerro Negro | RET001L072SE001L072 | S/E Los Angeles | 44
C. MIN. DEL PACIFICO | RET001L018SE004L018 | Algarrobo - S/E Algarrobo | 110 | 1 | 0.51 | 0.98 | 1520 | 2852 | 53% | 1 | 0.99 | 1 | 4 | 28 | 0% | 2009-05-29 | 13:37
C. MIN. DEL PACIFICO | RET001L018SE007L018 | CMP - S/E Magnetita | 110 | 1 | 0.94 | 0.98 | 44 | 1192 | 2% | 1 | 0.42 | 1 | 628 | 1688 | 22% | 2009-05-29 | 13:37
C. MIN. DEL PACIFICO | RET004L018SE001L018 | Los Colorados - S/E Los Colorados | 110 | 1 | 0.89 | 0.98 | 412 | 2016 | 14% | 1 | 0.35 | 1 | 660 | 864 | 23% | 2009-05-29 | 13:37
C. MIN. DEL PACIFICO | RET002L018SE002L018 | Pellets - S/E Pellets | 110 | 1 | 0.97 | 0.98 | 4 | 2880 | 0% | 0 | 0 | 1 | 0 | 0 | 0% | 2009-05-29 | 13:37
C. MIN. DEL PACIFICO | RET003L018SE006L018 | Romeral - S/E Romeral | 110 | 1 | 0.85 | 0.98 | 192 | 2840 | 7% | 1 | 0.97 | 1 | 16 | 28 | 1% | 2009-05-29 | 13:37
C. MIN. DOS AMIGOS (CEMIN) | RET001L023SE015T002 | CEMIN - S/E Dos Amigos | 23
C. MIN. LA CANDELARIA | RET001L057SE001L057 | MIN. LA CANDELARIA - S/E Candelaria | 220 | 1 | 0.96 | 0.98 | 182 | 2879 | 6% | 0 | 0 | 1 | 0 | 0 | 0% | 2009-09-08 | 12:25
C. MIN. MANTOS DE ORO | RET001L053SE001L053 | MIN. MANTOS DE ORO - S/E La Coipa | 220
C. MIN. OJOS DEL SALADO | RET001L052SE001L057 | MIN. OJOS DEL SALADO - S/E Candelaria | 23
C. MIN. PELAMBRES | RET001L051SE025T002 | MIN. PELAMBRES-L.Vilos - S/E Los Vilos | 220 | 1 | 0.01 | 0.98 | 720 | 2817 | 26% | 0 | 0 | 1 | 0 | 0 | 0% | 2009-09-03 | 16:49
C. MIN. PELAMBRES | RET001L051SE001L051 | MIN. PELAMBRES-Quillota - S/E Quillota | 220 | 1 | 0.31 | 0.98 | 472 | 2880 | 16% | 0 | 0 | 1 | 0 | 0 | 0% | 2012-01-18 | 15:41
C. MIN. REFUGIO | RET001L050SE001L050 | MIN. MARICUNGA - S/E Cardones | 110 | 1 | 0.93 | 0.98 | 2080 | 2880 | 72% | 0 | 0 | 1 | 0 | 0 | 0% | 2012-03-12 | 16:08
C. MIN. VALLE CENTRAL | RET001L049SE002L049 | MIN. VALLE CENTRAL - S/E Minera Valle Central | 154 | 1 | 0.61 | 0.98 | 1298 | 2879 | 45% | 0.97 | 0.97 | 1 | 1 | 1 | 0% | 2012-03-02 | 11:50
CAP | RET001L029SE001L029 | CAP Huachipato - S/E San Vicente | 154 | 1 | 0.98 | 0.98 | 0 | 2572 | 0% | 1 | 1 | 1 | 0 | 308 | 0% | 2012-01-20 | 18:52
CAP | RET001L028SE001L028 | CAP Rengo - S/E Indac | 154 | 1 | 0.98 | 0.98 | 0 | 651 | 0% | 1 | 1 | 1 | 0 | 2229 | 0% | 2012-01-20 | 18:52
CELULOSA ARAUCO | RET001G026SE001G002 | Arauco- Arauco - S/E Horcones | 66 | 1 | 0.01 | 0.96 | 302 | 548 | 22% | 1 | 0.01 | 0.98 | 533 | 833 | 39% | 2012-01-23 | 19:08
CELULOSA ARAUCO | RET001G026SE001G026 | Arauco- Constitución - S/E Constitución | 66 | 1 | 0.78 | 0.96 | 71 | 413 | 12% | 1 | 0.06 | 0.98 | 90 | 156 | 16% | 2012-01-23 | 19:08
CELULOSA ARAUCO | RET001G026SE004G026 | Arauco- Itata - S/E Santa Elvira | 66 | 0 | 0 | 0.96 | 0 | 0 | 0% | 0 | 0 | 0.98 | 0 | 0 | 0% | 2012-01-23 | 19:08
CELULOSA ARAUCO | RET001G026SE018R017 | Arauco- Licantén - S/E Licantén | 66 | 0.32 | 0.32 | 0.96 | 1 | 1 | 3% | 1 | 0.18 | 0.98 | 35 | 39 | 88% | 2012-01-23 | 19:08
CELULOSA ARAUCO | RET001G026SE003G026 | Arauco- Valdivia - S/E Los Ciruelos | 220 | 1 | 0.03 | 0.98 | 705 | 726 | 92% | 1 | 0.08 | 1 | 36 | 37 | 5% | 2012-01-23 | 19:08
CELULOSA ARAUCO | RET001L046SE007R017 | Aserraderos Arauco - S/E Constitución | 23 | 0.99 | 0.86 | 0.93 | 518 | 2876 | 18% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-01-23 | 19:08
CELULOSA ARAUCO | RET001G024SE001G002 | PANELES ARAUCO - S/E Cholguan | 66 | 0.99 | 0.26 | 0.96 | 14 | 33 | 34% | 0.92 | 0.37 | 0.98 | 8 | 8 | 20% | 2012-01-23 | 19:08
CELULOSA ARAUCO | RET001G024SE004G026 | PANELES ARAUCO - S/E Nueva Aldea | 66 | 0 | 0 | 0.96 | 0 | 0 | 0% | 0 | 0 | 0.98 | 0 | 0 | 0% | 2012-03-23 | 17:21
CEM. BIO BIO | RET001L024SE001L024 | CEMENTO BIO BIO - S/E Cementos Bío Bío | 66 | 1 | 0.8 | 0.96 | 275 | 2395 | 10% | 1 | 0.68 | 0.98 | 110 | 485 | 4% | 2009-05-05 | 11:06
CEM. MELON | RET001L026SE001L026 | CEMENTO MELON - S/E Calera Centro 6 | 62.5 | 1 | 0.96 | 0.96 | 0 | 2331 | 0% | 1 | 0.44 | 0.98 | 51 | 549 | 2% | 2012-01-17 | 18:54
CEM. POLPAICO | RET001L025SE001L025 | CEMENTO POLPAICO - S/E Polpaico | 110
Chilquinta | RET001R003SE007R003 | Concón | 12 | 1 | 0.93 | 0.93 | 0 | 2880 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-05-06 | 16:16
Chilquinta | RET001R003SE010R003 | La Calera | 12 | 1 | 0.95 | 0.93 | 0 | 2786 | 0% | 1 | 1 | 0.96 | 0 | 94 | 0% | 2009-05-06 | 16:16
Chilquinta | RET001R003SE021R003 | Las Vegas | 12 | 1 | 0.95 | 0.93 | 0 | 2004 | 0% | 1 | 0.77 | 0.96 | 126 | 876 | 4% | 2009-05-06 | 16:16
Chilquinta | PA02G010SE007G010 | Linea San Pedro | 110 | 1 | 0.01 | 0.98 | 1605 | 1751 | 81% | 1 | 0.02 | 1 | 199 | 238 | 10% | 2009-05-06 | 16:16
Chilquinta | RET001R017SE002R017 | Melipilla | 110 | 1 | 0.94 | 0.98 | 459 | 1349 | 16% | 1 | 0.97 | 1 | 389 | 1531 | 14% | 2009-05-06 | 16:16
Chilquinta | PA03R003SE003R003 | Melipilla Chilquinta | 12 | 1 | 0.97 | 0.93 | 0 | 731 | 0% | 1 | 0.35 | 0.96 | 1 | 2142 | 0% | 2009-05-06 | 16:16
Chilquinta | RET001R003SE013R003 | Miraflores | 12 | 1 | 0.52 | 0.93 | 6 | 106 | 0% | 1 | 0.01 | 0.96 | 242 | 1139 | 19% | 2009-05-06 | 16:16
Chilquinta | RET001R003SE046R003 | Quintero | 12 | 0 | 0 | 0.93 | 0 | 0 | 0% | 0.99 | 0.92 | 0.96 | 247 | 2877 | 9% | 2009-05-06 | 16:16
Chilquinta | RET001R003SE020R003 | San Felipe | 12 | 1 | 0.91 | 0.93 | 21 | 2667 | 1% | 1 | 0.99 | 0.96 | 0 | 213 | 0% | 2009-05-06 | 16:16
Chilquinta | BA01T001SE021R003 | San Luis | 220 | 1 | 0.87 | 0.98 | 103 | 1482 | 4% | 1 | 0.13 | 1 | 699 | 1398 | 24% | 2009-05-06 | 16:16
Chilquinta | RET001R003SE007G010 | San Pedro | 12 | 1 | 0.85 | 0.93 | 1179 | 2880 | 41% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-05-06 | 16:16
Chilquinta | PA05G010SE007G010 | San Pedro - Miraflores - San Luis | 110 | 1 | 0.96 | 0.98 | 219 | 2195 | 8% | 1 | 0.83 | 1 | 208 | 685 | 7% | 2009-05-06 | 16:16
Chilquinta | RET001R003SE022R003 | San Rafael | 12 | 1 | 0.95 | 0.93 | 0 | 2366 | 0% | 1 | 0.96 | 0.96 | 0 | 514 | 0% | 2009-05-06 | 16:16
Chilectra | RET001R002SE001R002 | Alonso de Córdova B1 | 12 | 1 | 0.98 | 0.93 | 0 | 1553 | 0% | 1 | 0.93 | 0.96 | 29 | 1327 | 1% | 2012-02-28 | 10:58
Chilectra | RET003R002SE001R002 | Alonso de Córdova B2 | 12 | 1 | 0.98 | 0.93 | 0 | 912 | 0% | 1 | 0.89 | 0.96 | 223 | 1968 | 8% | 2012-02-28 | 10:58
Chilectra | RET004R002SE001R002 | Alonso de Córdova B3 | 12 | 1 | 0.96 | 0.93 | 0 | 1149 | 0% | 1 | 0.92 | 0.96 | 186 | 1597 | 7% | 2012-02-28 | 10:58
Chilectra | RET001R002SE002R002 | Altamirano B1 | 12 | 1 | 0.97 | 0.93 | 0 | 1707 | 0% | 1 | 0.95 | 0.96 | 8 | 1173 | 0% | 2012-02-28 | 10:58
Chilectra | RET003R002SE002R002 | Altamirano B2 | 12 | 1 | 1 | 0.93 | 0 | 210 | 0% | 1 | 0.8 | 0.96 | 204 | 2670 | 7% | 2012-02-28 | 10:58
Chilectra | PA01R002SE002T002 | Alto Jahuel 110 | 110
Chilectra | RET001R002SE015R002 | Alto Jahuel-Buin-Florida 110 | 110 | 1 | 0.56 | 0.98 | 1859 | 2869 | 65% | 1 | 1 | 1 | 0 | 11 | 0% | 2012-02-28 | 10:58
Chilectra | RET001R002SE003R002 | Andes B1 | 12 | 1 | 0.97 | 0.93 | 0 | 417 | 0% | 1 | 0.9 | 0.96 | 141 | 2463 | 5% | 2012-02-28 | 10:58
Chilectra | RET003R002SE003R002 | Andes B2 | 12 | 1 | 0.99 | 0.93 | 0 | 205 | 0% | 1 | 0.64 | 0.96 | 714 | 2675 | 25% | 2012-02-28 | 10:58
Chilectra | RET001R002SE004R002 | Apoquindo B1 | 12 | 1 | 0.98 | 0.93 | 0 | 1153 | 0% | 1 | 0.89 | 0.96 | 162 | 1727 | 6% | 2012-02-28 | 10:58
Chilectra | RET003R002SE004R002 | Apoquindo B2 | 12 | 1 | 0.95 | 0.93 | 0 | 2231 | 0% | 1 | 0.99 | 0.96 | 0 | 649 | 0% | 2012-02-28 | 10:58
Chilectra | RET004R002SE004R002 | Apoquindo B3 | 12
Chilectra | RET001R002SE005R002 | Batuco 23KV B1 | 23 | 1 | 0.93 | 0.93 | 0 | 2863 | 0% | 1 | 0.95 | 0.96 | 1 | 17 | 0% | 2012-02-28 | 10:58
Chilectra | RET003R002SE005R002 | Batuco 23KV B2 | 23 | 1 | 0.96 | 0.93 | 0 | 2874 | 0% | 1 | 1 | 0.96 | 0 | 6 | 0% | 2012-02-28 | 10:58
Chilectra | RET002R002SE005R002 | Batuco 23KV B3 | 23 | 1 | 0.95 | 0.93 | 0 | 2129 | 0% | 1 | 0.96 | 0.96 | 0 | 751 | 0% | 2012-02-28 | 10:58
Chilectra | RET001R002SE085R002 | Bicentenario B1 | 12
Chilectra | RET001R002SE006R002 | Brasil B1 | 12 | 1 | 0.98 | 0.93 | 0 | 1384 | 0% | 1 | 0.97 | 0.96 | 0 | 1496 | 0% | 2012-02-28 | 10:58
Chilectra | RET002R002SE006R002 | Brasil B2 | 12 | 1 | 0.97 | 0.93 | 0 | 360 | 0% | 1 | 0.38 | 0.96 | 1488 | 2520 | 52% | 2012-02-28 | 10:58
Chilectra | RET001R002SE007R002 | Buin | 220 | 1 | 0.78 | 0.98 | 460 | 1568 | 16% | 1 | 0.62 | 1 | 800 | 1290 | 28% | 2012-02-28 | 10:58
Chilectra | BA01R002SE007R002 | Buin 110 | 110
Chilectra | RET001R002SE008R002 | Carrascal B1 | 12 | 1 | 0.97 | 0.93 | 0 | 2505 | 0% | 1 | 0.98 | 0.96 | 0 | 375 | 0% | 2012-02-28 | 10:58
Chilectra | RET003R002SE008R002 | Carrascal B2 | 12 | 1 | 0.96 | 0.93 | 0 | 1182 | 0% | 1 | 0.74 | 0.96 | 510 | 1698 | 18% | 2012-02-28 | 10:58
Chilectra | RET003R002SE008T002 | Cerro Navia | 110
Chilectra | RET002R002SE008T002 | Cerro Navia-Las Vegas | 110 | 1 | 0.01 | 0.98 | 253 | 355 | 20% | 1 | 0.01 | 1 | 827 | 892 | 66% | 2012-02-28 | 10:58
Chilectra | BA01R002SE008T002 | Cerro Navia1 (Hyundai) | 110 | 1 | 0.36 | 0.98 | 1451 | 2600 | 50% | 1 | 0.8 | 1 | 144 | 280 | 5% | 2012-02-28 | 10:58
Chilectra | BA01T002SE008T002 | Cerro Navia2 (Jeumont) | 110 | 1 | 0.06 | 0.98 | 1081 | 2572 | 38% | 1 | 0.91 | 1 | 100 | 268 | 4% | 2012-02-28 | 10:58
Chilectra | BA02T002SE008T002 | Cerro Navia2 (Jeumont) | 110
Chilectra | RET001R002SE009R002 | Chacabuco 23KV B2 | 23 | 1 | 0.97 | 0.93 | 0 | 395 | 0% | 1 | 0.72 | 0.96 | 294 | 2485 | 10% | 2012-02-28 | 10:58
Chilectra | RET003R002SE009R002 | Chacabuco 23KV B3 | 23 | 1 | 0.93 | 0.93 | 0 | 2880 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-02-28 | 10:58
Chilectra | RET004R002SE009R002 | Chacabuco B1 | 12 | 1 | 0.98 | 0.93 | 0 | 2093 | 0% | 1 | 0.99 | 0.96 | 0 | 787 | 0% | 2012-02-28 | 10:58
Chilectra | RET005R002SE009R002 | Chacabuco B4 | 12
Chilectra | RET02R002SE010R002 | Chena 220 | 220
Chilectra | RET001R002SE016R002 | Cisterna B1 | 12 | 1 | 0.96 | 0.93 | 0 | 1093 | 0% | 1 | 0.87 | 0.96 | 38 | 1787 | 1% | 2012-02-28 | 10:58
Chilectra | RET003R002SE016R002 | Cisterna B2 | 12 | 1 | 0.98 | 0.93 | 0 | 2650 | 0% | 1 | 0.98 | 0.96 | 0 | 230 | 0% | 2012-02-28 | 10:58
Chilectra | RET004R002SE016R002 | Cisterna B3 | 12 | 1 | 0.94 | 0.93 | 0 | 1202 | 0% | 1 | 0.92 | 0.96 | 82 | 1678 | 3% | 2012-02-28 | 10:58
Chilectra | RET001R002SE011R002 | Club Hípico B1 | 12 | 1 | 0.96 | 0.93 | 0 | 980 | 0% | 1 | 0.95 | 0.96 | 1 | 1859 | 0% | 2012-02-28 | 10:58
Chilectra | RET002R002SE011R002 | Club Hípico B2 | 12 | 1 | 0.55 | 0.93 | 1 | 1890 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-02-28 | 10:58
Chilectra | RET004R002SE011R002 | Club Hípico B3 | 12 | 1 | 0.94 | 0.93 | 0 | 2722 | 0% | 1 | 0.99 | 0.96 | 0 | 92 | 0% | 2012-02-28 | 10:58
Chilectra | RET005R002SE011R002 | Club Hípico B4 | 12
Chilectra | RET001R002SE012R002 | Curacaví Curacaví | 12 | 1 | 0.97 | 0.93 | 0 | 776 | 0% | 1 | 0.85 | 0.96 | 430 | 2104 | 15% | 2012-02-28 | 10:58
Chilectra | RET003R002SE012R002 | Curacaví Lolenco | 12 | 1 | 0.97 | 0.93 | 0 | 1629 | 0% | 1 | 0.97 | 0.96 | 0 | 1251 | 0% | 2012-02-28 | 10:58
Chilectra | RET003R002SE013R002 | El Manzano B3 | 23
Chilectra | RET004R002SE013R002 | El Manzano B4 | 23 | 0.98 | 0.3 | 0.93 | 976 | 2880 | 34% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-02-28 | 10:58
Chilectra | RET001R002SE002T002 | Integrado Alto Jahuel | 110
Chilectra | RET001R002SE008T002 | Integrado Cerro Navia | 110
Chilectra | RET001R002SE017R002 | La Dehesa B1 | 12 | 1 | 0.98 | 0.93 | 0 | 2566 | 0% | 1 | 1 | 0.96 | 0 | 314 | 0% | 2012-02-28 | 10:58
Chilectra | RET002R002SE017R002 | La Dehesa B2 | 12 | 1 | 0.93 | 0.93 | 0 | 2880 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-02-28 | 10:58
Chilectra | RET003R002SE017R002 | La Dehesa B3 | 12 | 1 | 0.96 | 0.93 | 0 | 2873 | 0% | 1 | 1 | 0.96 | 0 | 7 | 0% | 2012-02-28 | 10:58
Chilectra | RET001R002SE018R002 | La Pintana B1 | 12 | 1 | 0.95 | 0.93 | 0 | 2836 | 0% | 1 | 1 | 0.96 | 0 | 44 | 0% | 2012-02-28 | 10:58
Chilectra | RET003R002SE018R002 | La Pintana B2 | 12 | 0.98 | 0.87 | 0.93 | 1240 | 2880 | 43% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-02-28 | 10:58
Chilectra | RET001R002SE019R002 | La Reina B1 | 12 | 1 | 0.91 | 0.93 | 1 | 1588 | 0% | 1 | 0.7 | 0.96 | 25 | 1292 | 1% | 2012-02-28 | 10:58
Chilectra | RET002R002SE019R002 | La Reina B2 | 12 | 1 | 0.96 | 0.93 | 0 | 1466 | 0% | 1 | 0.97 | 0.96 | 0 | 1374 | 0% | 2012-02-28 | 10:58
Chilectra | RET004R002SE019R002 | La Reina B3 | 12
Chilectra | RET003R002SE019R002 | La Reina B4 | 12 | 1 | 1 | 0.93 | 0 | 252 | 0% | 1 | 0.86 | 0.96 | 255 | 2628 | 9% | 2012-02-28 | 10:58
Chilectra | RET003R002SE020R002 | Lampa | 220
Chilectra | RET002R002SE020R002 | Lampa 23KV | 23 | 1 | 0.98 | 0.93 | 0 | 368 | 0% | 1 | 0.12 | 0.96 | 1897 | 2512 | 66% | 2012-02-28 | 10:58
Chilectra | RET001R002SE020R002 | Lampa 23KV | 23 | 1 | 0.93 | 0.93 | 0 | 702 | 0% | 1 | 0.01 | 0.96 | 1926 | 2152 | 67% | 2012-02-28 | 10:58
Chilectra | RET001R002SE021R002 | Las Acacias 23KV B1 | 23 | 1 | 0.96 | 0.93 | 0 | 2269 | 0% | 1 | 0.92 | 0.96 | 39 | 611 | 1% | 2012-02-28 | 10:58
Chilectra | RET003R002SE021R002 | Las Acacias B2 | 23 | 1 | 0.42 | 0.93 | 929 | 2200 | 33% | 1 | 0.28 | 0.96 | 321 | 645 | 11% | 2012-02-28 | 10:58
Chilectra | RET001R002SE022R002 | Lo Aguirre B1 | 110 | 0.99 | 0.85 | 0.98 | 2614 | 2880 | 91% | 0 | 0 | 1 | 0 | 0 | 0% | 2012-02-28 | 10:58
Chilectra | RET001R002SE023R002 | Lo Boza B1 | 12 | 1 | 0.98 | 0.93 | 0 | 519 | 0% | 1 | 0.55 | 0.96 | 1314 | 2361 | 46% | 2012-02-28 | 10:58
Chilectra | RET003R002SE023R002 | Lo Boza B2 | 12 | 1 | 0.93 | 0.93 | 0 | 1758 | 0% | 1 | 0.88 | 0.96 | 40 | 1122 | 1% | 2012-02-28 | 10:58
Chilectra | RET004R002SE023R002 | Lo Boza B3 | 12 | 1 | 0.96 | 0.93 | 0 | 1149 | 0% | 1 | 0.92 | 0.96 | 201 | 1597 | 7% | 2012-02-28 | 10:58
Chilectra | RET005R002SE023R002 | Lo Boza B4 | 12 | 1 | 0.99 | 0.93 | 0 | 1351 | 0% | 1 | 0.96 | 0.96 | 0 | 1529 | 0% | 2012-02-28 | 10:58
Chilectra | RET001R002SE026R002 | Lo Valledor B1 | 12 | 1 | 0.96 | 0.93 | 0 | 873 | 0% | 1 | 0.89 | 0.96 | 96 | 2005 | 3% | 2012-02-28 | 10:58
Chilectra | RET003R002SE026R002 | Lo Valledor B2 | 12 | 1 | 0.93 | 0.93 | 0 | 2113 | 0% | 1 | 0.96 | 0.96 | 0 | 767 | 0% | 2012-02-28 | 10:58
Chilectra | RET004R002SE026R002 | Lo Valledor B3 | 12 | 1 | 0.95 | 0.93 | 0 | 534 | 0% | 1 | 0.83 | 0.96 | 415 | 2346 | 14% | 2010-05-20 | 10:42
Chilectra | RET001R002SE027R002 | Lord Cochrane B1 | 12 | 1 | 0.98 | 0.93 | 0 | 707 | 0% | 1 | 0.79 | 0.96 | 369 | 2173 | 13% | 2010-05-20 | 10:42
Chilectra | RET003R002SE027R002 | Lord Cochrane B2 | 12 | 1 | 0.97 | 0.93 | 0 | 338 | 0% | 1 | 0.67 | 0.96 | 553 | 2542 | 19% | 2010-05-20 | 10:42
Chilectra | RET001R002SE028R002 | Los Almendros 110 kV | 110 | 1 | 0.79 | 0.98 | 1201 | 2107 | 42% | 1 | 0.82 | 1 | 486 | 773 | 17% | 2012-02-28 | 10:58
Chilectra | RET001R002SE029R002 | Los Domínicos B1 | 12 | 1 | 0.97 | 0.93 | 0 | 2875 | 0% | 1 | 1 | 0.96 | 0 | 5 | 0% | 2010-05-20 | 10:42
Chilectra | RET003R002SE029R002 | Los Domínicos B2 | 12 | 1 | 0.98 | 0.93 | 0 | 1517 | 0% | 1 | 0.99 | 0.96 | 0 | 1363 | 0% | 2010-05-20 | 10:42
Chilectra | RET002R002SE030R002 | Macul 20KV B4 | 20 | 0 | 0 | 0.93 | 0 | 0 | 0% | 0.99 | 0.23 | 0.96 | 1998 | 2880 | 69% | 2010-05-20 | 10:42
Chilectra | RET003R002SE030R002 | Macul B1 | 12
Chilectra | RET004R002SE030R002 | Macul B2 | 12
Chilectra | RET005R002SE030R002 | Macul B3 | 12 | 1 | 0.98 | 0.93 | 0 | 399 | 0% | 1 | 0.87 | 0.96 | 207 | 2481 | 7% | 2010-05-20 | 10:42
Chilectra | RET006R002SE030R002 | Macul TR06 (Metro) | 20 | 0 | 0 | 0.93 | 0 | 0 | 0% | 1 | 0.36 | 0.96 | 1613 | 2880 | 56% | 2012-02-28 | 10:58
Chilectra | RET002R002SE031R002 | Maipú B1 | 12 | 1 | 0.94 | 0.93 | 0 | 1403 | 0% | 1 | 0.94 | 0.96 | 11 | 1477 | 0% | 2010-05-20 | 10:42
Chilectra | RET003R002SE031R002 | Maipú B2 | 12 | 1 | 0.94 | 0.93 | 0 | 2232 | 0% | 1 | 1 | 0.96 | 0 | 37 | 0% | 2010-05-20 | 10:42
Chilectra | RET004R002SE031R002 | Maipú B3 | 12
Chilectra | RET001R002SE032R002 | Malloco 23KV B3 | 23
Chilectra | RET003R002SE032R002 | Malloco B1 | 12
Chilectra | RET004R002SE032R002 | Malloco B2 | 12
Chilectra | RET001L014SE087R002 | Metro-Renca | 110
Chilectra | RET001R002SE033R002 | Ochagavía B1 | 12
Chilectra | RET003R002SE033R002 | Ochagavía B2 | 12
Chilectra | RET001R002SE034R002 | Pajaritos B1 | 12
Chilectra | RET003R002SE034R002 | Pajaritos B2 | 12
Chilectra | RET004R002SE034R002 | Pajaritos B3 | 12
Chilectra | RET001R002SE035R002 | Panamericana B1 | 12
Chilectra | RET003R002SE035R002 | Panamericana B2 | 12
Chilectra | RET002R002SE089R002 | Polpaico | 220
Chilectra | RET003R002SE089R002 | Polpaico 23KV B1 | 23
Chilectra | RET001R002SE036R002 | Pudahuel B1 | 12
Chilectra | RET003R002SE036R002 | Pudahuel B2 | 12
Chilectra | RET002R002SE037R002 | Quilicura B1 | 12
Chilectra | RET003R002SE037R002 | Quilicura B2 | 12
Chilectra | RET004R002SE037R002 | Quilicura B3 | 12
Chilectra | RET005R002SE037R002 | Quilicura B4 | 12
Chilectra | RET001R002SE038R002 | Recoleta B1 | 12
Chilectra | RET003R002SE038R002 | Recoleta B2 | 12
Chilectra | RET004R002SE038R002 | Recoleta B4 | 12
Chilectra | RET001R002SE039R002 | Renca | 110
Chilectra | RET001R002SE088R002 | Rungue 23KV | 23
Chilectra | RET002R002SE040R002 | San Bernardo B1 | 12
Chilectra | RET003R002SE040R002 | San Bernardo B2 | 12
Chilectra | RET004R002SE040R002 | San Bernardo B3 | 12
Chilectra | RET002R002SE041R002 | San Cristóbal B1 | 12
Chilectra | RET003R002SE041R002 | San Cristóbal B2 | 12
Chilectra | RET004R002SE041R002 | San Cristóbal B3 | 12
Chilectra | RET002R002SE042R002 | San Joaquín B1 | 12
Chilectra | RET003R002SE042R002 | San Joaquín B2 | 12
Chilectra | RET004R002SE042R002 | San Joaquín B3 | 12
Chilectra | RET005R002SE042R002 | San Joaquín B4 | 12
Chilectra | RET001R002SE043R002 | San José B1 | 12
Chilectra | RET003R002SE043R002 | San José B2 | 12
Chilectra | RET004R002SE043R002 | San José B3 | 12
Chilectra | RET005R002SE043R002 | San José B4 | 12
Chilectra | RET002R002SE044R002 | San Pablo 23KV B1 | 23
Chilectra | RET003R002SE044R002 | San Pablo 23KV B2 | 23
Chilectra | RET002R002SE045R002 | Santa Elena B1 | 12
Chilectra | RET003R002SE045R002 | Santa Elena B2 | 12
Chilectra | RET004R002SE045R002 | Santa Elena B3 | 12
Chilectra | RET005R002SE045R002 | Santa Elena B4 | 12
Chilectra | RET002R002SE046R002 | Santa Marta 23KV B3 | 23
Chilectra | RET003R002SE046R002 | Santa Marta B1 | 12
Chilectra | RET004R002SE046R002 | Santa Marta B2 | 12
Chilectra | RET001R002SE047R002 | Santa Raquel B1 | 12
Chilectra | RET003R002SE047R002 | Santa Raquel B2 | 12
Chilectra | RET004R002SE047R002 | Santa Raquel B4 | 12
Chilectra | RET005R002SE047R002 | Santa Raquel B5 | 12
Chilectra | RET001R002SE048R002 | Santa Rosa B1 | 12
Chilectra | RET003R002SE048R002 | Santa Rosa B2 | 12
Chilectra | RET004R002SE048R002 | Santa Rosa B3 | 12
Chilectra | RET002R002SE048R002 | Santa Rosa B4 Sur | 12
Chilectra | RET001R002SE013R002 | T1 El Manzano | 23 | 1 | 0.94 | 0.93 | 0 | 1544 | 0% | 1 | 0.7 | 0.96 | 772 | 1293 | 27% | 2012-02-28 | 10:58
Chilectra | RET002R002SE033R002 | T1 Metro - Ochagavia | 12
Chilectra | RET002R002SE013R002 | T2 El Manzano | 23 | 1 | 0.88 | 0.93 | 38 | 1344 | 2% | 1 | 0.01 | 0.96 | 103 | 260 | 6% | 2012-02-28 | 10:58
Chilectra | RET001R002SE049R002 | Vitacura B1 | 12
Chilectra | RET002R002SE049R002 | Vitacura B2 | 12
Chilectra | RET003R002SE049R002 | Vitacura B3 | 12
Chilectra | RET004R002SE049R002 | Vitacura B4 | 12
Chilectra | RET007L021SE038T002 | CMPC Cart- CHUMPULLO - S/E Chumpull | 6 | 1 | 0.9 | 0.93 | 3 | 2880 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-05-26 | 17:47
Chilectra | RET006L021SE003G004 | CMPC Cart- MAULE - S/E Colbún | 220 | 1 | 0.94 | 0.98 | 116 | 1643 | 4% | 1 | 0.24 | 1 | 29 | 1226 | 1% | 2009-05-06 | 18:11
CMPC | RET002L021SE008L021 | CMPC Cel- CELPAC - S/E Charrúa | 220 | 1 | 0.7 | 0.98 | 20 | 2754 | 1% | 1 | 0.98 | 1 | 5 | 130 | 0% | 2009-11-11 | 13:23
CMPC | RET001L021SE005L021 | CMPC Cel- LAJA - S/E Charrúa | 220
CMPC | RET003L021SE002L021 | CMPC Cel- SANTA FE - S/E Charrúa | 220
CMPC | RET001L021SE002G025 | CMPC Maderas Aserradero Bucalemu - S/E Bucalemu | 13 | 1 | 0.87 | 0.93 | 270 | 2874 | 9% | 1 | 0.99 | 0.96 | 0 | 6 | 0% | 2012-01-17 | 15:03
CMPC | RET005L021SE004L021 | CMPC-CORDILLERA - S/E Maipo | 110
CMPC | RET004L021SE007L021 | CMPC-INFORSA - S/E Charrúa | 220
CMPC | RET001L020SE002G013 | CODELCO A-Polpaico - S/E El Llano | 220 | 0 | 0 | 0.98 | 0 | 0 | 0% | 1 | 0.01 | 1 | 2465 | 2745 | 90% | 2009-08-11 | 15:06
CMPC | RET001L020SE003L020 | CODELCO A-Saladillo - S/E Saladillo | 66 | 1 | 0.98 | 0.96 | 0 | 1851 | 0% | 1 | 0.67 | 0.98 | 956 | 1029 | 33% | 2009-08-11 | 15:06
CODELCO | RET001L020SE005L020 | CODELCO Salvador - S/E Diego de Almagro | 110 | 0.97 | 0.92 | 0.98 | 2880 | 2880 | 100% | 0 | 0 | 1 | 0 | 0 | 0% | 2009-05-06 | 9:24
CODELCO | RET001L020SE002L020 | CODELCO T-Candelaria - S/E Candelaria | 220 | 0.96 | 0.78 | 0.98 | 2880 | 2880 | 100% | 0 | 0 | 1 | 0 | 0 | 0% | 2010-11-04 | 13:57
CODELCO | RET001L020SE009L020 | CODELCO Ventanas - S/E Tap Enami | 110 | 1 | 0.89 | 0.98 | 2059 | 2880 | 71% | 0 | 0 | 1 | 0 | 0 | 0% | 2009-08-05 | 23:21
CODELCO | RET001L020SE002G015 | S/E Los Maquis | 220
CODELCO | RET001R019SE058T005 | Lautaro | 13.2 | 1 | 0.85 | 0.93 | 109 | 1427 | 4% | 1 | 0.81 | 0.96 | 275 | 1453 | 10% | 2009-05-07 | 9:09
CODELCO | RET001R004SE129T005 | Loncoche | 13.2 | 1 | 0.71 | 0.93 | 30 | 2272 | 1% | 1 | 0.02 | 0.96 | 169 | 608 | 6% | 2009-05-07 | 9:09
CODINER | RET001R004SE092T005 | Pitrufquén | 13.2 | 0.34 | 0.01 | 0.93 | 566 | 566 | 98% | 0.2 | 0.02 | 0.96 | 12 | 12 | 2% | 2009-05-07 | 9:09
CODINER | RET001R004SE037T002 | Temuco | 23 | 0.97 | 0.01 | 0.93 | 1333 | 1335 | 59% | 0.99 | 0.01 | 0.96 | 923 | 926 | 41% | 2009-05-07 | 9:09
CODINER | RET001R004SE064T005 | Traiguén | 13.2 | 0.88 | 0.88 | 0.93 | 2880 | 2880 | 100% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-05-07 | 9:09
CODINER | RET001R019SE068T005 | Victoria | 13.2 | 1 | 0.01 | 0.93 | 382 | 2058 | 15% | 1 | 0.81 | 0.96 | 136 | 500 | 5% | 2009-05-07 | 9:09
CODINER | RET001R006SE003R019 | Cabrero (SGA) | 13.2 | 1 | 0.95 | 0.93 | 0 | 1736 | 0% | 1 | 0.82 | 0.96 | 484 | 1143 | 17% | 2012-04-23 | 10:38
CODINER | RET001R006SE004T003 | Cholguán (SGA) | 13.2 | 1 | 0.92 | 0.93 | 1 | 2880 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-04-23 | 10:38
COELCHA | RET001R007SE001R007 | Curicó T4 | 13.2 | 1 | 0.97 | 0.93 | 0 | 1795 | 0% | 1 | 0.7 | 0.96 | 575 | 1085 | 20% | 2009-05-11 | 9:33
COELCHA | RET001R007SE126T005 | Quinta | 66 | 1 | 0.01 | 0.93 | 647 | 2165 | 22% | 1 | 0.01 | 0.96 | 339 | 715 | 12% | 2010-05-06 | 16:40
COOP. CURICO (CEC) | RET001R007SE127T005 | Teno | 13.2 | 1 | 0.87 | 0.93 | 106 | 2743 | 4% | 1 | 0.95 | 0.96 | 1 | 137 | 0% | 2012-01-17 | 11:24
COOP. CURICO (CEC) | RET002R011SE076T005 | Canteras | 13.2 | 1 | 0.92 | 0.93 | 15 | 2880 | 1% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-01-20 | 21:47
COOP. CURICO (CEC) | RET004R011SE076T005 | Huaqui | 13.2 | 1 | 0.86 | 0.93 | 3 | 2880 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-01-20 | 21:47
COOPELAN | RET001R019SE076T005 | Los Angeles | 13.2 | 1 | 0.93 | 0.93 | 0 | 2880 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-01-20 | 21:47
COOPELAN | RET003R011SE076T005 | Santa Fe | 13.2 | 1 | 0.92 | 0.93 | 25 | 2880 | 1% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-01-20 | 21:47
COOPELAN | RET001R025SE012T003 | La Unión | 13.2 | 1 | 0.92 | 0.93 | 2 | 2880 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-07-08 | 15:15
COOPELAN | RET001R008SE001G008 | Pilmaiquén | 13.2 | 1 | 0.93 | 0.93 | 0 | 2876 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-07-08 | 15:15
COOPREL | RET002R013SE001R013 | Quilmo 66 KV | 13 | 1 | 0.96 | 0.93 | 0 | 2884 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-02-23 | 16:50
COOPREL | RET001R010SE021T003 | CRELL | 13.2 | 1 | 0.95 | 0.93 | 0 | 2425 | 0% | 1 | 0.99 | 0.96 | 0 | 455 | 0% | 2009-05-13 | 21:08
COPELEC | RET001L054SE001L054 | MANTO VERDE-Almagro - S/E Diego de Almagro | 110
CRELL | RET001L054SE002L054 | MANTO VERDE-Impulsion - S/E Impulsión | 23
Divisiones AngloAmerican | RET001L008SE002L008 | MSA-CHAGRES - S/E Chagres | 110 | 1 | 0.84 | 0.98 | 152 | 2435 | 5% | 1 | 0.94 | 1 | 200 | 541 | 7% | 2009-05-04 | 14:28
Divisiones AngloAmerican | RET001L061SE001L061 | MSA-EL SOLDADO - S/E La Calera | 110
Divisiones AngloAmerican | RET001L022SE004G010 | MSA-LOS BRONCES - S/E Polpaico | 220
Divisiones AngloAmerican | RET001R020SE005R020 | S/E El Totoral | 12
Divisiones AngloAmerican | RET001R020SE004R020 | S/E Tap El Manzano | 12
E. E. LITORAL | PA03R020SE003R020 | San Jerónimo | 66
E. E. LITORAL | RET001R020SE001R020 | SPD Las Balandras | 12
E. E. LITORAL | RET001R020SE002R020 | SPD Las Piñatas | 12
E. E. LITORAL | RET001R020SE003R020 | SPD San Jerónimo | 12
E. E. LITORAL | RET004R026SE018R002 | Pintana T4 | 110
E. E. LITORAL | RET001R026SE003R026 | Vizcachas | 110
E. E. PUENTE ALTO | RET001L015SE001L015 | EKA - S/E San Vicente | 154
E. E. PUENTE ALTO | RET001R001SE001R001 | Diego de Almagro | 110
EKA CHILE | RET001R016SE001R016 | S/E Caldera | 23
ELECDA | RET002R016SE002R016 | S/E Cerrillos | 23
EMELAT | RET001R016SE004R016 | S/E Copiapó | 13.8
EMELAT | RET002R016SE004R016 | S/E Copiapó CT4 | 13.8
EMELAT | RET001R016SE014T002 | S/E Diego De Almagro | 23
EMELAT | RET001R016SE005R016 | S/E Hernán Fuentes | 23
EMELAT | RET001R016SE019T002 | S/E Huasco | 13
EMELAT | RET001R016SE017T005 | S/E Incahuasi | 23
EMELAT | RET001R016SE006R016 | S/E Los Loros | 23
EMELAT | RET001R016SE007R016 | S/E Plantas | 23
EMELAT | RET001R016SE008R016 | S/E Tierra Amarilla | 23
EMELAT | RET002R016SE008R016 | S/E Tierra Amarilla ET2 | 23
EMELAT | RET001R016SE039T002 | Vallenar 13.2 | 13.2
EMELAT | RET001L030SE001L030 | ENAMI - Fundicion Paipote - S/E H. Videla L. | 110
EMELAT | RET001L030SE004G011 | ENAMI - Planta Matta - S/E Pta. Matta | 110
ENAMI - H. V. LIRA | RET001L002SE007R003 | ENAP ACONCAGUA - S/E Miraflores Barra | 110
ENAMI - H. V. LIRA | RET001L034SE001L034 | ENAP BIO BIO - S/E Petrox | 66
ENAP REFINERIAS | RET001L011SE003L011 | EFE - Curicó - S/E Curicó | 66
ENAP REFINERIAS | RET002L011SE007L011 | EFE - Jahuel 66 KV - S/E Jahuel | 66
FFCC | RET003L011SE008L011 | EFE - Laja - S/E Laja | 66
FFCC | RET005L011SE010L011 | EFE - Monte Aguila - S/E Charrua | 66
FFCC | RET006L011SE011L011 | EFE - San Fernando - S/E San Fernando | 66
FFCC | RET001G032SE001G032 | FPC - S/E Fopaco | 154
FFCC | BA01T002SE001G021 | ABANICO | 13.2
Forestal y Papelera Concepción | RET002R019SE028T005 | ANGOL 13.2 | 13.2
frontel | RET001R019SE028T005 | ANGOL 23 | 23 | 0.99 | 0.01 | 0.93 | 575 | 589 | 20% | 0.99 | 0.01 | 0.96 | 1639 | 2290 | 57% | 2010-05-06 | 16:40
frontel | RET001R019SE003R019 | CABRERO | 23
frontel | RET001R019SE033T005 | CARAMPANGUE | 23
frontel | RET001R019SE004T003 | CHOLGUAN | 13.2
frontel | RET001R019SE043T005 | COLLIPULLI | 13.2
frontel | RET001R019SE142T005 | CORONEL | 15
frontel | RET001R019SE013T005 | CURACAUTIN | 13.2
frontel | RET001R019SE036T005 | CURANILAHUE 13.2 | 13.2
frontel | RET002R019SE036T005 | CURANILAHUE 23 | 23
frontel | RET001R019SE004R019 | ENACAR | 13.2
frontel | RET001R019SE022T002 | LAJA | 13.2
frontel | RET001R019SE058T005 | LAUTARO | 13.2 | 1 | 0.85 | 0.93 | 109 | 1427 | 4% | 1 | 0.81 | 0.96 | 275 | 1453 | 10% | 2009-05-07 | 9:09
frontel | RET002R019SE058T005 | LAUTARO 23 | 23
frontel | RET001R019SE011T005 | LEBU | 13.2
frontel | RET002R019SE001R019 | LICANCO | 23
frontel | RET001R019SE076T005 | LOS ANGELES | 13.2 | 1 | 0.93 | 0.93 | 0 | 2880 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-01-20 | 21:47
frontel | RET001R019SE005R019 | LOTA | 13.2
frontel | RET001R019SE002R019 | NEGRETE | 23
frontel | RET001R019SE006R019 | NUEVA IMPERIAL | 23
frontel | RET001R019SE091T005 | PILLANLELBUN | 13.2
frontel | RET001R019SE092T005 | PITRUFQUEN | 13.2
frontel | RET001R019SE064T005 | TRAIGUEN | 13.2
frontel | RET002R019SE065T005 | TRES PINOS 13.2 | 13.2
frontel | RET001R019SE065T005 | TRES PINOS 23 | 23
frontel | RET001R019SE068T005 | VICTORIA | 13.2 | 1 | 0.01 | 0.93 | 382 | 2058 | 15% | 1 | 0.81 | 0.96 | 136 | 500 | 5% | 2009-05-07 | 9:09
frontel | RET001L064SE033T002 | FUNDICION TALLERES-Maestranza - S/E Maestranza | 66
frontel | RET001R017SE001R017 | S/E Alcones | 23
fundtalleres | RET001R017SE002R017 | S/E Bajo Melipilla | 13.2 | 1 | 0.94 | 0.98 | 459 | 1349 | 16% | 1 | 0.97 | 1 | 389 | 1531 | 14% | 2009-05-06 | 16:16
Grupo Emel | RET001R017SE003R017 | S/E Bollenar | 13.2
Grupo Emel | RET001R017SE004R017 | S/E Cauquenes | 13.2
Grupo Emel | RET001R017SE005R017 | S/E Chocalán | 13.2
Grupo Emel | RET001R017SE006R017 | S/E Cocharcas (Emelectric) | 33
Grupo Emel | RET001R017SE007R017 | S/E Constitución | 23
Grupo Emel | RET001R017SE008R017 | S/E El Maitén | 13.2
Grupo Emel | RET001R017SE009R017 | S/E El Monte | 13.2
Grupo Emel | RET001R017SE010R017 | S/E El Paico | 13.2
Grupo Emel | RET001R017SE011R017 | S/E El Peumo | 13.2
Grupo Emel | RET001R017SE012R017 | S/E El Retiro | 13.2
Grupo Emel | RET001R017SE013R017 | S/E Hualañe | 13.2
Grupo Emel | RET001R017SE020T002 | S/E Itahue | 13.2
Grupo Emel | RET001R017SE015R017 | S/E La Esperanza (Emelectric) | 13.2
Grupo Emel | RET001R017SE036R017 | S/E La Manga | 13.2
Grupo Emel | RET001R017SE016R017 | S/E Las Arañas | 13.2
Grupo Emel | RET004R017SE016R017 | S/E Las Arañas 23 | 23
Grupo Emel | RET001R017SE046R017 | S/E Leyda | 13.2
Grupo Emel | RET002R017SE018R017 | S/E Licanten | 13.8
Grupo Emel | RET001R017SE017R017 | S/E Lihueimo | 13.2
Grupo Emel | RET002R017SE017R017 | S/E Lihueimo 2 | 13.2
Grupo Emel | RET001R017SE019R017 | S/E Mandinga | 13.2
Grupo Emel | RET001R017SE020R017 | S/E Marchigüe | 13.2
Grupo Emel | RET001R017SE022R017 | S/E Nancagua | 13.2
Grupo Emel | RET001R017SE023R017 | S/E Paniahue | 13.2
Grupo Emel | RET001R017SE130T005 | S/E Parral | 13.2
Grupo Emel | RET001R017SE025R017 | S/E Parronal | 13.2
Grupo Emel | RET001R017SE026R017 | S/E Placilla | 13.2
Grupo Emel | RET001R017SE039R017 | S/E Quelentaro | 13.2
Grupo Emel | RET001R017SE028R017 | S/E San Carlos | 13.2
Grupo Emel | RET001R017SE029R017 | S/E San Javier | 23
Grupo Emel | RET001R017SE030R017 | S/E Santa Rosa | 23
Grupo Emel | RET001R017SE061T005 | S/E Talca | 15
Grupo Emel | RET001R017SE063T005 | S/E Tomé | 23
Grupo Emel | RET001R017SE031R017 | S/E Villa Prat | 13.2
Grupo Emel | RET001L005SE035T002 | INCHALAM - S/E San Vicente | 13
Grupo Emel | RET001L004SE002L004 | Indura - Graneros | 66
INCHALAM | RET001L004SE001L004 | Indura - Lirquen | 66
INDURA | RET003R021SE001R021 | Barrio Industrial | 13.2
INDURA | RET003R021SE002R021 | Colbún | 13.2
LUZLINARES y LUZPARRAL | RET002R021SE002R021 | Las Cañas | 23
LUZLINARES y LUZPARRAL | RET001R021SE001R021 | Linares Norte | 13.2
LUZLINARES y LUZPARRAL | RET002R021SE001R021 | Linares Sur | 13.2
LUZLINARES y LUZPARRAL | RET001R021SE002R021 | Panimávida | 13.2
LUZLINARES y LUZPARRAL | RET001R024SE011T003 | AIHUAPI | 23
LUZLINARES y LUZPARRAL | RET001R008SE012T003 | LA UNION 13.2 | 13.2
LUZOSORNO | RET002R008SE012T003 | LA UNION 23 | 23
LUZOSORNO | RET001R008SE007T003 | LOS NEGROS | 23
LUZOSORNO | RET001R024SE016T003 | OSORNO | 13.2
LUZOSORNO | RET001R008SE001G008 | PILMAIQUEN | 13.2 | 1 | 0.93 | 0.93 | 0 | 2876 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-07-08 | 15:15
LUZOSORNO | RET001R024SE022T003 | PURRANQUE | 13.2
LUZOSORNO | RET003R022SE130T005 | Bullileo | 13.2
LUZOSORNO | RET001R022SE001R022 | Longaví | 13.2
LUZPARRAL | RET001R017SE012R017 | Retiro | 13.2
LUZPARRAL | RET001R017SE028R017 | San Carlos | 13.2
LUZPARRAL | RET001L044SE001L044 | MASISA-Mapal - S/E Mapal | 154
LUZPARRAL | RET001L044SE003L044 | MASISA-Masonite - S/E FAM | 66
MASISA | RET001L044SE007R019 | MASISA-Masonite - S/E MASISA Cabrero | 13.2
MASISA | RET001L064SE001L064 | FUNDICION TALLERES-Rancagua - S/E Rancagua | 13
MASISA | RET002R002SE033R002 | METRO - S/E Ochagavia | 110
mblancos | RET001L014SE087R002 | METRO - S/E Renca | 110
METRO | RET001L031SE035T002 | MOLY-COP - S/E San Vicente | 13
METRO | RET001L043SE001L043 | OXY - S/E Oxy | 154
MOLY - COP CHILE | RET002L041SE001L041 | PAP. BIO BIO - S/E San Pedro | 66
OXY | RET001L038SE001L038 | PETRODOW - S/E Petrodow | 154
PAP. BIO BIO | RET001L035SE001L035 | PETROQUIM - S/E Petropower | 66
PETRODOW | RET001R024SE011T003 | AIHUAPI | 23
PETROQUIM | RET001R024SE002T003 | ANCUD | 23
SAESA | RET001R024SE027T003 | CALBUCO | 23
SAESA | RET002R024SE005T003 | CHONCHI | 23
SAESA | RET001R024SE006T003 | COLACO | 23
SAESA | RET001R024SE001T003 | CORRAL | 13.2
SAESA | RET003R024SE001G033 | DEGAN | 23
SAESA | RET001R024SE008T003 | EMPALME | 66
SAESA | RET001R024SE010T003 | FRUTILLAR | 13.2
SAESA | RET001R024SE007T003 | L.NEGROS | 23
SAESA | RET002R024SE012T003 | LA UNION 13.2 | 13.2
SAESA | RET001R024SE012T003 | LA UNION 23 | 23
SAESA | RET002R024SE129T005 | LONCOCHE 13.2 | 13.2
SAESA | RET001R024SE129T005 | LONCOCHE 23 | 23
SAESA | RET001R024SE014T003 | LOS LAGOS | 13.2
SAESA | RET001R024SE013T003 | MELIPULLI | 23
SAESA | RET001R024SE016T003 | OSORNO | 23
SAESA | RET002R024SE021T003 | P. VARAS 13.2 | 13.2
SAESA | RET001R024SE021T003 | P. VARAS 23 | 23
SAESA | RET001R024SE017T003 | PANGUIPULLI | 23
SAESA | RET002R024SE018T003 | PICARTE 13.2 | 13.2
SAESA | RET001R024SE018T003 | PICARTE 23 | 23
SAESA | RET002R024SE019T003 | PICHIRROPULLI 13.2 | 13.2
SAESA | RET001R024SE019T003 | PICHIRROPULLI 23 | 23
SAESA | RET001R024SE015T003 | PID PID | 23
SAESA | RET001R024SE001G008 | PILMAIQUEN | 13.2
SAESA | RET001R024SE031T002 | PTO. MONTT | 23
SAESA | RET002R024SE031T002 | PTO. MONTT T44 | 23
SAESA | RET001R024SE022T003 | PURRANQUE | 13.2
SAESA | RET002R024SE022T003 | PURRANQUE 23 kV | 23
SAESA | RET001R024SE026T003 | QUELLON | 23
SAESA | RET001R024SE038T002 | VALDIVIA | 13.2
SAESA | RET002R024SE038T002 | VALDIVIA 23 kV | 23
SAESA | RET001R024SE014T003 | Los Lagos | 13.2
SAESA | RET001R014SE001R014 | Paillaco | 13.2
SOCOEPA | RET002R012SE022T005 | S/E Alameda | 15 | 1 | 0.01 | 0.93 | 687 | 1420 | 24% | 1 | 0.01 | 0.96 | 860 | 1460 | 30% | 2010-05-06 | 16:40
SOCOEPA | RET001R012SE022T005 | S/E Alameda | 15 | 1 | 0.01 | 0.93 | 343 | 479 | 12% | 1 | 0.01 | 0.96 | 1302 | 2401 | 45% | 2010-05-06 | 16:40
TRANSNET | RET002R015SE026T005 | S/E Andacollo | 13.2 | 1 | 0.01 | 0.93 | 118 | 167 | 4% | 1 | 0.01 | 0.96 | 1097 | 2498 | 41% | 2010-05-06 | 16:40
TRANSNET | RET001R015SE026T005 | S/E Andacollo | 66 | 0.95 | 0.01 | 0.96 | 1543 | 1543 | 99% | 1 | 0.13 | 0.98 | 9 | 13 | 1% | 2010-05-06 | 16:40
TRANSNET | RET002R012SE027T005 | S/E Andali | 15 | 1 | 0.01 | 0.93 | 1217 | 2344 | 42% | 0.94 | 0.01 | 0.96 | 536 | 536 | 19% | 2010-05-06 | 16:40
TRANSNET | RET003R012SE027T005 | S/E Andali | 15 | 1 | 0.01 | 0.93 | 883 | 1671 | 31% | 0.99 | 0.01 | 0.96 | 1206 | 1209 | 42% | 2010-05-06 | 16:40
TRANSNET | RET001R019SE028T005 | S/E Angol | 13.2 | 0.99 | 0.01 | 0.93 | 575 | 589 | 20% | 0.99 | 0.01 | 0.96 | 1639 | 2290 | 57% | 2010-05-06 | 16:40
TRANSNET | RET002R012SE030T005 | S/E Buin (C.G.E.) | 15 | 0.99 | 0.01 | 0.93 | 440 | 477 | 15% | 1 | 0.01 | 0.96 | 1439 | 2371 | 51% | 2010-05-06 | 16:40
TRANSNET | RET004R012SE030T005 | S/E Buin (C.G.E.) | 15 | 1 | 0.01 | 0.93 | 394 | 425 | 14% | 1 | 0.01 | 0.96 | 1815 | 2454 | 63% | 2010-05-06 | 16:40
TRANSNET | RET002R015SE031T005 | S/E Cabildo | 23 | 0 | 0 | 0.93 | 0 | 0 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET003R015SE031T005 | S/E Cabildo | 23 | 1 | 0.01 | 0.93 | 345 | 1732 | 12% | 1 | 0.01 | 0.96 | 451 | 1148 | 16% | 2010-05-06 | 16:40
TRANSNET | RET005R012SE032T005 | S/E Cachapoal | 15 | 1 | 0.01 | 0.93 | 592 | 799 | 21% | 1 | 0.01 | 0.96 | 785 | 2081 | 27% | 2010-05-06 | 16:40
TRANSNET | RET002R012SE032T005 | S/E Cachapoal | 15 | 1 | 0.01 | 0.93 | 870 | 1091 | 30% | 1 | 0.01 | 0.96 | 863 | 1789 | 30% | 2010-05-06 | 16:40
TRANSNET | RET003R019SE033T005 | S/E Carampangue | 13.2 | 1 | 0.01 | 0.93 | 983 | 1146 | 61% | 0.82 | 0.02 | 0.96 | 476 | 476 | 29% | 2010-05-06 | 16:40
TRANSNET | RET004R015SE047T005 | S/E Casas Viejas | 13.2 | 1 | 0.01 | 0.93 | 1379 | 1381 | 49% | 0.79 | 0.01 | 0.96 | 1455 | 1455 | 51% | 2010-05-06 | 16:40
TRANSNET | RET001A002SE002A002 | S/E Celulosa Arauco | 66 | 1 | 0.01 | 0.96 | 396 | 583 | 27% | 1 | 0.01 | 0.98 | 678 | 888 | 46% | 2010-05-06 | 16:40
TRANSNET | RET002R005SE100T005 | S/E Chacahu | 13.2 | 1 | 0.01 | 0.93 | 1057 | 1356 | 37% | 1 | 0.01 | 0.96 | 1238 | 1519 | 43% | 2010-05-06 | 16:40
TRANSNET | RET001R005SE100T005 | S/E Chacahu | 13.2 | 0 | 0 | 0.93 | 0 | 0 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET002R012SE035T005 | S/E Chiguayante | 15 | 0.99 | 0.05 | 0.93 | 13 | 57 | 0% | 0.99 | 0.01 | 0.96 | 1822 | 2739 | 65% | 2010-05-06 | 16:40
TRANSNET | RET006R012SE035T005 | S/E Chiguayante | 15 | 1 | 0.01 | 0.93 | 1535 | 1950 | 53% | 1 | 0.01 | 0.96 | 715 | 930 | 25% | 2010-05-06 | 16:40
TRANSNET | RET008R012SE024T005 | S/E Chill | 15 | 1 | 0.01 | 0.93 | 960 | 1839 | 33% | 1 | 0.01 | 0.96 | 956 | 1041 | 33% | 2010-05-06 | 16:40
TRANSNET | RET007R012SE024T005 | S/E Chill | 15 | 1 | 0.01 | 0.93 | 312 | 586 | 11% | 1 | 0.01 | 0.96 | 881 | 2277 | 31% | 2010-05-06 | 16:40
TRANSNET | RET009R012SE037T005 | S/E Chimbarongo | 15 | 1 | 0.01 | 0.93 | 1542 | 1971 | 59% | 0.95 | 0.01 | 0.96 | 642 | 642 | 25% | 2010-05-06 | 16:40
TRANSNET | RET010R012SE038T005 | S/E Chivilc | 15 | 1 | 0.01 | 0.93 | 786 | 1988 | 27% | 1 | 0.01 | 0.96 | 471 | 892 | 16% | 2010-05-06 | 16:40
TRANSNET | RET002R012SE038T005 | S/E Chivilc | 15 | 1 | 0.01 | 0.93 | 172 | 180 | 6% | 1 | 0.01 | 0.96 | 1223 | 2695 | 43% | 2010-05-06 | 16:40
TRANSNET | RET011R012SE040T005 | S/E Chumaquito | 15 | 0 | 0 | 0.93 | 0 | 0 | 0% | 0.8 | 0.01 | 0.96 | 876 | 876 | 100% | 2010-05-06 | 16:40
TRANSNET | RET012R012SE128T005 | S/E Cocharcas (C.G.E) | 15 | 1 | 0.01 | 0.93 | 414 | 442 | 16% | 0.99 | 0.01 | 0.96 | 2111 | 2181 | 80% | 2010-05-06 | 16:40
TRANSNET | RET002R012SE041T005 | S/E Colchagua | 15 | 1 | 0.01 | 0.93 | 1079 | 1647 | 38% | 1 | 0.01 | 0.96 | 617 | 1223 | 21% | 2010-05-06 | 16:40
TRANSNET | RET014R012SE042T005 | S/E Colcura | 13.2 | 1 | 1 | 0.93 | 0 | 26 | 0% | 1 | 0.04 | 0.96 | 2350 | 2854 | 82% | 2010-05-06 | 16:40
TRANSNET | RET006R019SE043T005 | S/E Collipulli | 13.2 | 1 | 0.01 | 0.93 | 1023 | 1233 | 83% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET002R012SE044T005 | S/E Colo Colo | 15 | 1 | 0.01 | 0.93 | 2178 | 2880 | 76% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET015R012SE044T005 | S/E Colo Colo | 15 | 1 | 0.01 | 0.93 | 2371 | 2880 | 82% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET016R012SE013T002 | S/E Coronel | 15 | 1 | 0.01 | 0.93 | 542 | 2865 | 19% | 0.14 | 0.01 | 0.96 | 15 | 15 | 1% | 2010-05-06 | 16:40
TRANSNET | RET007R019SE013T002 | S/E Coronel | 15 | 1 | 0.33 | 0.93 | 4 | 1364 | 0% | 1 | 0.19 | 0.96 | 1016 | 1516 | 35% | 2010-05-06 | 16:40
TRANSNET | RET009R019SE036T005 | S/E Curanilahue | 23 | 1 | 0.01 | 0.93 | 548 | 567 | 25% | 1 | 0.01 | 0.96 | 1419 | 1607 | 65% | 2010-05-06 | 16:40
TRANSNET | RET002R005SE126T005 | S/E Curicó | 13.2 | 1 | 0.01 | 0.93 | 597 | 2531 | 21% | 1 | 0.01 | 0.96 | 303 | 349 | 11% | 2010-05-06 | 16:40
TRANSNET | RET003R005SE126T005 | S/E Curicó | 13.2 | 1 | 0.01 | 0.93 | 597 | 2531 | 21% | 1 | 0.01 | 0.96 | 303 | 349 | 11% | 2010-05-06 | 16:40
TRANSNET | RET001R007SE126T005 | S/E Curicó | 13 | 1 | 0.01 | 0.93 | 647 | 2165 | 22% | 1 | 0.01 | 0.96 | 339 | 715 | 12% | 2010-05-06 | 16:40
TRANSNET | RET002R012SE002T005 | S/E Ejército | 15 | 1 | 0.01 | 0.93 | 1596 | 2880 | 55% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET019R012SE002T005 | S/E Ejército | 15 | 0.98 | 0.01 | 0.93 | 1531 | 2843 | 53% | 0.26 | 0.01 | 0.96 | 37 | 37 | 1% | 2010-05-06 | 16:40
TRANSNET | RET020R012SE003T005 | S/E El Avellano | 23 | 1 | 0.01 | 0.93 | 881 | 1545 | 33% | 0.99 | 0.01 | 0.96 | 1032 | 1106 | 39% | 2010-05-06 | 16:40
TRANSNET | RET022R012SE115T005 | S/E El Manzano (C.G.E.) | 15 | 0.96 | 0.01 | 0.93 | 455 | 1076 | 42% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET006R015SE005T005 | S/E El Peñon | 23 | 0.99 | 0.01 | 0.93 | 1201 | 1463 | 43% | 0.98 | 0.01 | 0.96 | 1243 | 1306 | 45% | 2010-05-06 | 16:40
TRANSNET | RET023R012SE007T005 | S/E Escuadr?n (C.G.E.) | 15 | 1 | 0.01 | 0.93 | 618 | 1593 | 21% | 0.99 | 0.01 | 0.96 | 949 | 1287 | 33% | 2010-05-06 | 16:40
TRANSNET | RET024R012SE023T005 | S/E F?tima | 15 | 0 | 0 | 0.93 | 0 | 0 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET025R012SE012T005 | S/E Graneros | 15 | 1 | 0.01 | 0.93 | 941 | 1142 | 33% | 0.99 | 0.01 | 0.96 | 912 | 1720 | 32% | 2010-05-06 | 16:40
TRANSNET | RET009R015SE001T005 | S/E Guayac | 13.2 | 1 | 0.01 | 0.93 | 1712 | 2607 | 63% | 0.92 | 0.01 | 0.96 | 115 | 115 | 4% | 2010-05-06 | 16:40
TRANSNET | RET010R015SE001T005 | S/E Guayac | 13.2 | 1 | 0.01 | 0.93 | 1047 | 1575 | 49% | 0.65 | 0.01 | 0.96 | 569 | 569 | 27% | 2010-05-06 | 16:40
TRANSNET | RET026R012SE015T005 | S/E Hospital | 15 | 0.95 | 0.66 | 0.93 | 1 | 2 | 0% | 0.98 | 0.01 | 0.96 | 2637 | 2846 | 93% | 2010-05-06 | 16:40
TRANSNET | RET011R015SE016T005 | S/E Illapel | 23 | 0.99 | 0.01 | 0.93 | 2018 | 2490 | 78% | 0.83 | 0.01 | 0.96 | 99 | 99 | 4% | 2010-05-06 | 16:40
TRANSNET | RET003R005SE010T005 | S/E La Palma | 13.2 | 0.99 | 0.01 | 0.93 | 1330 | 2575 | 52% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET023R012SE018T005 | S/E La Ronda | 15 | 1 | 0.01 | 0.93 | 853 | 1799 | 32% | 0.97 | 0.01 | 0.96 | 852 | 858 | 32% | 2010-05-06 | 16:40
TRANSNET | RET028R012SE019T005 | S/E Las Cabras | 15 | 0.78 | 0.01 | 0.93 | 48 | 48 | 2% | 0.99 | 0.01 | 0.96 | 1469 | 2002 | 72% | 2010-05-06 | 16:40
TRANSNET | RET014R015SE020T005 | S/E Las Compa??as | 13.2 | 1 | 0.01 | 0.93 | 777 | 2514 | 30% | 0.99 | 0.01 | 0.96 | 53 | 55 | 2% | 2010-05-06 | 16:40
TRANSNET | RET029R012SE021T005 | S/E Latorre | 15 | 0.99 | 0.01 | 0.93 | 47 | 55 | 2% | 1 | 0.01 | 0.96 | 1467 | 2821 | 51% | 2010-05-06 | 16:40
TRANSNET | RET002R012SE021T005 | S/E Latorre | 15 | 1 | 1 | 0.93 | 0 | 15 | 0% | 0.99 | 0.45 | 0.96 | 2654 | 2865 | 92% | 2010-05-06 | 16:40
TRANSNET | RET030R012SE058T005 | S/E Lautaro | 15 | 1 | 0.01 | 0.93 | 117 | 594 | 4% | 1 | 0.42 | 0.96 | 1988 | 2180 | 72% | 2010-05-06 | 16:40
TRANSNET | RET031R012SE072T005 | S/E Lirqu | 15 | 0.02 | 0.02 | 0.93 | 1 | 1 | 0% | 0.99 | 0.01 | 0.96 | 2074 | 2382 | 87% | 2010-05-06 | 16:40
TRANSNET | RET002R012SE073T005 | S/E Lo Miranda | 15 | 0.95 | 0.2 | 0.93 | 49 | 2583 | 2% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET032R012SE073T005 | S/E Lo Miranda | 15 | 0.95 | 0.92 | 0.93 | 1 | 2041 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET033R012SE074T005 | S/E Loma Colorada | 15 | 0.99 | 0.01 | 0.93 | 585 | 2880 | 20% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET002R004SE129T005 | S/E Loncoche | 13.2 | 0 | 0 | 0.93 | 0 | 0 | 0% | 1 | 0.63 | 0.96 | 1219 | 1293 | 94% | 2010-05-06 | 16:40
TRANSNET | RET016R024SE129T005 | S/E Loncoche | 13.2 | 0 | 0 | 0.93 | 0 | 0 | 0% | 1 | 0.63 | 0.96 | 1219 | 1293 | 94% | 2010-05-06 | 16:40
TRANSNET | RET034R012SE129T005 | S/E Loncoche | 23 | 0 | 0 | 0.93 | 0 | 0 | 0% | 1 | 0.22 | 0.96 | 1335 | 2880 | 46% | 2010-05-06 | 16:40
TRANSNET | RET008R024SE129T005 | S/E Loncoche | 13.2 | 0 | 0 | 0.93 | 0 | 0 | 0% | 1 | 0.63 | 0.96 | 1219 | 1293 | 94% | 2010-05-06 | 16:40
TRANSNET | RET007R024SE129T005 | S/E Loncoche | 13.2 | 0 | 0 | 0.93 | 0 | 0 | 0% | 1 | 0.63 | 0.96 | 1219 | 1293 | 94% | 2010-05-06 | 16:40
TRANSNET | RET035R012SE075T005 | S/E Loreto | 15 | 0.98 | 0.01 | 0.93 | 1041 | 1694 | 50% | 0.96 | 0.01 | 0.96 | 372 | 373 | 18% | 2010-05-06 | 16:40
TRANSNET | RET036R012SE076T005 | S/E Los Angeles | 15 | 0.99 | 0.01 | 0.93 | 15 | 36 | 1% | 0.99 | 0.01 | 0.96 | 1497 | 2844 | 52% | 2010-05-06 | 16:40
TRANSNET | RET001R011SE076T005 | S/E Los Angeles | 13 | 0.99 | 0.01 | 0.93 | 874 | 2863 | 30% | 0.59 | 0.06 | 0.96 | 17 | 17 | 1% | 2010-05-06 | 16:40
TRANSNET | RET037R012SE076T005 | S/E Los Angeles | 13.2 | 0.99 | 0.01 | 0.93 | 874 | 2863 | 30% | 0.59 | 0.06 | 0.96 | 17 | 17 | 1% | 2010-05-06 | 16:40
TRANSNET | RET001L007SE076T005 | S/E Los Angeles | 13 | 0.99 | 0.01 | 0.93 | 874 | 2863 | 30% | 0.59 | 0.06 | 0.96 | 17 | 17 | 1% | 2010-05-06 | 16:40
TRANSNET | RET016R019SE076T005 | S/E Los Angeles | 13.2 | 0.99 | 0.01 | 0.93 | 874 | 2863 | 30% | 0.59 | 0.06 | 0.96 | 17 | 17 | 1% | 2010-05-06 | 16:40
TRANSNET | RET015R015SE025T002 | S/E Los Vilos | 23 | 0.97 | 0.01 | 0.93 | 1087 | 1326 | 82% | 0.02 | 0.02 | 0.96 | 1 | 1 | 0% | 2010-05-06 | 16:40
TRANSNET | RET001R012SE147T005 | S/E Machalí | 15
TRANSNET | RET002R012SE077T005 | S/E Mahns | 15 | 0.98 | 0.01 | 0.93 | 2093 | 2229 | 78% | 0.82 | 0.01 | 0.96 | 438 | 438 | 16% | 2010-05-06 | 16:40
TRANSNET | RET038R012SE077T005 | S/E Mahns | 15 | 1 | 0.01 | 0.93 | 500 | 522 | 19% | 0.95 | 0.01 | 0.96 | 2124 | 2124 | 80% | 2010-05-06 | 16:40
TRANSNET | RET039R012SE078T005 | S/E Malloa | 15 | 1 | 0.01 | 0.93 | 549 | 566 | 27% | 1 | 0.01 | 0.96 | 1414 | 1494 | 69% | 2010-05-06 | 16:40
TRANSNET | RET041R012SE079T005 | S/E Manso de Velasco | 15 | 1 | 0.01 | 0.93 | 88 | 115 | 3% | 1 | 0.01 | 0.96 | 1622 | 2765 | 56% | 2010-05-06 | 16:40
TRANSNET | RET017R015SE080T005 | S/E Marquesa_1 | 23 | 1 | 0.01 | 0.93 | 746 | 1390 | 50% | 1 | 0.02 | 0.96 | 60 | 96 | 4% | 2010-05-06 | 16:40
TRANSNET | RET018R015SE080T005 | S/E Marquesa_2 | 23 | 1 | 0.01 | 0.93 | 785 | 1421 | 53% | 1 | 0.02 | 0.96 | 54 | 74 | 4% | 2010-05-06 | 16:40
TRANSNET | RET019R015SE080T005 | S/E Marquesa_3 | 23 | 1 | 0.01 | 0.93 | 932 | 1725 | 51% | 1 | 0.02 | 0.96 | 72 | 114 | 4% | 2010-05-06 | 16:40
TRANSNET | RET001L059SE001L059 | S/E Minera Carmen de Andacollo | 110 | 0.97 | 0.66 | 0.98 | 2875 | 2875 | 100% | 0 | 0 | 1 | 0 | 0 | 0% | 2012-01-19 | 14:35
TRANSNET | RET002R005SE009T005 | S/E Molina | 13.2 | 1 | 0.01 | 0.93 | 969 | 2880 | 34% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET002R012SE009T005 | S/E Molina | 66 | 1 | 0.01 | 0.96 | 1029 | 2370 | 36% | 1 | 0.01 | 0.98 | 419 | 510 | 15% | 2010-05-06 | 16:40
TRANSNET | RET006R005SE009T005 | S/E Molina | 13.2 | 1 | 0.01 | 0.93 | 23 | 27 | 1% | 1 | 0.01 | 0.96 | 1877 | 2853 | 65% | 2010-05-06 | 16:40
TRANSNET | RET001R009SE082T005 | S/E Monte Patria | 13.2 | 1 | 0.01 | 0.93 | 419 | 484 | 34% | 1 | 0.01 | 0.96 | 719 | 739 | 59% | 2010-05-06 | 16:40
TRANSNET | RET018R015SE082T005 | S/E Monte Patria | 23 | 1 | 0.01 | 0.93 | 880 | 1262 | 44% | 1 | 0.01 | 0.96 | 718 | 722 | 36% | 2010-05-06 | 16:40
TRANSNET | RET005A002SE004A002 | S/E Nueva Aldea | 66 | 0 | 0 | 0.96 | 0 | 0 | 0% | 0 | 0 | 0.98 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET020R015SE071T005 | S/E Ovalle | 23 | 1 | 0.01 | 0.93 | 979 | 2800 | 34% | 0.9 | 0.01 | 0.96 | 76 | 76 | 3% | 2010-05-06 | 16:40
TRANSNET | RET021R015SE071T005 | S/E Ovalle | 13.2 | 1 | 0.01 | 0.93 | 1193 | 2711 | 42% | 0.9 | 0.01 | 0.96 | 118 | 118 | 4% | 2010-05-06 | 16:40
TRANSNET | RET043R012SE084T005 | S/E Padre Las Casas | 15 | 1 | 0.01 | 0.93 | 551 | 609 | 19% | 0.99 | 0.01 | 0.96 | 1029 | 2262 | 36% | 2010-05-06 | 16:40
TRANSNET | RET022R015SE027T002 | S/E Pan de Azúcar | 13.2 | 0.99 | 0.01 | 0.93 | 23 | 2876 | 1% | 0.02 | 0.02 | 0.96 | 1 | 1 | 0% | 2010-05-06 | 16:40
TRANSNET | RET044R012SE086T005 | S/E Panguilemo | 15 | 1 | 0.01 | 0.93 | 1213 | 1692 | 67% | 1 | 0.02 | 0.96 | 87 | 124 | 5% | 2010-05-06 | 16:40
TRANSNET | RET045R012SE087T005 | S/E Pelequ | 15 | 1 | 0.01 | 0.93 | 455 | 1004 | 16% | 1 | 0.01 | 0.96 | 937 | 1844 | 33% | 2010-05-06 | 16:40
TRANSNET | RET046R012SE088T005 | S/E Penco | 15 | 0.98 | 0.01 | 0.93 | 1678 | 1710 | 98% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET047R012SE089T005 | S/E Perales | 15 | 0.99 | 0.01 | 0.93 | 424 | 471 | 15% | 1 | 0.01 | 0.96 | 1938 | 2409 | 67% | 2010-05-06 | 16:40
TRANSNET | RET030R017SE090T005 | S/E Piduco | 15 | 1 | 0.01 | 0.93 | 331 | 1937 | 17% | 0.12 | 0.01 | 0.96 | 36 | 36 | 2% | 2010-05-06 | 16:40
TRANSNET | RET048R012SE090T005 | S/E Piduco | 15 | 0.99 | 0.01 | 0.93 | 176 | 758 | 23% | 0.99 | 0.99 | 0.96 | 0 | 6 | 0% | 2010-05-06 | 16:40
TRANSNET | RET049R012SE091T005 | S/E Pillanlelb?n | 15 | 1 | 0.01 | 0.93 | 674 | 678 | 28% | 0.98 | 0.01 | 0.96 | 1711 | 1746 | 71% | 2010-05-06 | 16:40
TRANSNET | RET050R012SE117T005 | S/E Pirque | 13.2 | 1 | 0.01 | 0.93 | 1911 | 1955 | 72% | 0.66 | 0.01 | 0.96 | 716 | 716 | 27% | 2010-05-06 | 16:40
TRANSNET | RET051R012SE092T005 | S/E Pitrufqu | 13.2 | 1 | 0.01 | 0.93 | 1541 | 1571 | 66% | 0.6 | 0.01 | 0.96 | 751 | 751 | 32% | 2010-05-06 | 16:40
TRANSNET | RET053R012SE083T005 | S/E Pumahue | 15 | 1 | 0.01 | 0.93 | 716 | 1034 | 25% | 1 | 0.01 | 0.96 | 785 | 1846 | 27% | 2010-05-06 | 16:40
TRANSNET | RET002R009SE081T005 | S/E Punitaqui | 13.2 | 0.8 | 0.01 | 0.93 | 223 | 223 | 9% | 0.99 | 0.01 | 0.96 | 2322 | 2339 | 91% | 2010-05-06 | 16:40
TRANSNET | RET024R015SE051T005 | S/E Qu?nquimo | 23 | 1 | 0.01 | 0.93 | 1205 | 2325 | 42% | 0.98 | 0.01 | 0.96 | 553 | 555 | 19% | 2010-05-06 | 16:40
TRANSNET | RET001R012SE154T005 | S/E Quinta de Tilcoco | 15
TRANSNET | RET007R005SE008T005 | S/E Rauqu | 13.2 | 1 | 0.01 | 0.93 | 504 | 1620 | 18% | 1 | 0.01 | 0.96 | 756 | 1260 | 26% | 2010-05-06 | 16:40
TRANSNET | RET056R012SE052T005 | S/E Rengo | 15 | 0.99 | 0.01 | 0.93 | 45 | 46 | 2% | 1 | 0.01 | 0.96 | 866 | 2834 | 30% | 2010-05-06 | 16:40
TRANSNET | RET069R005SE053T005 | S/E Salamanca | 23 | 1 | 0.01 | 0.93 | 698 | 699 | 38% | 0.96 | 0.01 | 0.96 | 1152 | 1153 | 62% | 2010-05-06 | 16:40
TRANSNET | RET002L040SE055T005 | S/E San Francisco de Mostazal | 15 | 1 | 0.21 | 0.93 | 2231 | 2395 | 83% | 1 | 0.12 | 0.96 | 273 | 295 | 10% | 2010-05-06 | 16:40
TRANSNET | RET003L040SE055T005 | S/E San Francisco de Mostazal | 15 | 1 | 0.01 | 0.93 | 46 | 2315 | 2% | 1 | 0.01 | 0.96 | 24 | 459 | 1% | 2010-05-06 | 16:40
TRANSNET | RET001L040SE055T005 | S/E San Francisco de Mostazal | 15 | 1 | 0.01 | 0.93 | 46 | 2315 | 2% | 1 | 0.01 | 0.96 | 24 | 459 | 1% | 2010-05-06 | 16:40
TRANSNET | RET058R012SE055T005 | S/E San Francisco de Mostazal | 15 | 1 | 0.01 | 0.93 | 2869 | 2874 | 100% | 0.2 | 0.04 | 0.96 | 5 | 5 | 0% | 2010-05-06 | 16:40
TRANSNET | RET057R012SE055T005 | S/E San Francisco de Mostazal | 15 | 1 | 0.01 | 0.93 | 1211 | 1840 | 42% | 0.99 | 0.01 | 0.96 | 1032 | 1040 | 36% | 2010-05-06 | 16:40
TRANSNET | RET025R015SE056T005 | S/E San Joaqu?n (C.G.E.) | 13.2 | 1 | 0.01 | 0.93 | 31 | 2877 | 1% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET002R015SE056T005 | S/E San Joaqu?n (C.G.E.) | 13.2 | 1 | 0.01 | 0.93 | 1300 | 2780 | 45% | 0.95 | 0.01 | 0.96 | 97 | 97 | 3% | 2010-05-06 | 16:40
TRANSNET | RET058R012SE057T005 | S/E San Miguel | 15 | 1 | 0.01 | 0.93 | 413 | 441 | 24% | 0.97 | 0.01 | 0.96 | 1246 | 1266 | 73% | 2010-05-06 | 16:40
TRANSNET | RET001L041SE120T005 | S/E San Pedro (C.G.E.) | 15 | 0.99 | 0.01 | 0.93 | 2075 | 2849 | 73% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET060R012SE059T005 | S/E San Vicente de Tagua Tagua | 15 | 1 | 0.01 | 0.93 | 1306 | 1461 | 46% | 0.98 | 0.01 | 0.96 | 1037 | 1379 | 37% | 2010-05-06 | 16:40
TRANSNET | RET002R012SE059T005 | S/E San Vicente de Tagua Tagua | 15 | 1 | 0.01 | 0.93 | 620 | 2349 | 22% | 0.99 | 0.01 | 0.96 | 510 | 517 | 18% | 2010-05-06 | 16:40
TRANSNET | RET002R012SE048T005 | S/E Santa Elvira | 15 | 1 | 0.01 | 0.93 | 925 | 2834 | 33% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET062R012SE061T005 | S/E Talca | 15 | 1 | 0.01 | 0.93 | 2275 | 2880 | 79% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET063R012SE061T005 | S/E Talca | 15 | 0.99 | 0.01 | 0.93 | 1263 | 2880 | 44% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-05-06 | 16:40
TRANSNET | RET063R012SE062T005 | S/E Talcahuano | 15 | 1 | 0.01 | 0.93 | 415 | 1664 | 14% | 1 | 0.01 | 0.96 | 610 | 1216 | 21% | 2010-05-06 | 16:40
TRANSNET | RET002R012SE062T005 | S/E Talcahuano | 15 | 1 | 0.01 | 0.93 | 923 | 995 | 33% | 0.99 | 0.01 | 0.96 | 1700 | 1815 | 60% | 2010-05-06 | 16:40
TRANSNET | RET064R012SE127T005 | S/E Teno | 15 | 1 | 0.01 | 0.93 | 584 | 814 | 20% | 0.99 | 0.01 | 0.96 | 1852 | 2058 | 64% | 2010-05-06 | 16:40