## Informe FP 15 min Oct-2009
RESUMEN FACTOR DE POTENCIA ARTÍCULO 6-17 NORMA TÉCNICA MES DE OCTUBRE DE 2009
|  |  |  | INDUCTIVO | [5 empty] | CAPACITIVO | [5 empty] | Carga de Datos
Empresa | Clave | Retiro | Tensión | Máximo | Mínimo | Permitido | Intervalos Fuera de | Total de | Fuera de | Máximo | Mínimo | Permitido | Intervalos Fuera de | Total de | Fuera de | Fecha | Hora
|  |  | Nominal |  |  |  | Rango | Intervalos | Rango |  |  |  | Rango | Intervalos | Rango
|  |  | [kV] | [p.u.] | [p.u.] | [p.u.] |  |  | [%] | [p.u.] | [p.u.] | [p.u.] |  |  | [%]
C. MIN. C. DE ANDACOLLO | RET001L059SE001L059 | MIN. C. DE ANDACOLLO - S/E Minera Carmen de Andacollo | 110 | 1 | 0.9 | 0.98 | 523 | 2972 | 18% | 0 | 0 | 1 | 0 | 0 | 0% | 2012-01-19 | 14:35
C. MIN. C. DE ANDACOLLO | RET002L059SE001L059 | S/E Minera Carmen de Andacollo 220 kV | 220
C. Min. Cerro Negro | RET001L072SE001L072 | S/E Los Angeles | 44
C. MIN. DEL PACIFICO | RET001L018SE004L018 | Algarrobo - S/E Algarrobo | 110 | 1 | 0.43 | 0.98 | 2564 | 2932 | 87% | 1 | 1 | 1 | 0 | 4 | 0% | 2009-12-16 | 16:29
C. MIN. DEL PACIFICO | RET001L018SE007L018 | CMP - S/E Magnetita | 110 | 1 | 0.96 | 0.98 | 24 | 2528 | 1% | 1 | 1 | 1 | 0 | 444 | 0% | 2009-12-16 | 16:29
C. MIN. DEL PACIFICO | RET004L018SE001L018 | Los Colorados - S/E Los Colorados | 110 | 1 | 0.85 | 0.98 | 1680 | 2300 | 57% | 1 | 0.52 | 1 | 368 | 672 | 12% | 2009-12-16 | 16:29
C. MIN. DEL PACIFICO | RET002L018SE002L018 | Pellets - S/E Pellets | 110 | 1 | 0.98 | 0.98 | 0 | 2972 | 0% | 0 | 0 | 1 | 0 | 0 | 0% | 2009-12-16 | 16:29
C. MIN. DEL PACIFICO | RET003L018SE006L018 | Romeral - S/E Romeral | 110 | 1 | 0.96 | 0.98 | 12 | 2972 | 0% | 0 | 0 | 1 | 0 | 0 | 0% | 2009-12-16 | 16:29
C. MIN. DOS AMIGOS (CEMIN) | RET001L023SE015T002 | CEMIN - S/E Dos Amigos | 23
C. MIN. LA CANDELARIA | RET001L057SE001L057 | MIN. LA CANDELARIA - S/E Candelaria | 220
C. MIN. MANTOS DE ORO | RET001L053SE001L053 | MIN. MANTOS DE ORO - S/E La Coipa | 220
C. MIN. OJOS DEL SALADO | RET001L052SE001L057 | MIN. OJOS DEL SALADO - S/E Candelaria | 23
C. MIN. PELAMBRES | RET001L051SE025T002 | MIN. PELAMBRES-L.Vilos - S/E Los Vilos | 220 | 1 | 0.94 | 0.98 | 138 | 2976 | 5% | 0 | 0 | 1 | 0 | 0 | 0% | 2012-01-18 | 15:24
C. MIN. PELAMBRES | RET001L051SE001L051 | MIN. PELAMBRES-Quillota - S/E Quillota | 220 | 1 | 0.96 | 0.98 | 3 | 2972 | 0% | 0 | 0 | 1 | 0 | 0 | 0% | 2012-01-18 | 15:24
C. MIN. REFUGIO | RET001L050SE001L050 | MIN. MARICUNGA - S/E Cardones | 110 | 1 | 0.01 | 0.98 | 1889 | 2968 | 64% | 0 | 0 | 1 | 0 | 0 | 0% | 2012-03-12 | 16:32
C. MIN. VALLE CENTRAL | RET001L049SE002L049 | MIN. VALLE CENTRAL - S/E Minera Valle Central | 154 | 1 | 0.95 | 0.98 | 2445 | 2972 | 82% | 0 | 0 | 1 | 0 | 0 | 0% | 2012-03-02 | 11:50
CAP | RET001L029SE001L029 | CAP Huachipato - S/E San Vicente | 154 | 1 | 0.98 | 0.98 | 0 | 2700 | 0% | 1 | 1 | 1 | 0 | 276 | 0% | 2012-01-20 | 18:54
CAP | RET001L028SE001L028 | CAP Rengo - S/E Indac | 154 | 1 | 0.98 | 0.98 | 0 | 1999 | 0% | 1 | 1 | 1 | 0 | 977 | 0% | 2012-01-20 | 18:54
CELULOSA ARAUCO | RET001G026SE001G002 | Arauco- Arauco - S/E Horcones | 66 | 1 | 0.15 | 0.96 | 107 | 660 | 4% | 1 | 0.09 | 0.98 | 855 | 2245 | 29% | 2012-03-19 | 14:15
CELULOSA ARAUCO | RET001G026SE001G026 | Arauco- Constitución - S/E Constitución | 66 | 0.99 | 0.02 | 0.96 | 25 | 27 | 83% | 0.3 | 0.09 | 0.98 | 3 | 3 | 10% | 2012-03-19 | 14:15
CELULOSA ARAUCO | RET001G026SE004G026 | Arauco- Itata - S/E Santa Elvira | 66 | 0 | 0 | 0.96 | 0 | 0 | 0% | 0 | 0 | 0.98 | 0 | 0 | 0% | 2012-03-19 | 14:15
CELULOSA ARAUCO | RET001G026SE018R017 | Arauco- Licantén - S/E Licantén | 66 | 0.95 | 0.22 | 0.96 | 11 | 11 | 26% | 0.77 | 0.05 | 0.98 | 32 | 32 | 74% | 2012-03-19 | 14:15
CELULOSA ARAUCO | RET001G026SE003G026 | Arauco- Valdivia - S/E Los Ciruelos | 220 | 0 | 0 | 0.98 | 0 | 0 | 0% | 0.7 | 0.13 | 1 | 9 | 9 | 100% | 2012-03-19 | 14:15
CELULOSA ARAUCO | RET001L046SE007R017 | Aserraderos Arauco - S/E Constitución | 23
CELULOSA ARAUCO | RET001G024SE001G002 | PANELES ARAUCO - S/E Cholguan | 66 | 0.64 | 0.08 | 0.96 | 3 | 3 | 10% | 0.99 | 0.07 | 0.98 | 26 | 27 | 87% | 2012-03-27 | 11:56
CELULOSA ARAUCO | RET001G024SE004G026 | PANELES ARAUCO - S/E Nueva Aldea | 66 | 0.98 | 0.94 | 0.96 | 1 | 28 | 4% | 0 | 0 | 0.98 | 0 | 0 | 0% | 2012-03-27 | 11:56
CEM. BIO BIO | RET001L024SE001L024 | CEMENTO BIO BIO - S/E Cementos Bío Bío | 66 | 1 | 0.9 | 0.96 | 264 | 2796 | 9% | 1 | 0.64 | 0.98 | 97 | 176 | 3% | 2009-11-11 | 11:04
CEM. MELON | RET001L026SE001L026 | CEMENTO MELON - S/E Calera Centro 6 | 62.5 | 1 | 0.65 | 0.96 | 36 | 2167 | 1% | 1 | 0.54 | 0.98 | 316 | 809 | 11% | 2012-01-19 | 17:12
CEM. POLPAICO | RET001L025SE001L025 | CEMENTO POLPAICO - S/E Polpaico | 110
Chilquinta | RET001R003SE007R003 | Concón | 12 | 1 | 0.92 | 0.93 | 3 | 2916 | 0% | 1 | 1 | 0.96 | 0 | 56 | 0% | 2009-11-06 | 14:51
Chilquinta | RET001R003SE010R003 | La Calera | 12 | 1 | 0.95 | 0.93 | 0 | 2861 | 0% | 1 | 1 | 0.96 | 0 | 111 | 0% | 2009-11-06 | 14:51
Chilquinta | RET001R003SE021R003 | Las Vegas | 12 | 1 | 0.97 | 0.93 | 0 | 2810 | 0% | 1 | 1 | 0.96 | 0 | 162 | 0% | 2009-11-06 | 14:51
Chilquinta | PA02G010SE007G010 | Linea San Pedro | 110 | 1 | 0.01 | 0.98 | 1276 | 1792 | 46% | 1 | 0.04 | 1 | 853 | 986 | 31% | 2009-11-06 | 14:51
Chilquinta | RET001R017SE002R017 | Melipilla | 110 | 1 | 0.95 | 0.98 | 416 | 1533 | 14% | 1 | 0.93 | 1 | 850 | 1439 | 29% | 2009-11-06 | 14:51
Chilquinta | PA03R003SE003R003 | Melipilla Chilquinta | 12 | 1 | 0.99 | 0.93 | 0 | 650 | 0% | 1 | 0.94 | 0.96 | 5 | 2322 | 0% | 2009-11-06 | 14:51
Chilquinta | RET001R003SE013R003 | Miraflores | 12 | 1 | 0.02 | 0.93 | 63 | 220 | 4% | 1 | 0.01 | 0.96 | 767 | 1287 | 51% | 2009-11-06 | 14:51
Chilquinta | RET001R003SE046R003 | Quintero | 12 | 0.99 | 0.92 | 0.93 | 57 | 2972 | 2% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-11-06 | 14:51
Chilquinta | RET001R003SE020R003 | San Felipe | 12 | 1 | 0.97 | 0.93 | 0 | 2395 | 0% | 1 | 0.95 | 0.96 | 7 | 577 | 0% | 2009-11-06 | 14:51
Chilquinta | BA01T001SE021R003 | San Luis | 220 | 1 | 0.25 | 0.98 | 68 | 1698 | 2% | 1 | 0.8 | 1 | 367 | 1274 | 12% | 2009-11-06 | 14:51
Chilquinta | RET001R003SE007G010 | San Pedro | 12 | 1 | 0.88 | 0.93 | 866 | 2972 | 29% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-11-06 | 14:51
Chilquinta | PA05G010SE007G010 | San Pedro - Miraflores - San Luis | 110 | 1 | 0.98 | 0.98 | 0 | 1364 | 0% | 1 | 0.93 | 1 | 634 | 1608 | 21% | 2009-11-06 | 14:51
Chilquinta | RET001R003SE022R003 | San Rafael | 12 | 1 | 0.94 | 0.93 | 0 | 2259 | 0% | 1 | 0.97 | 0.96 | 0 | 713 | 0% | 2009-11-06 | 14:51
Chilectra | RET001R002SE001R002 | Alonso de Córdova B1 | 12 | 1 | 0.01 | 0.93 | 424 | 1000 | 14% | 1 | 0.02 | 0.96 | 599 | 1972 | 20% | 2009-11-24 | 9:29
Chilectra | RET003R002SE001R002 | Alonso de Córdova B2 | 12 | 1 | 0.01 | 0.93 | 334 | 611 | 11% | 1 | 0.02 | 0.96 | 663 | 2361 | 22% | 2009-11-24 | 9:29
Chilectra | RET004R002SE001R002 | Alonso de Córdova B3 | 12 | 1 | 0.97 | 0.93 | 0 | 1077 | 0% | 1 | 0.91 | 0.96 | 364 | 1891 | 12% | 2012-02-28 | 10:58
Chilectra | RET001R002SE002R002 | Altamirano B1 | 12 | 1 | 0.01 | 0.93 | 664 | 1729 | 22% | 1 | 0.01 | 0.96 | 623 | 1243 | 21% | 2009-11-24 | 9:29
Chilectra | RET003R002SE002R002 | Altamirano B2 | 12 | 1 | 0.02 | 0.93 | 499 | 855 | 17% | 1 | 0.01 | 0.96 | 593 | 2117 | 20% | 2009-11-24 | 9:29
Chilectra | PA01R002SE002T002 | Alto Jahuel 110 | 110
Chilectra | RET001R002SE015R002 | Alto Jahuel-Buin-Florida 110 | 110 | 1 | 0.91 | 0.98 | 290 | 2877 | 10% | 1 | 0.99 | 1 | 10 | 95 | 0% | 2012-02-28 | 10:58
Chilectra | RET001R002SE003R002 | Andes B1 | 12 | 1 | 0.01 | 0.93 | 349 | 427 | 12% | 1 | 0.01 | 0.96 | 906 | 2545 | 30% | 2009-11-24 | 9:29
Chilectra | RET003R002SE003R002 | Andes B2 | 12 | 1 | 0.01 | 0.93 | 147 | 151 | 5% | 1 | 0.01 | 0.96 | 1453 | 2821 | 49% | 2009-11-24 | 9:29
Chilectra | RET001R002SE004R002 | Apoquindo B1 | 12 | 1 | 0.01 | 0.93 | 458 | 1131 | 15% | 1 | 0.03 | 0.96 | 214 | 1841 | 7% | 2009-11-24 | 9:29
Chilectra | RET003R002SE004R002 | Apoquindo B2 | 12 | 1 | 0.02 | 0.93 | 311 | 2166 | 10% | 1 | 0.02 | 0.96 | 374 | 806 | 13% | 2009-11-24 | 9:29
Chilectra | RET004R002SE004R002 | Apoquindo B3 | 12
Chilectra | RET001R002SE005R002 | Batuco 23KV B1 | 23 | 1 | 0.01 | 0.93 | 7 | 2970 | 0% | 0.98 | 0.03 | 0.96 | 1 | 2 | 0% | 2009-11-24 | 9:29
Chilectra | RET003R002SE005R002 | Batuco 23KV B2 | 23 | 1 | 0.01 | 0.93 | 366 | 2967 | 12% | 0.54 | 0.12 | 0.96 | 5 | 5 | 0% | 2009-11-24 | 9:29
Chilectra | RET002R002SE005R002 | Batuco 23KV B3 | 23 | 1 | 0.01 | 0.93 | 724 | 2350 | 24% | 1 | 0.01 | 0.96 | 493 | 622 | 17% | 2009-11-24 | 9:29
Chilectra | RET001R002SE085R002 | Bicentenario B1 | 12
Chilectra | RET001R002SE006R002 | Brasil B1 | 12 | 1 | 0.02 | 0.93 | 347 | 1833 | 12% | 1 | 0.02 | 0.96 | 507 | 1139 | 17% | 2009-11-24 | 9:29
Chilectra | RET002R002SE006R002 | Brasil B2 | 12 | 0.65 | 0.01 | 0.93 | 108 | 108 | 4% | 1 | 0.01 | 0.96 | 1791 | 2854 | 60% | 2009-11-24 | 9:29
Chilectra | RET001R002SE007R002 | Buin | 220 | 1 | 0.93 | 0.98 | 433 | 2004 | 15% | 1 | 0.89 | 1 | 395 | 932 | 13% | 2012-02-28 | 10:58
Chilectra | BA01R002SE007R002 | Buin 110 | 110
Chilectra | RET001R002SE008R002 | Carrascal B1 | 12 | 1 | 0.01 | 0.93 | 957 | 1294 | 33% | 1 | 0.01 | 0.96 | 891 | 1604 | 31% | 2009-11-24 | 9:29
Chilectra | RET003R002SE008R002 | Carrascal B2 | 12 | 0.99 | 0.01 | 0.93 | 502 | 801 | 17% | 1 | 0.01 | 0.96 | 1264 | 2130 | 43% | 2009-11-24 | 9:29
Chilectra | RET003R002SE008T002 | Cerro Navia | 110
Chilectra | RET002R002SE008T002 | Cerro Navia-Las Vegas | 110 | 0.8 | 0.01 | 0.98 | 52 | 52 | 93% | 0.19 | 0.06 | 1 | 4 | 4 | 7% | 2012-02-28 | 10:58
Chilectra | BA01R002SE008T002 | Cerro Navia1 (Hyundai) | 110 | 1 | 0.96 | 0.98 | 28 | 2142 | 1% | 1 | 0.96 | 1 | 82 | 830 | 3% | 2012-02-28 | 10:58
Chilectra | BA01T002SE008T002 | Cerro Navia2 (Jeumont) | 110 | 1 | 0.95 | 0.98 | 24 | 2383 | 1% | 1 | 0.95 | 1 | 67 | 589 | 2% | 2012-02-28 | 10:58
Chilectra | BA02T002SE008T002 | Cerro Navia2 (Jeumont) | 110
Chilectra | RET001R002SE009R002 | Chacabuco 23KV B2 | 23 | 1 | 0.02 | 0.93 | 102 | 105 | 3% | 1 | 0.01 | 0.96 | 990 | 2867 | 33% | 2009-11-24 | 9:29
Chilectra | RET003R002SE009R002 | Chacabuco 23KV B3 | 23 | 1 | 0.01 | 0.93 | 8 | 2972 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-11-24 | 9:29
Chilectra | RET004R002SE009R002 | Chacabuco B1 | 12 | 1 | 0.02 | 0.93 | 742 | 2265 | 25% | 1 | 0.02 | 0.96 | 560 | 707 | 19% | 2009-11-24 | 9:29
Chilectra | RET005R002SE009R002 | Chacabuco B4 | 12
Chilectra | RET02R002SE010R002 | Chena 220 | 220
Chilectra | RET001R002SE016R002 | Cisterna B1 | 12 | 1 | 0.01 | 0.93 | 503 | 744 | 17% | 1 | 0.01 | 0.96 | 1076 | 2228 | 36% | 2009-11-24 | 9:29
Chilectra | RET003R002SE016R002 | Cisterna B2 | 12 | 1 | 0.01 | 0.93 | 1333 | 2494 | 45% | 1 | 0.01 | 0.96 | 374 | 478 | 13% | 2009-11-24 | 9:29
Chilectra | RET004R002SE016R002 | Cisterna B3 | 12 | 1 | 0.01 | 0.93 | 344 | 956 | 12% | 1 | 0.01 | 0.96 | 778 | 2016 | 26% | 2009-11-24 | 9:29
Chilectra | RET001R002SE011R002 | Club Hípico B1 | 12 | 1 | 0.01 | 0.93 | 351 | 448 | 12% | 1 | 0.01 | 0.96 | 1291 | 2444 | 45% | 2009-11-24 | 9:29
Chilectra | RET002R002SE011R002 | Club Hípico B2 | 12 | 1 | 0.01 | 0.93 | 904 | 2097 | 41% | 0.99 | 0.01 | 0.96 | 108 | 112 | 5% | 2009-11-24 | 9:29
Chilectra | RET004R002SE011R002 | Club Hípico B3 | 12 | 1 | 0.01 | 0.93 | 1048 | 2698 | 36% | 0.8 | 0.01 | 0.96 | 248 | 248 | 8% | 2009-11-24 | 9:29
Chilectra | RET005R002SE011R002 | Club Hípico B4 | 12
Chilectra | RET001R002SE012R002 | Curacaví Curacaví | 12 | 1 | 0.01 | 0.93 | 512 | 519 | 18% | 1 | 0.01 | 0.96 | 1771 | 2307 | 63% | 2009-11-24 | 9:29
Chilectra | RET003R002SE012R002 | Curacaví Lolenco | 12 | 1 | 0.01 | 0.93 | 1558 | 1568 | 58% | 0.97 | 0.01 | 0.96 | 1128 | 1130 | 42% | 2009-11-24 | 9:29
Chilectra | RET003R002SE013R002 | El Manzano B3 | 23
Chilectra | RET004R002SE013R002 | El Manzano B4 | 23 | 1 | 0.36 | 0.93 | 19 | 1508 | 1% | 1 | 0.03 | 0.96 | 34 | 126 | 2% | 2012-02-28 | 10:58
Chilectra | RET001R002SE002T002 | Integrado Alto Jahuel | 110
Chilectra | RET001R002SE008T002 | Integrado Cerro Navia | 110
Chilectra | RET001R002SE017R002 | La Dehesa B1 | 12 | 1 | 0.01 | 0.93 | 1339 | 2185 | 45% | 1 | 0.01 | 0.96 | 779 | 786 | 26% | 2009-11-24 | 9:29
Chilectra | RET002R002SE017R002 | La Dehesa B2 | 12 | 1 | 0.01 | 0.93 | 1941 | 2092 | 93% | 0.01 | 0.01 | 0.96 | 2 | 2 | 0% | 2009-11-24 | 9:29
Chilectra | RET003R002SE017R002 | La Dehesa B3 | 12 | 0.99 | 0.01 | 0.93 | 1719 | 2926 | 59% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-11-24 | 9:29
Chilectra | RET001R002SE018R002 | La Pintana B1 | 12 | 1 | 0.01 | 0.93 | 280 | 2878 | 10% | 0.98 | 0.01 | 0.96 | 38 | 39 | 1% | 2009-11-24 | 9:29
Chilectra | RET003R002SE018R002 | La Pintana B2 | 12 | 1 | 0.01 | 0.93 | 531 | 2424 | 21% | 0.66 | 0.01 | 0.96 | 115 | 115 | 5% | 2009-11-24 | 9:29
Chilectra | RET001R002SE019R002 | La Reina B1 | 12 | 1 | 0.01 | 0.93 | 649 | 811 | 22% | 1 | 0.01 | 0.96 | 1520 | 2153 | 51% | 2009-11-24 | 9:29
Chilectra | RET002R002SE019R002 | La Reina B2 | 12 | 1 | 0.01 | 0.93 | 961 | 1727 | 32% | 1 | 0.01 | 0.96 | 722 | 1245 | 24% | 2009-11-24 | 9:29
Chilectra | RET004R002SE019R002 | La Reina B3 | 12
Chilectra | RET003R002SE019R002 | La Reina B4 | 12 | 1 | 0.02 | 0.93 | 202 | 395 | 7% | 1 | 0.01 | 0.96 | 444 | 2577 | 15% | 2009-11-24 | 9:29
Chilectra | RET003R002SE020R002 | Lampa | 220
Chilectra | RET002R002SE020R002 | Lampa 23KV | 23 | 1 | 0.01 | 0.93 | 741 | 1282 | 25% | 0.99 | 0.01 | 0.96 | 1234 | 1690 | 42% | 2009-11-24 | 9:29
Chilectra | RET001R002SE020R002 | Lampa 23KV | 23 | 1 | 0.03 | 0.93 | 122 | 1438 | 4% | 1 | 0.02 | 0.96 | 537 | 1496 | 18% | 2009-11-24 | 9:29
Chilectra | RET001R002SE021R002 | Las Acacias 23KV B1 | 23 | 1 | 0.01 | 0.93 | 806 | 2254 | 28% | 1 | 0.01 | 0.96 | 423 | 668 | 14% | 2009-11-24 | 9:29
Chilectra | RET003R002SE021R002 | Las Acacias B2 | 23 | 1 | 0.93 | 0.93 | 0 | 2948 | 0% | 0.99 | 0.98 | 0.96 | 0 | 24 | 0% | 2012-02-28 | 10:58
Chilectra | RET001R002SE022R002 | Lo Aguirre B1 | 110 | 0.98 | 0.01 | 0.98 | 2154 | 2159 | 100% | 0 | 0 | 1 | 0 | 0 | 0% | 2009-11-24 | 9:29
Chilectra | RET001R002SE023R002 | Lo Boza B1 | 12 | 1 | 0.01 | 0.93 | 131 | 156 | 4% | 1 | 0.01 | 0.96 | 2093 | 2816 | 70% | 2009-11-24 | 9:29
Chilectra | RET003R002SE023R002 | Lo Boza B2 | 12 | 1 | 0.01 | 0.93 | 811 | 1744 | 27% | 1 | 0.01 | 0.96 | 786 | 1228 | 26% | 2009-11-24 | 9:29
Chilectra | RET004R002SE023R002 | Lo Boza B3 | 12 | 1 | 0.88 | 0.93 | 360 | 2936 | 12% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-02-28 | 10:58
Chilectra | RET005R002SE023R002 | Lo Boza B4 | 12 | 1 | 0.02 | 0.93 | 586 | 2251 | 20% | 1 | 0.02 | 0.96 | 440 | 721 | 15% | 2009-11-24 | 9:29
Chilectra | RET001R002SE026R002 | Lo Valledor B1 | 12 | 1 | 0.01 | 0.93 | 177 | 263 | 6% | 1 | 0.01 | 0.96 | 1005 | 2709 | 34% | 2009-11-24 | 9:29
Chilectra | RET003R002SE026R002 | Lo Valledor B2 | 12 | 1 | 0.01 | 0.93 | 878 | 2166 | 30% | 0.99 | 0.01 | 0.96 | 687 | 746 | 24% | 2009-11-24 | 9:29
Chilectra | RET004R002SE026R002 | Lo Valledor B3 | 12 | 1 | 0.01 | 0.93 | 163 | 481 | 5% | 1 | 0.01 | 0.96 | 1168 | 2491 | 39% | 2009-11-24 | 9:29
Chilectra | RET001R002SE027R002 | Lord Cochrane B1 | 12 | 1 | 0.02 | 0.93 | 296 | 418 | 10% | 1 | 0.01 | 0.96 | 1090 | 2520 | 37% | 2009-11-24 | 9:29
Chilectra | RET003R002SE027R002 | Lord Cochrane B2 | 12 | 1 | 0.02 | 0.93 | 56 | 94 | 2% | 1 | 0.01 | 0.96 | 1252 | 2878 | 42% | 2009-11-24 | 9:29
Chilectra | RET001R002SE028R002 | Los Almendros 110 kV | 110 | 1 | 0.03 | 0.98 | 583 | 1884 | 20% | 1 | 0.93 | 1 | 314 | 980 | 11% | 2012-02-28 | 10:58
Chilectra | RET001R002SE029R002 | Los Domínicos B1 | 12 | 1 | 0.01 | 0.93 | 192 | 2972 | 6% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-11-24 | 9:29
Chilectra | RET003R002SE029R002 | Los Domínicos B2 | 12 | 1 | 0.01 | 0.93 | 701 | 2213 | 24% | 1 | 0.01 | 0.96 | 705 | 759 | 24% | 2009-11-24 | 9:29
Chilectra | RET002R002SE030R002 | Macul 20KV B4 | 20 | 1 | 0.01 | 0.93 | 244 | 462 | 8% | 1 | 0.01 | 0.96 | 458 | 2510 | 15% | 2009-11-24 | 9:29
Chilectra | RET003R002SE030R002 | Macul B1 | 12
Chilectra | RET004R002SE030R002 | Macul B2 | 12
Chilectra | RET005R002SE030R002 | Macul B3 | 12 | 1 | 0.01 | 0.93 | 153 | 416 | 5% | 1 | 0.01 | 0.96 | 792 | 2511 | 27% | 2009-11-24 | 9:29
Chilectra | RET006R002SE030R002 | Macul TR06 (Metro) | 20 | 0 | 0 | 0.93 | 0 | 0 | 0% | 0.99 | 0.29 | 0.96 | 1977 | 2972 | 67% | 2012-02-28 | 10:58
Chilectra | RET002R002SE031R002 | Maipú B1 | 12 | 1 | 0.01 | 0.93 | 821 | 1890 | 28% | 1 | 0.01 | 0.96 | 776 | 1080 | 26% | 2009-11-24 | 9:29
Chilectra | RET003R002SE031R002 | Maipú B2 | 12 | 1 | 0.01 | 0.93 | 270 | 2282 | 12% | 0.99 | 0.01 | 0.96 | 46 | 48 | 2% | 2009-11-24 | 9:29
Chilectra | RET004R002SE031R002 | Maipú B3 | 12 | 1 | 0.01 | 0.93 | 467 | 2369 | 20% | 0.98 | 0.05 | 0.96 | 2 | 15 | 0% | 2009-11-24 | 9:29
Chilectra | RET001R002SE032R002 | Malloco 23KV B3 | 23 | 0.96 | 0.9 | 0.93 | 394 | 2972 | 13% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-11-24 | 9:29
Chilectra | RET003R002SE032R002 | Malloco B1 | 12 | 1 | 0.01 | 0.93 | 1065 | 2147 | 36% | 0.99 | 0.01 | 0.96 | 734 | 825 | 25% | 2009-11-24 | 9:29
Chilectra | RET004R002SE032R002 | Malloco B2 | 12 | 0.99 | 0.01 | 0.93 | 135 | 2949 | 5% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-11-24 | 9:29
Chilectra | RET001L014SE087R002 | Metro-Renca | 110
Chilectra | RET001R002SE033R002 | Ochagavía B1 | 12
Chilectra | RET003R002SE033R002 | Ochagavía B2 | 12 | 1 | 0.01 | 0.93 | 475 | 1470 | 16% | 1 | 0.01 | 0.96 | 364 | 1502 | 12% | 2009-11-24 | 9:29
Chilectra | RET001R002SE034R002 | Pajaritos B1 | 12 | 1 | 0.01 | 0.93 | 337 | 341 | 20% | 1 | 0.01 | 0.96 | 1258 | 1324 | 76% | 2009-11-24 | 9:29
Chilectra | RET003R002SE034R002 | Pajaritos B2 | 12 | 1 | 0.02 | 0.93 | 320 | 2209 | 11% | 1 | 0.02 | 0.96 | 306 | 763 | 10% | 2009-11-24 | 9:29
Chilectra | RET004R002SE034R002 | Pajaritos B3 | 12 | 1 | 0.89 | 0.93 | 381 | 2972 | 13% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-02-28 | 10:58
Chilectra | RET001R002SE035R002 | Panamericana B1 | 12 | 1 | 0.01 | 0.93 | 546 | 1382 | 18% | 1 | 0.01 | 0.96 | 1386 | 1590 | 47% | 2009-11-24 | 9:29
Chilectra | RET003R002SE035R002 | Panamericana B2 | 12 | 1 | 0.01 | 0.93 | 495 | 1408 | 17% | 1 | 0.01 | 0.96 | 826 | 1564 | 28% | 2009-11-24 | 9:29
Chilectra | RET002R002SE089R002 | Polpaico | 220 | 1 | 0.96 | 0.98 | 28 | 1236 | 1% | 1 | 0.83 | 1 | 915 | 1736 | 31% | 2012-02-28 | 10:58
Chilectra | RET003R002SE089R002 | Polpaico 23KV B1 | 23 | 1 | 0.01 | 0.93 | 942 | 1173 | 44% | 0.98 | 0.01 | 0.96 | 944 | 945 | 45% | 2009-11-24 | 9:29
Chilectra | RET001R002SE036R002 | Pudahuel B1 | 12 | 0.99 | 0.01 | 0.93 | 7 | 2972 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-11-24 | 9:29
Chilectra | RET003R002SE036R002 | Pudahuel B2 | 12 | 0.99 | 0.01 | 0.93 | 20 | 2932 | 1% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-11-24 | 9:29
Chilectra | RET002R002SE037R002 | Quilicura B1 | 12
Chilectra | RET003R002SE037R002 | Quilicura B2 | 12 | 1 | 0.01 | 0.93 | 615 | 1578 | 21% | 0.99 | 0.01 | 0.96 | 1242 | 1343 | 43% | 2009-11-24 | 9:29
Chilectra | RET004R002SE037R002 | Quilicura B3 | 12 | 1 | 0.01 | 0.93 | 173 | 485 | 6% | 0.99 | 0.01 | 0.96 | 1720 | 2483 | 58% | 2009-11-24 | 9:29
Chilectra | RET005R002SE037R002 | Quilicura B4 | 12
Chilectra | RET001R002SE038R002 | Recoleta B1 | 12 | 1 | 0.01 | 0.93 | 1068 | 2660 | 36% | 0.99 | 0.01 | 0.96 | 310 | 312 | 10% | 2009-11-24 | 9:29
Chilectra | RET003R002SE038R002 | Recoleta B2 | 12
Chilectra | RET004R002SE038R002 | Recoleta B4 | 12 | 1 | 0.01 | 0.93 | 722 | 1784 | 24% | 1 | 0.02 | 0.96 | 563 | 1188 | 19% | 2009-11-24 | 9:29
Chilectra | RET001R002SE039R002 | Renca | 110
Chilectra | RET001R002SE088R002 | Rungue 23KV | 23 | 1 | 0.99 | 0.93 | 0 | 464 | 0% | 1 | 0.43 | 0.96 | 1241 | 2508 | 42% | 2012-02-28 | 10:58
Chilectra | RET002R002SE040R002 | San Bernardo B1 | 12 | 1 | 0.97 | 0.93 | 0 | 1370 | 0% | 1 | 0.72 | 0.96 | 259 | 1602 | 9% | 2012-02-28 | 10:58
Chilectra | RET003R002SE040R002 | San Bernardo B2 | 12 | 1 | 0.97 | 0.93 | 0 | 47 | 0% | 1 | 0.01 | 0.96 | 1945 | 2454 | 78% | 2012-02-28 | 10:58
Chilectra | RET004R002SE040R002 | San Bernardo B3 | 12 | 1 | 0.95 | 0.93 | 0 | 2258 | 0% | 1 | 0.92 | 0.96 | 48 | 714 | 2% | 2012-02-28 | 10:58
Chilectra | RET002R002SE041R002 | San Cristóbal B1 | 12 | 1 | 0.97 | 0.93 | 0 | 316 | 0% | 1 | 0.79 | 0.96 | 569 | 2578 | 20% | 2012-02-28 | 10:58
Chilectra | RET003R002SE041R002 | San Cristóbal B2 | 12 | 1 | 0.98 | 0.93 | 0 | 157 | 0% | 1 | 0.78 | 0.96 | 597 | 2815 | 20% | 2012-02-28 | 10:58
Chilectra | RET004R002SE041R002 | San Cristóbal B3 | 12 | 1 | 0.99 | 0.93 | 0 | 2107 | 0% | 1 | 0.99 | 0.96 | 0 | 822 | 0% | 2012-02-28 | 10:58
Chilectra | RET002R002SE042R002 | San Joaquín B1 | 12 | 1 | 0.97 | 0.93 | 0 | 449 | 0% | 1 | 0.74 | 0.96 | 835 | 2523 | 28% | 2012-02-28 | 10:58
Chilectra | RET003R002SE042R002 | San Joaquín B2 | 12 | 1 | 0.93 | 0.93 | 0 | 1404 | 0% | 1 | 0.73 | 0.96 | 556 | 1568 | 19% | 2012-02-28 | 10:58
Chilectra | RET004R002SE042R002 | San Joaquín B3 | 12 | 1 | 0.98 | 0.93 | 0 | 1587 | 0% | 1 | 0.88 | 0.96 | 91 | 1385 | 3% | 2012-02-28 | 10:58
Chilectra | RET005R002SE042R002 | San Joaquín B4 | 12 | 1 | 0.99 | 0.93 | 0 | 652 | 0% | 1 | 0.66 | 0.96 | 921 | 2091 | 34% | 2012-02-28 | 10:58
Chilectra | RET001R002SE043R002 | San José B1 | 12 | 1 | 0.95 | 0.93 | 0 | 2972 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-02-28 | 10:58
Chilectra | RET003R002SE043R002 | San José B2 | 12 | 1 | 0.95 | 0.93 | 0 | 2270 | 0% | 1 | 0.98 | 0.96 | 0 | 688 | 0% | 2012-02-28 | 10:58
Chilectra | RET004R002SE043R002 | San José B3 | 12 | 1 | 0.96 | 0.93 | 0 | 2911 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-02-28 | 10:58
Chilectra | RET005R002SE043R002 | San José B4 | 12
Chilectra | RET002R002SE044R002 | San Pablo 23KV B1 | 23 | 1 | 0.95 | 0.93 | 0 | 117 | 0% | 1 | 0.94 | 0.96 | 1 | 2855 | 0% | 2012-02-28 | 10:58
Chilectra | RET003R002SE044R002 | San Pablo 23KV B2 | 23 | 1 | 0.97 | 0.93 | 0 | 2500 | 0% | 1 | 0.99 | 0.96 | 0 | 472 | 0% | 2012-02-28 | 10:58
Chilectra | RET002R002SE045R002 | Santa Elena B1 | 12 | 1 | 0.82 | 0.93 | 1290 | 2359 | 43% | 1 | 0.75 | 0.96 | 144 | 613 | 5% | 2012-02-28 | 10:58
Chilectra | RET003R002SE045R002 | Santa Elena B2 | 12 | 1 | 0.96 | 0.93 | 0 | 455 | 0% | 1 | 0.87 | 0.96 | 138 | 2517 | 5% | 2012-02-28 | 10:58
Chilectra | RET004R002SE045R002 | Santa Elena B3 | 12 | 1 | 0.96 | 0.93 | 0 | 2954 | 0% | 1 | 1 | 0.96 | 0 | 18 | 0% | 2012-02-28 | 10:58
Chilectra | RET005R002SE045R002 | Santa Elena B4 | 12 | 1 | 0.98 | 0.93 | 0 | 1545 | 0% | 1 | 0.9 | 0.96 | 69 | 1427 | 2% | 2012-02-28 | 10:58
Chilectra | RET002R002SE046R002 | Santa Marta 23KV B3 | 23 | 1 | 0.97 | 0.93 | 0 | 2535 | 0% | 1 | 0.96 | 0.96 | 0 | 370 | 0% | 2012-02-28 | 10:58
Chilectra | RET003R002SE046R002 | Santa Marta B1 | 12 | 0 | 0 | 0.93 | 0 | 0 | 0% | 1 | 0.61 | 0.96 | 2164 | 2925 | 74% | 2012-02-28 | 10:58
Chilectra | RET004R002SE046R002 | Santa Marta B2 | 12 | 1 | 0.9 | 0.93 | 144 | 2816 | 5% | 1 | 0.79 | 0.96 | 32 | 156 | 1% | 2012-02-28 | 10:58
Chilectra | RET001R002SE047R002 | Santa Raquel B1 | 12 | 1 | 0.91 | 0.93 | 82 | 2912 | 3% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-02-28 | 10:58
Chilectra | RET003R002SE047R002 | Santa Raquel B2 | 12 | 1 | 0.93 | 0.93 | 0 | 2972 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-02-28 | 10:58
Chilectra | RET004R002SE047R002 | Santa Raquel B4 | 12 | 1 | 0.93 | 0.93 | 0 | 379 | 0% | 1 | 0.77 | 0.96 | 1052 | 2593 | 35% | 2012-02-28 | 10:58
Chilectra | RET005R002SE047R002 | Santa Raquel B5 | 12 | 0 | 0 | 0.93 | 0 | 0 | 0% | 0.99 | 0.26 | 0.96 | 1811 | 2972 | 61% | 2012-02-28 | 10:58
Chilectra | RET001R002SE048R002 | Santa Rosa B1 | 12 | 0.99 | 0.88 | 0.93 | 224 | 2913 | 8% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-02-28 | 10:58
Chilectra | RET003R002SE048R002 | Santa Rosa B2 | 12 | 1 | 0.01 | 0.93 | 919 | 2965 | 31% | 0.7 | 0.05 | 0.96 | 7 | 7 | 0% | 2009-11-24 | 9:29
Chilectra | RET004R002SE048R002 | Santa Rosa B3 | 12 | 0.98 | 0.88 | 0.93 | 833 | 2927 | 28% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-11-24 | 9:29
Chilectra | RET002R002SE048R002 | Santa Rosa B4 Sur | 12 | 0.99 | 0.01 | 0.93 | 90 | 2967 | 3% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-11-24 | 9:29
Chilectra | RET001R002SE013R002 | T1 El Manzano | 23 | 0.98 | 0.01 | 0.93 | 501 | 2228 | 22% | 0.11 | 0.02 | 0.96 | 2 | 2 | 0% | 2009-11-24 | 9:29
Chilectra | RET002R002SE033R002 | T1 Metro - Ochagavia | 12
Chilectra | RET002R002SE013R002 | T2 El Manzano | 23 | 0.98 | 0.01 | 0.93 | 393 | 2234 | 18% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-11-24 | 9:29
Chilectra | RET001R002SE049R002 | Vitacura B1 | 12 | 1 | 0.01 | 0.93 | 167 | 334 | 6% | 1 | 0.01 | 0.96 | 1275 | 2638 | 43% | 2009-11-24 | 9:29
Chilectra | RET002R002SE049R002 | Vitacura B2 | 12 | 1 | 0.01 | 0.93 | 483 | 1625 | 16% | 0.99 | 0.01 | 0.96 | 1120 | 1347 | 38% | 2009-11-24 | 9:29
Chilectra | RET003R002SE049R002 | Vitacura B3 | 12 | 1 | 0.02 | 0.93 | 56 | 119 | 2% | 1 | 0.02 | 0.96 | 1456 | 2853 | 49% | 2009-11-24 | 9:29
Chilectra | RET004R002SE049R002 | Vitacura B4 | 12 | 1 | 0.01 | 0.93 | 297 | 479 | 10% | 1 | 0.01 | 0.96 | 815 | 2493 | 27% | 2009-11-24 | 9:29
Chilectra | RET007L021SE038T002 | CMPC Cart- CHUMPULLO - S/E Chumpull | 6 | 1 | 0.9 | 0.93 | 1 | 2943 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-11-09 | 10:38
Chilectra | RET006L021SE003G004 | CMPC Cart- MAULE - S/E Colbún | 220 | 1 | 0.02 | 0.98 | 650 | 2323 | 22% | 1 | 0.01 | 1 | 483 | 649 | 16% | 2009-11-19 | 11:55
CMPC | RET002L021SE008L021 | CMPC Cel- CELPAC - S/E Charrúa | 220 | 1 | 0.85 | 0.98 | 127 | 2972 | 4% | 0 | 0 | 1 | 0 | 0 | 0% | 2009-11-11 | 11:14
CMPC | RET001L021SE005L021 | CMPC Cel- LAJA - S/E Charrúa | 220
CMPC | RET003L021SE002L021 | CMPC Cel- SANTA FE - S/E Charrúa | 220
CMPC | RET001L021SE002G025 | CMPC Maderas Aserradero Bucalemu - S/E Bucalemu | 13 | 1 | 0.9 | 0.93 | 71 | 2946 | 2% | 1 | 0.89 | 0.96 | 12 | 26 | 0% | 2012-01-17 | 17:06
CMPC | RET005L021SE004L021 | CMPC-CORDILLERA - S/E Maipo | 110
CMPC | RET004L021SE007L021 | CMPC-INFORSA - S/E Charrúa | 220
CMPC | RET001L020SE002G013 | CODELCO A-Polpaico - S/E El Llano | 220 | 0 | 0 | 0.98 | 0 | 0 | 0% | 1 | 0.01 | 1 | 1859 | 2092 | 89% | 2010-04-15 | 13:18
CMPC | RET001L020SE003L020 | CODELCO A-Saladillo - S/E Saladillo | 66 | 1 | 0.94 | 0.96 | 1 | 521 | 0% | 1 | 0.95 | 0.98 | 67 | 2455 | 2% | 2010-04-15 | 13:18
CODELCO | RET001L020SE005L020 | CODELCO Salvador - S/E Diego de Almagro | 110 | 0.97 | 0.88 | 0.98 | 2972 | 2972 | 100% | 0 | 0 | 1 | 0 | 0 | 0% | 2009-11-06 | 12:56
CODELCO | RET001L020SE002L020 | CODELCO T-Candelaria - S/E Candelaria | 220 | 0.97 | 0.88 | 0.98 | 2972 | 2972 | 100% | 0 | 0 | 1 | 0 | 0 | 0% | 2010-11-04 | 17:09
CODELCO | RET001L020SE009L020 | CODELCO Ventanas - S/E Tap Enami | 110 | 1 | 0.95 | 0.98 | 1634 | 2972 | 55% | 0 | 0 | 1 | 0 | 0 | 0% | 2009-12-18 | 10:13
CODELCO | RET001L020SE002G015 | S/E Los Maquis | 220
CODELCO | RET001R019SE058T005 | Lautaro | 13.2 | 1 | 0.88 | 0.93 | 30 | 1826 | 1% | 1 | 0.86 | 0.96 | 14 | 1146 | 0% | 2009-11-06 | 16:02
CODELCO | RET001R004SE129T005 | Loncoche | 13.2 | 1 | 0.76 | 0.93 | 604 | 2098 | 20% | 1 | 0.02 | 0.96 | 316 | 874 | 11% | 2009-11-06 | 16:02
CODINER | RET001R004SE092T005 | Pitrufquén | 13.2 | 0.01 | 0.01 | 0.93 | 303 | 303 | 100% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-11-06 | 16:02
CODINER | RET001R004SE037T002 | Temuco | 23 | 1 | 0.01 | 0.93 | 929 | 942 | 47% | 1 | 0.01 | 0.96 | 1027 | 1033 | 52% | 2009-11-06 | 16:02
CODINER | RET001R004SE064T005 | Traiguén | 13.2 | 0.94 | 0.94 | 0.93 | 0 | 2976 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2009-11-06 | 16:02
CODINER | RET001R019SE068T005 | Victoria | 13.2 | 1 | 0.01 | 0.93 | 168 | 1621 | 7% | 1 | 0.95 | 0.96 | 1 | 746 | 0% | 2009-11-06 | 16:02
CODINER | RET001R006SE003R019 | Cabrero (SGA) | 13.2 | 1 | 0.93 | 0.93 | 0 | 11682 | 0% | 1 | 0.74 | 0.96 | 574 | 2464 | 4% | 2012-04-23 | 10:38
CODINER | RET001R006SE004T003 | Cholguán (SGA) | 13.2 | 1 | 0.87 | 0.93 | 239 | 14219 | 2% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-04-23 | 10:38
COELCHA | RET001R007SE001R007 | Curicó T4 | 13.2 | 1 | 1 | 0.93 | 0 | 138 | 0% | 1 | 0.57 | 0.96 | 1947 | 2834 | 66% | 2009-11-13 | 16:57
COELCHA | RET001R007SE126T005 | Quinta | 66 | 1 | 0.94 | 0.96 | 41 | 1422 | 1% | 1 | 0.8 | 0.98 | 420 | 1550 | 14% | 2009-11-13 | 16:57
COOP. CURICO (CEC) | RET001R007SE127T005 | Teno | 13.2 | 1 | 0.97 | 0.93 | 0 | 2179 | 0% | 1 | 0.96 | 0.96 | 0 | 793 | 0% | 2012-01-17 | 11:24
COOP. CURICO (CEC) | RET002R011SE076T005 | Canteras | 13.2 | 1 | 0.91 | 0.93 | 23 | 2972 | 1% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-01-20 | 21:47
COOP. CURICO (CEC) | RET004R011SE076T005 | Huaqui | 13.2 | 1 | 0.95 | 0.93 | 0 | 2972 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-01-20 | 21:47
COOPELAN | RET001R019SE076T005 | Los Angeles | 13.2 | 1 | 0.95 | 0.93 | 0 | 2972 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-01-20 | 21:47
COOPELAN | RET003R011SE076T005 | Santa Fe | 13.2 | 1 | 0.93 | 0.93 | 0 | 2972 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-01-20 | 21:47
COOPELAN | RET001R025SE012T003 | La Unión | 13.2 | 1 | 0.91 | 0.93 | 31 | 2972 | 1% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-07-08 | 15:15
COOPELAN | RET001R008SE001G008 | Pilmaiquén | 13.2 | 1 | 0.94 | 0.93 | 0 | 2964 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-07-08 | 15:15
COOPREL | RET002R013SE001R013 | Quilmo 66 KV | 13 | 1 | 0.95 | 0.93 | 0 | 2972 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-02-23 | 16:58
COOPREL | RET001R010SE021T003 | CRELL | 13.2 | 1 | 0.96 | 0.93 | 0 | 2366 | 0% | 1 | 0.99 | 0.96 | 0 | 601 | 0% | 2009-11-10 | 16:34
COPELEC | RET001L054SE001L054 | MANTO VERDE-Almagro - S/E Diego de Almagro | 110
CRELL | RET001L054SE002L054 | MANTO VERDE-Impulsion - S/E Impulsión | 23
Divisiones AngloAmerican | RET001L008SE002L008 | MSA-CHAGRES - S/E Chagres | 110 | 1 | 0.95 | 0.98 | 6 | 2950 | 0% | 1 | 0.99 | 1 | 12 | 22 | 0% | 2009-11-06 | 13:01
Divisiones AngloAmerican | RET001L061SE001L061 | MSA-EL SOLDADO - S/E La Calera | 110
Divisiones AngloAmerican | RET001L022SE004G010 | MSA-LOS BRONCES - S/E Polpaico | 220
Divisiones AngloAmerican | RET001R020SE005R020 | S/E El Totoral | 12
Divisiones AngloAmerican | RET001R020SE004R020 | S/E Tap El Manzano | 12
E. E. LITORAL | PA03R020SE003R020 | San Jerónimo | 66
E. E. LITORAL | RET001R020SE001R020 | SPD Las Balandras | 12
E. E. LITORAL | RET001R020SE002R020 | SPD Las Piñatas | 12
E. E. LITORAL | RET001R020SE003R020 | SPD San Jerónimo | 12
E. E. LITORAL | RET004R026SE018R002 | Pintana T4 | 110
E. E. LITORAL | RET001R026SE003R026 | Vizcachas | 110
E. E. PUENTE ALTO | RET001L015SE001L015 | EKA - S/E San Vicente | 154
E. E. PUENTE ALTO | RET001R001SE001R001 | Diego de Almagro | 110
EKA CHILE | RET001R016SE001R016 | S/E Caldera | 23
ELECDA | RET002R016SE002R016 | S/E Cerrillos | 23
EMELAT | RET001R016SE004R016 | S/E Copiapó | 13.8
EMELAT | RET002R016SE004R016 | S/E Copiapó CT4 | 13.8
EMELAT | RET001R016SE014T002 | S/E Diego De Almagro | 23
EMELAT | RET001R016SE005R016 | S/E Hernán Fuentes | 23
EMELAT | RET001R016SE019T002 | S/E Huasco | 13
EMELAT | RET001R016SE017T005 | S/E Incahuasi | 23
EMELAT | RET001R016SE006R016 | S/E Los Loros | 23
EMELAT | RET001R016SE007R016 | S/E Plantas | 23
EMELAT | RET001R016SE008R016 | S/E Tierra Amarilla | 23
EMELAT | RET002R016SE008R016 | S/E Tierra Amarilla ET2 | 23
EMELAT | RET001R016SE039T002 | Vallenar 13.2 | 13.2
EMELAT | RET001L030SE001L030 | ENAMI - Fundicion Paipote - S/E H. Videla L. | 110
EMELAT | RET001L030SE004G011 | ENAMI - Planta Matta - S/E Pta. Matta | 110
ENAMI - H. V. LIRA | RET001L002SE007R003 | ENAP ACONCAGUA - S/E Miraflores Barra | 110
ENAMI - H. V. LIRA | RET001L034SE001L034 | ENAP BIO BIO - S/E Petrox | 66
ENAP REFINERIAS | RET001L011SE003L011 | EFE - Curicó - S/E Curicó | 66
ENAP REFINERIAS | RET002L011SE007L011 | EFE - Jahuel 66 KV - S/E Jahuel | 66
FFCC | RET003L011SE008L011 | EFE - Laja - S/E Laja | 66
FFCC | RET005L011SE010L011 | EFE - Monte Aguila - S/E Charrua | 66
FFCC | RET006L011SE011L011 | EFE - San Fernando - S/E San Fernando | 66
FFCC | RET001G032SE001G032 | FPC - S/E Fopaco | 154
FFCC | BA01T002SE001G021 | ABANICO | 13.2
Forestal y Papelera Concepción | RET002R019SE028T005 | ANGOL 13.2 | 13.2
frontel | RET001R019SE028T005 | ANGOL 23 | 23
frontel | RET001R019SE003R019 | CABRERO | 23
frontel | RET001R019SE033T005 | CARAMPANGUE | 23
frontel | RET001R019SE004T003 | CHOLGUAN | 13.2
frontel | RET001R019SE043T005 | COLLIPULLI | 13.2
frontel | RET001R019SE142T005 | CORONEL | 15
frontel | RET001R019SE013T005 | CURACAUTIN | 13.2
frontel | RET001R019SE036T005 | CURANILAHUE 13.2 | 13.2
frontel | RET002R019SE036T005 | CURANILAHUE 23 | 23
frontel | RET001R019SE004R019 | ENACAR | 13.2
frontel | RET001R019SE022T002 | LAJA | 13.2
frontel | RET001R019SE058T005 | LAUTARO | 13.2 | 1 | 0.88 | 0.93 | 30 | 1826 | 1% | 1 | 0.86 | 0.96 | 14 | 1146 | 0% | 2009-11-06 | 16:02
frontel | RET002R019SE058T005 | LAUTARO 23 | 23
frontel | RET001R019SE011T005 | LEBU | 13.2
frontel | RET002R019SE001R019 | LICANCO | 23
frontel | RET001R019SE076T005 | LOS ANGELES | 13.2 | 1 | 0.95 | 0.93 | 0 | 2972 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2012-01-20 | 21:47
frontel | RET001R019SE005R019 | LOTA | 13.2
frontel | RET001R019SE002R019 | NEGRETE | 23
frontel | RET001R019SE006R019 | NUEVA IMPERIAL | 23
frontel | RET001R019SE091T005 | PILLANLELBUN | 13.2
frontel | RET001R019SE092T005 | PITRUFQUEN | 13.2
frontel | RET001R019SE064T005 | TRAIGUEN | 13.2
frontel | RET002R019SE065T005 | TRES PINOS 13.2 | 13.2
frontel | RET001R019SE065T005 | TRES PINOS 23 | 23
frontel | RET001R019SE068T005 | VICTORIA | 13.2 | 1 | 0.01 | 0.93 | 168 | 1621 | 7% | 1 | 0.95 | 0.96 | 1 | 746 | 0% | 2009-11-06 | 16:02
frontel | RET001L064SE033T002 | FUNDICION TALLERES-Maestranza - S/E Maestranza | 66
frontel | RET001R017SE001R017 | S/E Alcones | 23
fundtalleres | RET001R017SE002R017 | S/E Bajo Melipilla | 13.2 | 1 | 0.95 | 0.98 | 416 | 1533 | 14% | 1 | 0.93 | 1 | 850 | 1439 | 29% | 2009-11-06 | 14:51
Grupo Emel | RET001R017SE003R017 | S/E Bollenar | 13.2
Grupo Emel | RET001R017SE004R017 | S/E Cauquenes | 13.2
Grupo Emel | RET001R017SE005R017 | S/E Chocalán | 13.2
Grupo Emel | RET001R017SE006R017 | S/E Cocharcas (Emelectric) | 33
Grupo Emel | RET001R017SE007R017 | S/E Constitución | 23
Grupo Emel | RET001R017SE008R017 | S/E El Maitén | 13.2
Grupo Emel | RET001R017SE009R017 | S/E El Monte | 13.2
Grupo Emel | RET001R017SE010R017 | S/E El Paico | 13.2
Grupo Emel | RET001R017SE011R017 | S/E El Peumo | 13.2
Grupo Emel | RET001R017SE012R017 | S/E El Retiro | 13.2
Grupo Emel | RET001R017SE013R017 | S/E Hualañe | 13.2
Grupo Emel | RET001R017SE020T002 | S/E Itahue | 13.2
Grupo Emel | RET001R017SE015R017 | S/E La Esperanza (Emelectric) | 13.2
Grupo Emel | RET001R017SE036R017 | S/E La Manga | 13.2
Grupo Emel | RET001R017SE016R017 | S/E Las Arañas | 13.2
Grupo Emel | RET004R017SE016R017 | S/E Las Arañas 23 | 23
Grupo Emel | RET001R017SE046R017 | S/E Leyda | 13.2
Grupo Emel | RET002R017SE018R017 | S/E Licanten | 13.8
Grupo Emel | RET001R017SE017R017 | S/E Lihueimo | 13.2
Grupo Emel | RET002R017SE017R017 | S/E Lihueimo 2 | 13.2
Grupo Emel | RET001R017SE019R017 | S/E Mandinga | 13.2
Grupo Emel | RET001R017SE020R017 | S/E Marchigüe | 13.2
Grupo Emel | RET001R017SE022R017 | S/E Nancagua | 13.2
Grupo Emel | RET001R017SE023R017 | S/E Paniahue | 13.2
Grupo Emel | RET001R017SE130T005 | S/E Parral | 13.2
Grupo Emel | RET001R017SE025R017 | S/E Parronal | 13.2
Grupo Emel | RET001R017SE026R017 | S/E Placilla | 13.2
Grupo Emel | RET001R017SE039R017 | S/E Quelentaro | 13.2
Grupo Emel | RET001R017SE028R017 | S/E San Carlos | 13.2
Grupo Emel | RET001R017SE029R017 | S/E San Javier | 23
Grupo Emel | RET001R017SE030R017 | S/E Santa Rosa | 23
Grupo Emel | RET001R017SE061T005 | S/E Talca | 15
Grupo Emel | RET001R017SE063T005 | S/E Tomé | 23
Grupo Emel | RET001R017SE031R017 | S/E Villa Prat | 13.2
Grupo Emel | RET001L005SE035T002 | INCHALAM - S/E San Vicente | 13
Grupo Emel | RET001L004SE002L004 | Indura - Graneros | 66
INCHALAM | RET001L004SE001L004 | Indura - Lirquen | 66
INDURA | RET003R021SE001R021 | Barrio Industrial | 13.2
INDURA | RET003R021SE002R021 | Colbún | 13.2
LUZLINARES y LUZPARRAL | RET002R021SE002R021 | Las Cañas | 23
LUZLINARES y LUZPARRAL | RET001R021SE001R021 | Linares Norte | 13.2
LUZLINARES y LUZPARRAL | RET002R021SE001R021 | Linares Sur | 13.2
LUZLINARES y LUZPARRAL | RET001R021SE002R021 | Panimávida | 13.2
LUZLINARES y LUZPARRAL | RET001R024SE011T003 | AIHUAPI | 23
LUZLINARES y LUZPARRAL | RET001R008SE012T003 | LA UNION 13.2 | 13.2
LUZOSORNO | RET002R008SE012T003 | LA UNION 23 | 23
LUZOSORNO | RET001R008SE007T003 | LOS NEGROS | 23
LUZOSORNO | RET001R024SE016T003 | OSORNO | 13.2
LUZOSORNO | RET001R008SE001G008 | PILMAIQUEN | 13.2 | 1 | 0.94 | 0.93 | 0 | 2964 | 0% | 0 | 0 | 0.96 | 0 | 0 | 0% | 2010-07-08 | 15:15
LUZOSORNO | RET001R024SE022T003 | PURRANQUE | 13.2
LUZOSORNO | RET003R022SE130T005 | Bullileo | 13.2
LUZOSORNO | RET001R022SE001R022 | Longaví | 13.2
LUZPARRAL | RET001R017SE012R017 | Retiro | 13.2
LUZPARRAL | RET001R017SE028R017 | San Carlos | 13.2
LUZPARRAL | RET001L044SE001L044 | MASISA-Mapal - S/E Mapal | 154
LUZPARRAL | RET001L044SE003L044 | MASISA-Masonite - S/E FAM | 66
MASISA | RET001L044SE007R019 | MASISA-Masonite - S/E MASISA Cabrero | 13.2
MASISA | RET001L064SE001L064 | FUNDICION TALLERES-Rancagua - S/E Rancagua | 13
MASISA | RET002R002SE033R002 | METRO - S/E Ochagavia | 110
mblancos | RET001L014SE087R002 | METRO - S/E Renca | 110
METRO | RET001L031SE035T002 | MOLY-COP - S/E San Vicente | 13
METRO | RET001L043SE001L043 | OXY - S/E Oxy | 154
MOLY - COP CHILE | RET002L041SE001L041 | PAP. BIO BIO - S/E San Pedro | 66
OXY | RET001L038SE001L038 | PETRODOW - S/E Petrodow | 154
PAP. BIO BIO | RET001L035SE001L035 | PETROQUIM - S/E Petropower | 66
PETRODOW | RET001R024SE011T003 | AIHUAPI | 23
PETROQUIM | RET001R024SE002T003 | ANCUD | 23
SAESA | RET001R024SE027T003 | CALBUCO | 23
SAESA | RET002R024SE005T003 | CHONCHI | 23
SAESA | RET001R024SE006T003 | COLACO | 23
SAESA | RET001R024SE001T003 | CORRAL | 13.2
SAESA | RET003R024SE001G033 | DEGAN | 23
SAESA | RET001R024SE008T003 | EMPALME | 66
SAESA | RET001R024SE010T003 | FRUTILLAR | 13.2
SAESA | RET001R024SE007T003 | L.NEGROS | 23
SAESA | RET002R024SE012T003 | LA UNION 13.2 | 13.2
SAESA | RET001R024SE012T003 | LA UNION 23 | 23
SAESA | RET002R024SE129T005 | LONCOCHE 13.2 | 13.2
SAESA | RET001R024SE129T005 | LONCOCHE 23 | 23
SAESA | RET001R024SE014T003 | LOS LAGOS | 13.2
SAESA | RET001R024SE013T003 | MELIPULLI | 23
SAESA | RET001R024SE016T003 | OSORNO | 23
SAESA | RET002R024SE021T003 | P. VARAS 13.2 | 13.2
SAESA | RET001R024SE021T003 | P. VARAS 23 | 23
SAESA | RET001R024SE017T003 | PANGUIPULLI | 23
SAESA | RET002R024SE018T003 | PICARTE 13.2 | 13.2
SAESA | RET001R024SE018T003 | PICARTE 23 | 23
SAESA | RET002R024SE019T003 | PICHIRROPULLI 13.2 | 13.2
SAESA | RET001R024SE019T003 | PICHIRROPULLI 23 | 23
SAESA | RET001R024SE015T003 | PID PID | 23
SAESA | RET001R024SE001G008 | PILMAIQUEN | 13.2
SAESA | RET001R024SE031T002 | PTO. MONTT | 23
SAESA | RET002R024SE031T002 | PTO. MONTT T44 | 23
SAESA | RET001R024SE022T003 | PURRANQUE | 13.2
SAESA | RET002R024SE022T003 | PURRANQUE 23 kV | 23
SAESA | RET001R024SE026T003 | QUELLON | 23
SAESA | RET001R024SE038T002 | VALDIVIA | 13.2
SAESA | RET002R024SE038T002 | VALDIVIA 23 kV | 23
SAESA | RET001R024SE014T003 | Los Lagos | 13.2
SAESA | RET001R014SE001R014 | Paillaco | 13.2
SOCOEPA | RET002R012SE022T005 | S/E Alameda | 15
SOCOEPA | RET001R012SE022T005 | S/E Alameda | 15
TRANSNET | RET002R015SE026T005 | S/E Andacollo | 13.2
TRANSNET | RET001R015SE026T005 | S/E Andacollo | 66 | 0.92 | 0.45 | 0.96 | 15 | 15 | 100% | 0 | 0 | 0.98 | 0 | 0 | 0% | 2010-05-10 | 9:08
TRANSNET | RET002R012SE027T005 | S/E Andali | 15
TRANSNET | RET003R012SE027T005 | S/E Andali | 15
TRANSNET | RET001R019SE028T005 | S/E Angol | 13.2
TRANSNET | RET002R012SE030T005 | S/E Buin (C.G.E.) | 15
TRANSNET | RET004R012SE030T005 | S/E Buin (C.G.E.) | 15
TRANSNET | RET002R015SE031T005 | S/E Cabildo | 23
TRANSNET | RET003R015SE031T005 | S/E Cabildo | 23
TRANSNET | RET005R012SE032T005 | S/E Cachapoal | 15
TRANSNET | RET002R012SE032T005 | S/E Cachapoal | 15
TRANSNET | RET003R019SE033T005 | S/E Carampangue | 13.2
TRANSNET | RET004R015SE047T005 | S/E Casas Viejas | 13.2
TRANSNET | RET001A002SE002A002 | S/E Celulosa Arauco | 66 | 1 | 0.01 | 0.96 | 385 | 692 | 13% | 1 | 0.01 | 0.98 | 1202 | 2186 | 42% | 2010-05-10 | 9:08
TRANSNET | RET002R005SE100T005 | S/E Chacahu | 13.2
TRANSNET | RET001R005SE100T005 | S/E Chacahu | 13.2
TRANSNET | RET002R012SE035T005 | S/E Chiguayante | 15
TRANSNET | RET006R012SE035T005 | S/E Chiguayante | 15
TRANSNET | RET008R012SE024T005 | S/E Chill | 15 | 1 | 0.01 | 0.93 | 795 | 920 | 27% | 1 | 0.01 | 0.96 | 923 | 2012 | 31% | 2010-05-10 | 9:08
TRANSNET | RET007R012SE024T005 | S/E Chill | 15
TRANSNET | RET009R012SE037T005 | S/E Chimbarongo | 15 | 0 | 0 | 0.93 | 0 | 0 | 0% | 0.96 | 0.01 | 0.96 | 1756 | 1757 | 100% | 2010-05-10 | 9:08
TRANSNET | RET010R012SE038T005 | S/E Chivilc | 15
TRANSNET | RET002R012SE038T005 | S/E Chivilc | 15
TRANSNET | RET011R012SE040T005 | S/E Chumaquito | 15
TRANSNET | RET012R012SE128T005 | S/E Cocharcas (C.G.E) | 15 | 1 | 0.01 | 0.93 | 105 | 109 | 4% | 1 | 0.01 | 0.96 | 2283 | 2330 | 94% | 2010-05-10 | 9:08
TRANSNET | RET002R012SE041T005 | S/E Colchagua | 15
TRANSNET | RET014R012SE042T005 | S/E Colcura | 13.2 | 1 | 1 | 0.93 | 0 | 10 | 0% | 1 | 0.03 | 0.96 | 2552 | 2962 | 86% | 2010-05-10 | 9:08
TRANSNET | RET006R019SE043T005 | S/E Collipulli | 13.2
TRANSNET | RET002R012SE044T005 | S/E Colo Colo | 15
TRANSNET | RET015R012SE044T005 | S/E Colo Colo | 15
TRANSNET | RET016R012SE013T002 | S/E Coronel | 15
TRANSNET | RET007R019SE013T002 | S/E Coronel | 15
TRANSNET | RET009R019SE036T005 | S/E Curanilahue | 23 | 1 | 0.01 | 0.93 | 591 | 599 | 27% | 1 | 0.01 | 0.96 | 1605 | 1608 | 73% | 2010-05-10 | 9:08
TRANSNET | RET002R005SE126T005 | S/E Curicó | 13.2
TRANSNET | RET003R005SE126T005 | S/E Curicó | 13.2
TRANSNET | RET001R007SE126T005 | S/E Curicó | 13 | 1 | 0.94 | 0.96 | 41 | 1422 | 1% | 1 | 0.8 | 0.98 | 420 | 1550 | 14% | 2009-11-13 | 16:57
TRANSNET | RET002R012SE002T005 | S/E Ejército | 15
TRANSNET | RET019R012SE002T005 | S/E Ejército | 15
TRANSNET | RET020R012SE003T005 | S/E El Avellano | 23
TRANSNET | RET022R012SE115T005 | S/E El Manzano (C.G.E.) | 15 | 1 | 0.01 | 0.93 | 888 | 1240 | 68% | 1 | 0.01 | 0.96 | 61 | 74 | 5% | 2010-05-10 | 9:08
TRANSNET | RET006R015SE005T005 | S/E El Peñon | 23
TRANSNET | RET023R012SE007T005 | S/E Escuadr?n (C.G.E.) | 15
TRANSNET | RET024R012SE023T005 | S/E F?tima | 15
TRANSNET | RET025R012SE012T005 | S/E Graneros | 15
TRANSNET | RET009R015SE001T005 | S/E Guayac | 13.2
TRANSNET | RET010R015SE001T005 | S/E Guayac | 13.2
TRANSNET | RET026R012SE015T005 | S/E Hospital | 15
TRANSNET | RET011R015SE016T005 | S/E Illapel | 23
TRANSNET | RET003R005SE010T005 | S/E La Palma | 13.2
TRANSNET | RET023R012SE018T005 | S/E La Ronda | 15 | 1 | 0.01 | 0.93 | 345 | 359 | 14% | 0.96 | 0.01 | 0.96 | 2140 | 2170 | 85% | 2010-05-10 | 9:08
TRANSNET | RET028R012SE019T005 | S/E Las Cabras | 15
TRANSNET | RET014R015SE020T005 | S/E Las Compa??as | 13.2
TRANSNET | RET029R012SE021T005 | S/E Latorre | 15
TRANSNET | RET002R012SE021T005 | S/E Latorre | 15
TRANSNET | RET030R012SE058T005 | S/E Lautaro | 15 | 1 | 0.01 | 0.93 | 39 | 47 | 1% | 1 | 0.01 | 0.96 | 2740 | 2876 | 94% | 2010-05-10 | 9:08
TRANSNET | RET031R012SE072T005 | S/E Lirqu | 15
TRANSNET | RET002R012SE073T005 | S/E Lo Miranda | 15
TRANSNET | RET032R012SE073T005 | S/E Lo Miranda | 15
TRANSNET | RET033R012SE074T005 | S/E Loma Colorada | 15
TRANSNET | RET002R004SE129T005 | S/E Loncoche | 13.2
TRANSNET | RET016R024SE129T005 | S/E Loncoche | 13.2
TRANSNET | RET034R012SE129T005 | S/E Loncoche | 23
TRANSNET | RET008R024SE129T005 | S/E Loncoche | 13.2
TRANSNET | RET007R024SE129T005 | S/E Loncoche | 13.2
TRANSNET | RET035R012SE075T005 | S/E Loreto | 15
TRANSNET | RET036R012SE076T005 | S/E Los Angeles | 15
TRANSNET | RET001R011SE076T005 | S/E Los Angeles | 13
TRANSNET | RET037R012SE076T005 | S/E Los Angeles | 13.2
TRANSNET | RET001L007SE076T005 | S/E Los Angeles | 13
TRANSNET | RET016R019SE076T005 | S/E Los Angeles | 13.2
TRANSNET | RET015R015SE025T002 | S/E Los Vilos | 23
TRANSNET | RET001R012SE147T005 | S/E Machalí | 15
TRANSNET | RET002R012SE077T005 | S/E Mahns | 15
TRANSNET | RET038R012SE077T005 | S/E Mahns | 15
TRANSNET | RET039R012SE078T005 | S/E Malloa | 15 | 0 | 0 | 0.93 | 0 | 0 | 0% | 0.97 | 0.57 | 0.96 | 2662 | 2737 | 97% | 2010-05-10 | 9:08
TRANSNET | RET041R012SE079T005 | S/E Manso de Velasco | 15
TRANSNET | RET017R015SE080T005 | S/E Marquesa_1 | 23
TRANSNET | RET018R015SE080T005 | S/E Marquesa_2 | 23
TRANSNET | RET019R015SE080T005 | S/E Marquesa_3 | 23
TRANSNET | RET001L059SE001L059 | S/E Minera Carmen de Andacollo | 110 | 1 | 0.9 | 0.98 | 523 | 2972 | 18% | 0 | 0 | 1 | 0 | 0 | 0% | 2012-01-19 | 14:35
TRANSNET | RET002R005SE009T005 | S/E Molina | 13.2
TRANSNET | RET002R012SE009T005 | S/E Molina | 66
TRANSNET | RET006R005SE009T005 | S/E Molina | 13.2
TRANSNET | RET001R009SE082T005 | S/E Monte Patria | 13.2 | 1 | 0.01 | 0.93 | 872 | 931 | 55% | 1 | 0.01 | 0.96 | 655 | 663 | 41% | 2010-05-10 | 9:08
TRANSNET | RET018R015SE082T005 | S/E Monte Patria | 23
TRANSNET | RET005A002SE004A002 | S/E Nueva Aldea | 66 | 0 | 0 | 0.96 | 0 | 0 | 0% | 0 | 0 | 0.98 | 0 | 0 | 0% | 2010-05-10 | 9:08
TRANSNET | RET020R015SE071T005 | S/E Ovalle | 23
TRANSNET | RET021R015SE071T005 | S/E Ovalle | 13.2
TRANSNET | RET043R012SE084T005 | S/E Padre Las Casas | 15
TRANSNET | RET022R015SE027T002 | S/E Pan de Azúcar | 13.2
TRANSNET | RET044R012SE086T005 | S/E Panguilemo | 15 | 1 | 0.01 | 0.93 | 911 | 1500 | 45% | 1 | 0.01 | 0.96 | 436 | 539 | 21% | 2010-05-10 | 9:08
TRANSNET | RET045R012SE087T005 | S/E Pelequ | 15
TRANSNET | RET046R012SE088T005 | S/E Penco | 15
TRANSNET | RET047R012SE089T005 | S/E Perales | 15
TRANSNET | RET030R017SE090T005 | S/E Piduco | 15
TRANSNET | RET048R012SE090T005 | S/E Piduco | 15
TRANSNET | RET049R012SE091T005 | S/E Pillanlelb?n | 15 | 1 | 0.01 | 0.93 | 765 | 778 | 30% | 0.94 | 0.01 | 0.96 | 1797 | 1797 | 70% | 2010-05-10 | 9:08
TRANSNET | RET050R012SE117T005 | S/E Pirque | 13.2 | 1 | 0.01 | 0.93 | 758 | 766 | 28% | 0.71 | 0.01 | 0.96 | 1963 | 1963 | 72% | 2010-05-10 | 9:08
TRANSNET | RET051R012SE092T005 | S/E Pitrufqu | 13.2 | 1 | 0.01 | 0.93 | 1695 | 1722 | 59% | 0.61 | 0.01 | 0.96 | 1148 | 1148 | 40% | 2010-05-10 | 9:08
TRANSNET | RET053R012SE083T005 | S/E Pumahue | 15
TRANSNET | RET002R009SE081T005 | S/E Punitaqui | 13.2 | 1 | 0.01 | 0.93 | 722 | 729 | 27% | 1 | 0.01 | 0.96 | 1163 | 1972 | 43% | 2010-05-10 | 9:08
TRANSNET | RET024R015SE051T005 | S/E Qu?nquimo | 23
TRANSNET | RET001R012SE154T005 | S/E Quinta de Tilcoco | 15
TRANSNET | RET007R005SE008T005 | S/E Rauqu | 13.2
TRANSNET | RET056R012SE052T005 | S/E Rengo | 15
TRANSNET | RET069R005SE053T005 | S/E Salamanca | 23
TRANSNET | RET002L040SE055T005 | S/E San Francisco de Mostazal | 15
TRANSNET | RET003L040SE055T005 | S/E San Francisco de Mostazal | 15
TRANSNET | RET001L040SE055T005 | S/E San Francisco de Mostazal | 15
TRANSNET | RET058R012SE055T005 | S/E San Francisco de Mostazal | 15
TRANSNET | RET057R012SE055T005 | S/E San Francisco de Mostazal | 15
TRANSNET | RET025R015SE056T005 | S/E San Joaqu?n (C.G.E.) | 13.2
TRANSNET | RET002R015SE056T005 | S/E San Joaqu?n (C.G.E.) | 13.2
TRANSNET | RET058R012SE057T005 | S/E San Miguel | 15 | 1 | 0.04 | 0.93 | 19 | 20 | 1% | 0.95 | 0.01 | 0.96 | 1851 | 1851 | 99% | 2010-05-10 | 9:08
TRANSNET | RET001L041SE120T005 | S/E San Pedro (C.G.E.) | 15
TRANSNET | RET060R012SE059T005 | S/E San Vicente de Tagua Tagua | 15
TRANSNET | RET002R012SE059T005 | S/E San Vicente de Tagua Tagua | 15
TRANSNET | RET002R012SE048T005 | S/E Santa Elvira | 15
TRANSNET | RET062R012SE061T005 | S/E Talca | 15
TRANSNET | RET063R012SE061T005 | S/E Talca | 15
TRANSNET | RET063R012SE062T005 | S/E Talcahuano | 15
TRANSNET | RET002R012SE062T005 | S/E Talcahuano | 15
TRANSNET | RET064R012SE127T005 | S/E Teno | 15