## Informe CT 15 min Feb-2012
RESUMEN CONTROL DE TENSIÓN ARTÍCULO 6-17 NORMA TÉCNICA MES DE FEBRERO DE 2012
Empresa | Clave | Retiro | Tensión | Tensión | Máximo | Mínimo | Permitido | Permitido | Intervalos Fuera de | Total | Intervalos Fuera de | Fecha | Hora
|  |  | Nominal | Servicio |  |  | Max | Min | Rango | Intervalos | Rango
|  |  | [kV] | [kV] |  |  | [p.u.] | [p.u.]
C. MIN. C. DE ANDACOLLO | RET001L059SE001L059 | MIN. C. DE ANDACOLLO - S/E Minera Carmen de Andacollo | 110 | 111 | 1.07 | 1 | 1.08 | 0.94 | 0 | 2784 | 0% | 2012-03-20 | 12:36
C. MIN. C. DE ANDACOLLO | RET002L059SE001L059 | S/E Minera Carmen de Andacollo 220 kV | 220 | 226 | 1.09 | 1.01 | 1.08 | 0.98 | 118 | 2784 | 4% | 2012-03-20 | 12:36
C. Min. Cerro Negro | RET001L072SE001L072 | S/E Los Angeles | 44 | 44 | 1.07 | 0.83 | 1.07 | 0.93 | 1601 | 2768 | 58% | 2012-10-30 | 21:13
C. MIN. DEL PACIFICO | RET001L018SE004L018 | Algarrobo - S/E Algarrobo | 110 | 111 | 1.03 | 1.01 | 1.08 | 0.94 | 0 | 2784 | 0% | 2012-04-15 | 23:54
C. MIN. DEL PACIFICO | RET001L018SE007L018 | CMP - S/E Magnetita | 110 | 111 | 1.02 | 1 | 1.08 | 0.94 | 0 | 2784 | 0% | 2012-04-15 | 23:54
C. MIN. DEL PACIFICO | RET004L018SE001L018 | Los Colorados - S/E Los Colorados | 110 | 111 | 1.03 | 1.01 | 1.08 | 0.94 | 0 | 2784 | 0% | 2012-04-15 | 23:54
C. MIN. DEL PACIFICO | RET002L018SE002L018 | Pellets - S/E Pellets | 110 | 111 | 1.01 | 0.99 | 1.08 | 0.94 | 0 | 2783 | 0% | 2012-04-15 | 23:54
C. MIN. DEL PACIFICO | RET003L018SE006L018 | Romeral - S/E Romeral | 110 | 111 | 1.04 | 1.02 | 1.08 | 0.94 | 0 | 2784 | 0% | 2012-04-15 | 23:54
C. MIN. DOS AMIGOS (CEMIN) | RET001L023SE015T002 | CEMIN - S/E Dos Amigos | 23 | 23
C. MIN. LA CANDELARIA | RET001L057SE001L057 | MIN. LA CANDELARIA - S/E Candelaria | 220 | 226
C. MIN. MANTOS DE ORO | RET001L053SE001L053 | MIN. MANTOS DE ORO - S/E La Coipa | 220 | 224
C. MIN. OJOS DEL SALADO | RET001L052SE001L057 | MIN. OJOS DEL SALADO - S/E Candelaria | 23 | 23
C. MIN. PELAMBRES | RET001L051SE025T002 | MIN. PELAMBRES-L.Vilos - S/E Los Vilos | 220 | 226 | 1.08 | 0.47 | 1.08 | 0.98 | 52 | 2656 | 2% | 2012-01-17 | 9:27
C. MIN. PELAMBRES | RET001L051SE001L051 | MIN. PELAMBRES-Quillota - S/E Quillota | 220 | 226 | 1.07 | 0.73 | 1.08 | 0.98 | 2 | 2616 | 0% | 2012-01-17 | 9:27
C. MIN. REFUGIO | RET001L050SE001L050 | MIN. MARICUNGA - S/E Cardones | 110 | 111
C. MIN. VALLE CENTRAL | RET001L049SE002L049 | MIN. VALLE CENTRAL - S/E Minera Valle Central | 154 | 156 | 1.04 | 0.35 | 1.08 | 0.94 | 2 | 2743 | 0% | 2012-04-17 | 9:53
CAP | RET001L029SE001L029 | CAP Huachipato - S/E San Vicente | 154 | 156 | 1.04 | 1 | 1.08 | 0.94 | 0 | 2784 | 0% | 2012-05-09 | 15:22
CAP | RET001L028SE001L028 | CAP Rengo - S/E Indac | 154 | 156
CELULOSA ARAUCO | RET001G026SE001G002 | Arauco- Arauco - S/E Horcones | 66 | 67 | 1.06 | 0.99 | 1.09 | 0.94 | 0 | 2784 | 0% | 2013-03-11 | 17:20
CELULOSA ARAUCO | RET001G026SE001G026 | Arauco- Constitución - S/E Constitución | 66 | 67 | 1.11 | 0.88 | 1.09 | 0.94 | 349 | 2784 | 13% | 2013-03-11 | 17:20
CELULOSA ARAUCO | RET001G026SE004G026 | Arauco- Itata - S/E Santa Elvira | 66 | 67 | 1.05 | 1.02 | 1.09 | 0.94 | 0 | 2784 | 0% | 2013-03-11 | 17:20
CELULOSA ARAUCO | RET001G026SE018R017 | Arauco- Licantén - S/E Licantén | 66 | 67 | 1.04 | 0.29 | 1.09 | 0.94 | 2 | 2783 | 0% | 2013-03-11 | 17:20
CELULOSA ARAUCO | RET001G026SE003G026 | Arauco- Valdivia - S/E Los Ciruelos | 220 | 228 | 1.08 | 1.04 | 1.09 | 0.98 | 0 | 2784 | 0% | 2013-03-11 | 17:20
CELULOSA ARAUCO | RET001L046SE007R017 | Aserraderos Arauco - S/E Constitución | 23 | 23
CELULOSA ARAUCO | RET001G024SE001G002 | PANELES ARAUCO - S/E Cholguan | 66 | 67 | 1.1 | 0.95 | 1.09 | 0.94 | 60 | 2784 | 2% | 2013-03-11 | 17:20
CELULOSA ARAUCO | RET001G024SE004G026 | PANELES ARAUCO - S/E Nueva Aldea | 66 | 67 | 1.05 | 1.02 | 1.09 | 0.94 | 0 | 2784 | 0% | 2013-03-11 | 17:20
CEM. BIO BIO | RET001L024SE001L024 | CEMENTO BIO BIO - S/E Cementos Bío Bío | 66 | 67 | 1.07 | 1.02 | 1.09 | 0.94 | 0 | 2784 | 0% | 2012-03-01 | 10:33
CEM. MELON | RET001L026SE001L026 | CEMENTO MELON - S/E Calera Centro 6 | 62.5 | 62.5 | 1.03 | 0.93 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-15 | 8:29
CEM. POLPAICO | RET001L025SE001L025 | CEMENTO POLPAICO - S/E Polpaico | 110 | 111
Chilquinta | RET001R003SE007R003 | Concón | 12 | 12 | 1.05 | 1.01 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-15 | 10:22
Chilquinta | RET001R003SE010R003 | La Calera | 12 | 12 | 1.04 | 0.97 | 1.07 | 0.93 | 0 | 2658 | 0% | 2012-03-15 | 10:22
Chilquinta | RET001R003SE021R003 | Las Vegas | 12 | 12
Chilquinta | RET001R017SE002R017 | Melipilla | 13.2 | 13.2 | 1.04 | 1 | 1.08 | 0.94 | 0 | 2757 | 0% | 2012-03-15 | 10:22
Chilquinta | PA03R003SE003R003 | Melipilla Chilquinta | 12 | 12
Chilquinta | RET001R003SE013R003 | Miraflores | 12 | 12 | 1.04 | 1 | 1.07 | 0.93 | 0 | 2683 | 0% | 2012-03-15 | 10:22
Chilquinta | RET001R003SE046R003 | Quintero | 12 | 12
Chilquinta | RET001R003SE020R003 | San Felipe | 12 | 12
Chilquinta | BA01T001SE021R003 | San Luis | 220 | 228
Chilquinta | RET001R003SE007G010 | San Pedro | 12 | 12
Chilquinta | RET001R003SE022R003 | San Rafael | 12 | 12
Chilectra | RET001R002SE001R002 | Alonso de Córdova B1 | 12 | 12 | 1 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE001R002 | Alonso de Córdova B2 | 12 | 12 | 0.99 | 0.96 | 1.07 | 0.93 | 0 | 2783 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE001R002 | Alonso de Córdova B3 | 12 | 12
Chilectra | RET001R002SE002R002 | Altamirano B1 | 12 | 12 | 1 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE002R002 | Altamirano B2 | 12 | 12 | 1.01 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE003R002 | Andes B1 | 12 | 12 | 1 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE003R002 | Andes B2 | 12 | 12 | 1.01 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE004R002 | Apoquindo B1 | 12 | 12 | 1.04 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE004R002 | Apoquindo B2 | 12 | 12 | 1 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE004R002 | Apoquindo B3 | 12 | 12
Chilectra | RET001R002SE005R002 | Batuco 23KV B1 | 23 | 23 | 1.03 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE005R002 | Batuco 23KV B2 | 23 | 23 | 1 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET002R002SE005R002 | Batuco 23KV B3 | 23 | 23 | 0.99 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE085R002 | Bicentenario B1 | 12 | 12
Chilectra | RET001R002SE006R002 | Brasil B1 | 12 | 12 | 1.02 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET002R002SE006R002 | Brasil B2 | 12 | 12 | 1.03 | 0.99 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE007R002 | Buin | 220 | 224 | 1.06 | 1.01 | 1.07 | 0.97 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE008R002 | Carrascal B1 | 12 | 12 | 1.05 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE008R002 | Carrascal B2 | 12 | 12 | 1.03 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET002R002SE008T002 | Cerro Navia-Las Vegas | 110 | 111 | 1.06 | 1.04 | 1.08 | 0.94 | 0 | 39 | 0% | 2012-03-16 | 11:48
Chilectra | BA01R002SE008T002 | Cerro Navia1 (Hyundai) | 110 | 111 | 1.03 | 0.97 | 1.08 | 0.94 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | BA02T002SE008T002 | Cerro Navia2 (Jeumont) | 110 | 111 | 1.03 | 0.96 | 1.08 | 0.94 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE009R002 | Chacabuco 23KV B2 | 23 | 23 | 1 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE009R002 | Chacabuco 23KV B3 | 23 | 23 | 1 | 0.97 | 1.07 | 0.93 | 0 | 2745 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE009R002 | Chacabuco B1 | 12 | 12 | 1.04 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET02R002SE010R002 | Chena 220 | 220 | 224
Chilectra | RET001R002SE016R002 | Cisterna B1 | 12 | 12 | 1 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE016R002 | Cisterna B2 | 12 | 12 | 1.04 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE016R002 | Cisterna B3 | 12 | 12 | 1 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE011R002 | Club Hípico B1 | 12 | 12 | 1.05 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET002R002SE011R002 | Club Hípico B2 | 12 | 12 | 1 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE011R002 | Club Hípico B3 | 12 | 12 | 0.99 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET005R002SE011R002 | Club Hípico B4 | 12 | 12
Chilectra | RET001R002SE012R002 | Curacaví Curacaví | 12 | 12 | 1.07 | 0.96 | 1.07 | 0.93 | 0 | 2780 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE012R002 | Curacaví Lolenco | 12 | 12 | 1.09 | 0.97 | 1.07 | 0.93 | 104 | 2781 | 4% | 2012-03-16 | 11:48
Chilectra | RET004R002SE013R002 | El Manzano B4 | 23 | 23
Chilectra | RET001R002SE017R002 | La Dehesa B1 | 12 | 12 | 1 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET002R002SE017R002 | La Dehesa B2 | 12 | 12 | 1 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE017R002 | La Dehesa B3 | 12 | 12 | 1 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE018R002 | La Pintana B1 | 12 | 12 | 0.99 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE018R002 | La Pintana B2 | 12 | 12 | 1 | 0.99 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE019R002 | La Reina B1 | 12 | 12 | 1.07 | 1.01 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET002R002SE019R002 | La Reina B2 | 12 | 12 | 1 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE019R002 | La Reina B3 | 12 | 12
Chilectra | RET003R002SE019R002 | La Reina B4 | 12 | 12 | 1 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE020R002 | Lampa | 220 | 224 | 1.06 | 1 | 1.07 | 0.97 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET002R002SE020R002 | Lampa 23KV | 23 | 23 | 1.03 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE020R002 | Lampa 23KV | 23 | 23 | 1.08 | 0.87 | 1.07 | 0.93 | 59 | 2784 | 2% | 2012-03-16 | 11:48
Chilectra | RET001R002SE021R002 | Las Acacias 23KV B1 | 23 | 23 | 1 | 0.95 | 1.07 | 0.93 | 0 | 2649 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE021R002 | Las Acacias B2 | 23 | 23
Chilectra | RET004R002SE021R002 | Las Acacias 23 kV B3 | 23 | 23
Chilectra | RET001R002SE022R002 | Lo Aguirre B1 | 110 | 111 | 1.03 | 0.96 | 1.08 | 0.94 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE023R002 | Lo Boza B1 | 12 | 12 | 1.01 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE023R002 | Lo Boza B2 | 12 | 12 | 1.04 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE023R002 | Lo Boza B3 | 12 | 12
Chilectra | RET005R002SE023R002 | Lo Boza B4 | 12 | 12 | 1.04 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE026R002 | Lo Valledor B1 | 12 | 12 | 1.02 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE026R002 | Lo Valledor B2 | 12 | 12 | 1.03 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE026R002 | Lo Valledor B3 | 12 | 12 | 1.02 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE027R002 | Lord Cochrane B1 | 12 | 12 | 1.01 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE027R002 | Lord Cochrane B2 | 12 | 12 | 1.02 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE028R002 | Los Almendros 110 kV | 110 | 111
Chilectra | RET001R002SE029R002 | Los Domínicos B1 | 12 | 12 | 1.03 | 1.01 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE029R002 | Los Domínicos B2 | 12 | 12 | 1.09 | 0.97 | 1.07 | 0.93 | 79 | 2784 | 3% | 2012-03-16 | 11:48
Chilectra | RET002R002SE030R002 | Macul 20KV B4 | 20 | 20 | 0.97 | 0.92 | 1.07 | 0.93 | 28 | 2784 | 1% | 2012-03-16 | 11:48
Chilectra | RET005R002SE030R002 | Macul B3 | 12 | 12 | 0.99 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET006R002SE030R002 | Macul TR06 (Metro) | 20 | 20
Chilectra | RET002R002SE031R002 | Maipú B1 | 12 | 12 | 1.02 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE031R002 | Maipú B2 | 12 | 12 | 1.05 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE031R002 | Maipú B3 | 12 | 12 | 1.05 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE032R002 | Malloco 23KV B3 | 23 | 23 | 1.04 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE032R002 | Malloco B1 | 12 | 12 | 1.03 | 0.94 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE032R002 | Malloco B2 | 12 | 12 | 1.04 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE033R002 | Ochagavía B2 | 12 | 12 | 1.02 | 0.96 | 1.07 | 0.93 | 0 | 2758 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE034R002 | Pajaritos B1 | 12 | 12 | 1.01 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE034R002 | Pajaritos B2 | 12 | 12 | 1.03 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE034R002 | Pajaritos B3 | 12 | 12
Chilectra | RET001R002SE035R002 | Panamericana B1 | 12 | 12 | 1 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE035R002 | Panamericana B2 | 12 | 12 | 1.06 | 0.93 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET002R002SE089R002 | Polpaico | 220 | 224 | 1.06 | 1.03 | 1.07 | 0.97 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE089R002 | Polpaico 23KV B1 | 23 | 23 | 1.03 | 0.94 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE036R002 | Pudahuel B1 | 12 | 12 | 1.04 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE036R002 | Pudahuel B2 | 12 | 12 | 1.04 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET002R002SE037R002 | Quilicura B1 | 12 | 12 | 1 | 0.93 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE037R002 | Quilicura B2 | 12 | 12 | 1.02 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE037R002 | Quilicura B3 | 12 | 12 | 1.01 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET005R002SE037R002 | Quilicura B4 | 12 | 12 | 1.06 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE038R002 | Recoleta B1 | 12 | 12 | 1.01 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE038R002 | Recoleta B2 | 12 | 12 | 1 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE038R002 | Recoleta B4 | 12 | 12 | 1.06 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE088R002 | Rungue 23KV | 23 | 23 | 1.07 | 0.94 | 1.07 | 0.93 | 0 | 2762 | 0% | 2012-03-16 | 11:48
Chilectra | RET002R002SE040R002 | San Bernardo B1 | 12 | 12 | 1.04 | 0.94 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE040R002 | San Bernardo B2 | 12 | 12 | 1.04 | 0.93 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE040R002 | San Bernardo B3 | 12 | 12 | 1.04 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET002R002SE041R002 | San Cristóbal B1 | 12 | 12 | 1.04 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE041R002 | San Cristóbal B2 | 12 | 12 | 1.05 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE041R002 | San Cristóbal B3 | 12 | 12 | 1.09 | 0.97 | 1.07 | 0.93 | 114 | 2784 | 4% | 2012-03-16 | 11:48
Chilectra | RET005R002SE041R002 | San Cristóbal B4 | 12 | 12
Chilectra | RET002R002SE042R002 | San Joaquín B1 | 12 | 12 | 1 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE042R002 | San Joaquín B2 | 12 | 12 | 1.02 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE042R002 | San Joaquín B3 | 12 | 12 | 1.03 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET005R002SE042R002 | San Joaquín B4 | 12 | 12 | 1.06 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE043R002 | San José B1 | 12 | 12 | 1.06 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE043R002 | San José B2 | 12 | 12 | 1.01 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE043R002 | San José B3 | 12 | 12 | 1.06 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET005R002SE043R002 | San José B4 | 12 | 12
Chilectra | RET002R002SE044R002 | San Pablo 23KV B1 | 23 | 23 | 1 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE044R002 | San Pablo 23KV B2 | 23 | 23 | 1 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET002R002SE045R002 | Santa Elena B1 | 12 | 12 | 1.09 | 1.02 | 1.07 | 0.93 | 73 | 2783 | 3% | 2012-03-16 | 11:48
Chilectra | RET003R002SE045R002 | Santa Elena B2 | 12 | 12 | 1.01 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE045R002 | Santa Elena B3 | 12 | 12 | 1.05 | 0.99 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET005R002SE045R002 | Santa Elena B4 | 12 | 12 | 1 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET002R002SE046R002 | Santa Marta 23KV B3 | 23 | 23 | 1.06 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET005R002SE046R002 | Santa Marta 23 kV B4 | 23 | 23
Chilectra | RET003R002SE046R002 | Santa Marta B1 | 12 | 12 | 1.03 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE046R002 | Santa Marta B2 | 12 | 12 | 1 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE047R002 | Santa Raquel B1 | 12 | 12 | 1 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE047R002 | Santa Raquel B2 | 12 | 12 | 1 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE047R002 | Santa Raquel B4 | 12 | 12 | 0.98 | 0.91 | 1.07 | 0.93 | 87 | 2784 | 3% | 2012-03-16 | 11:48
Chilectra | RET005R002SE047R002 | Santa Raquel B5 | 12 | 12
Chilectra | RET001R002SE048R002 | Santa Rosa B1 | 12 | 12 | 1.02 | 0.99 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE048R002 | Santa Rosa B2 | 12 | 12 | 1.01 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE048R002 | Santa Rosa B3 | 12 | 12 | 1 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET002R002SE048R002 | Santa Rosa B4 Sur | 12 | 12 | 1.05 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE013R002 | T1 El Manzano | 23 | 23 | 1 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET002R002SE013R002 | T2 El Manzano | 23 | 23 | 1.04 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET001R002SE049R002 | Vitacura B1 | 12 | 12 | 0.99 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET002R002SE049R002 | Vitacura B2 | 12 | 12 | 1 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET003R002SE049R002 | Vitacura B3 | 12 | 12 | 0.99 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
Chilectra | RET004R002SE049R002 | Vitacura B4 | 12 | 12 | 1 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 11:48
CMPC | RET007L021SE038T002 | CMPC Cart- CHUMPULLO - S/E Chumpull | 6 | 6 | 1.14 | 0.26 | 1.07 | 0.93 | 2774 | 2775 | 100% | 2012-07-10 | 17:23
CMPC | RET006L021SE003G004 | CMPC Cart- MAULE - S/E Colbún | 220 | 226 | 1.02 | 0.96 | 1.08 | 0.98 | 65 | 2784 | 2% | 2012-05-10 | 11:31
CMPC | RET002L021SE008L021 | CMPC Cel- CELPAC - S/E Charrúa | 220 | 226 | 1.06 | 0.48 | 1.08 | 0.98 | 2 | 2927 | 0% | 2012-03-10 | 10:24
CMPC | RET001L021SE005L021 | CMPC Cel- LAJA - S/E Charrúa | 220 | 226 | 1.06 | 0.48 | 1.08 | 0.98 | 2 | 2927 | 0% | 2012-03-10 | 10:24
CMPC | RET003L021SE002L021 | CMPC Cel- SANTA FE - S/E Charrúa | 220 | 226 | 1.06 | 0.48 | 1.08 | 0.98 | 2 | 2927 | 0% | 2012-03-10 | 10:24
CMPC | RET001L021SE002G025 | CMPC Maderas Aserradero Bucalemu - S/E Bucalemu | 13 | 13 | 1.02 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-07-13 | 9:48
CMPC | RET005L021SE004L021 | CMPC-CORDILLERA - S/E Maipo | 110 | 111
CMPC | RET004L021SE007L021 | CMPC-INFORSA - S/E Charrúa | 220 | 226 | 1.06 | 0.48 | 1.08 | 0.98 | 2 | 2927 | 0% | 2012-03-10 | 10:24
CODELCO | RET001L020SE002G013 | CODELCO A-Polpaico - S/E El Llano | 220 | 224 | 1.06 | 1.03 | 1.07 | 0.97 | 0 | 2770 | 0% | 2012-05-14 | 15:49
CODELCO | RET001L020SE003L020 | CODELCO A-Saladillo - S/E Saladillo | 66 | 67 | 1.05 | 1.02 | 1.09 | 0.94 | 0 | 2770 | 0% | 2012-05-14 | 15:49
CODELCO | RET001L020SE005L020 | CODELCO Salvador - S/E Diego de Almagro | 110 | 111 | 1.03 | 1.01 | 1.08 | 0.94 | 0 | 2784 | 0% | 2012-03-06 | 10:43
CODELCO | RET001L020SE002L020 | CODELCO T-Candelaria - S/E Candelaria | 220 | 226 | 1.02 | 0.96 | 1.08 | 0.98 | 219 | 2784 | 8% | 2012-06-25 | 10:16
CODELCO | RET001L020SE009L020 | CODELCO Ventanas - S/E Tap Enami | 110 | 111 | 1.05 | 1.02 | 1.08 | 0.94 | 0 | 2784 | 0% | 2012-03-02 | 16:37
CODELCO | RET001L020SE002G015 | S/E Los Maquis | 220 | 224 | 215.99 | 0.98 | 1.07 | 0.97 | 3 | 2770 | 0% | 2012-05-14 | 15:49
CODINER | RET001R019SE058T005 | Lautaro | 13.2 | 13.2 | 107 | 97 | 1.07 | 0.93 | 2784 | 2784 | 100% | 2012-03-06 | 12:06
CODINER | RET001R004SE129T005 | Loncoche | 13.2 | 13.2 | 108 | 94 | 1.07 | 0.93 | 2784 | 2784 | 100% | 2012-03-06 | 12:06
CODINER | RET001R004SE092T005 | Pitrufquén | 13.2 | 13.2 | 102 | 89 | 1.07 | 0.93 | 2784 | 2784 | 100% | 2012-03-06 | 12:06
CODINER | RET001R004SE037T002 | Temuco | 23 | 23 | 106 | 98 | 1.07 | 0.93 | 2784 | 2784 | 100% | 2012-03-06 | 12:06
CODINER | RET001R004SE064T005 | Traiguén | 13.2 | 13.2 | 108 | 92 | 1.07 | 0.93 | 2779 | 2779 | 100% | 2012-03-06 | 12:06
CODINER | RET001R019SE068T005 | Victoria | 13.2 | 13.2 | 108 | 95 | 1.07 | 0.93 | 2783 | 2783 | 100% | 2012-03-06 | 12:06
COELCHA | RET001R006SE003R019 | Cabrero (SGA) | 13.2 | 13.2 | 1.03 | 0.95 | 1.07 | 0.93 | 0 | 2783 | 0% | 2012-04-23 | 11:34
COELCHA | RET001R006SE004T003 | Cholguán (SGA) | 13.2 | 13.2 | 1.03 | 1 | 1.07 | 0.93 | 0 | 2783 | 0% | 2012-04-23 | 11:34
COOP. CURICO (CEC) | RET001R007SE001R007 | Curicó T4 | 13.2 | 13.2 | 0.98 | 0.32 | 1.07 | 0.93 | 1 | 2784 | 0% | 2012-03-05 | 15:33
COOP. CURICO (CEC) | RET001R007SE126T005 | Quinta | 66 | 67 | 1.06 | 1.01 | 1.09 | 0.94 | 0 | 2784 | 0% | 2012-03-05 | 15:33
COOP. CURICO (CEC) | RET001R007SE127T005 | Teno | 13.2 | 13.2 | 1 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-05 | 15:33
COOPELAN | RET002R011SE076T005 | Canteras | 13.2 | 13.2
COOPELAN | RET004R011SE076T005 | Huaqui | 13.2 | 13.2
COOPELAN | RET001R019SE076T005 | Los Angeles | 13.2 | 13.2 | 1.04 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:46
COOPELAN | RET003R011SE076T005 | Santa Fe | 13.2 | 13.2
COOPREL | RET001R025SE012T003 | La Unión | 13.2 | 13.2 | 1.04 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-05 | 10:10
COOPREL | RET001R008SE001G008 | Pilmaiquén | 13.2 | 13.2 | 1.07 | 0.99 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-05 | 10:10
COPELEC | RET002R013SE001R013 | Quilmo 66 KV | 13 | 13
CRELL | RET001R010SE021T003 | CRELL | 13.2 | 13.2 | 1.05 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-16 | 15:45
Divisiones AngloAmerican | RET001L054SE001L054 | MANTO VERDE-Almagro - S/E Diego de Almagro | 110 | 111
Divisiones AngloAmerican | RET001L054SE002L054 | MANTO VERDE-Impulsion - S/E Impulsión | 23 | 23
Divisiones AngloAmerican | RET001L008SE002L008 | MSA-CHAGRES - S/E Chagres | 110 | 111
Divisiones AngloAmerican | RET001L061SE001L061 | MSA-EL SOLDADO - S/E La Calera | 110 | 111 | 1.04 | 0.97 | 1.08 | 0.94 | 0 | 2784 | 0% | 2012-03-08 | 8:34
Divisiones AngloAmerican | RET001L022SE004G010 | MSA-LOS BRONCES - S/E Polpaico | 220 | 224 | 1.04 | 1.01 | 1.07 | 0.97 | 0 | 2784 | 0% | 2012-04-24 | 14:05
E. E. LITORAL | RET001R020SE005R020 | S/E El Totoral | 12 | 12 | 1.04 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-05 | 11:08
E. E. LITORAL | RET001R020SE001R020 | SPD Las Balandras | 12 | 12 | 1.04 | 1.01 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-05 | 11:08
E. E. LITORAL | RET001R020SE002R020 | SPD Las Piñatas | 12 | 12 | 1.05 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-05 | 11:08
E. E. LITORAL | RET001R020SE003R020 | SPD San Jerónimo | 12 | 12 | 1.05 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-05 | 11:08
E. E. PUENTE ALTO | RET004R026SE018R002 | Pintana T4 | 110 | 111 | 1.03 | 0.98 | 1.08 | 0.94 | 0 | 2784 | 0% | 2012-03-14 | 15:23
E. E. PUENTE ALTO | RET001R026SE003R026 | Vizcachas | 110 | 111 | 1.04 | 0.99 | 1.08 | 0.94 | 0 | 2784 | 0% | 2012-03-14 | 15:23
EKA CHILE | RET001L015SE001L015 | EKA - S/E San Vicente | 154 | 156 | 1.04 | 1 | 1.08 | 0.94 | 0 | 2784 | 0% | 2012-03-14 | 18:55
ELECDA | RET001R001SE001R001 | Diego de Almagro | 110 | 111
EMELAT | RET001R016SE001R016 | S/E Caldera | 23 | 23 | 1.01 | 0.95 | 1.07 | 0.93 | 0 | 2782 | 0% | 2012-09-13 | 17:57
EMELAT | RET002R016SE002R016 | S/E Cerrillos | 23 | 23 | 1.03 | 0.99 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-13 | 17:57
EMELAT | RET001R016SE004R016 | S/E Copiapó | 13.8 | 13.8 | 1 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-13 | 17:57
EMELAT | RET002R016SE004R016 | S/E Copiapó CT4 | 13.8 | 13.8 | 0.99 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-13 | 17:57
EMELAT | RET001R016SE014T002 | S/E Diego De Almagro | 23 | 23
EMELAT | RET001R016SE005R016 | S/E Hernán Fuentes | 23 | 23 | 1.04 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-13 | 17:57
EMELAT | RET001R016SE019T002 | S/E Huasco | 13 | 13
EMELAT | RET001R016SE017T005 | S/E Incahuasi | 23 | 23
EMELAT | RET001R016SE006R016 | S/E Los Loros | 23 | 23 | 1.03 | 0.98 | 1.07 | 0.93 | 0 | 2768 | 0% | 2012-09-13 | 17:57
EMELAT | RET001R016SE007R016 | S/E Plantas | 23 | 23 | 1 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-13 | 17:57
EMELAT | RET001R016SE008R016 | S/E Tierra Amarilla | 23 | 23 | 1.03 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-13 | 17:57
EMELAT | RET002R016SE008R016 | S/E Tierra Amarilla ET2 | 23 | 23 | 1.04 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-13 | 17:57
EMELAT | RET001R016SE039T002 | Vallenar 13.2 | 13.2 | 13.2 | 0.98 | 0.38 | 1.07 | 0.93 | 2 | 2779 | 0% | 2012-09-13 | 17:57
ENAMI - H. V. LIRA | RET001L030SE001L030 | ENAMI - Fundicion Paipote - S/E H. Videla L. | 110 | 111 | 1.03 | 0.99 | 1.08 | 0.94 | 0 | 2784 | 0% | 2012-03-06 | 10:18
ENAMI - H. V. LIRA | RET001L030SE004G011 | ENAMI - Planta Matta - S/E Pta. Matta | 110 | 111 | 1.03 | 0.99 | 1.08 | 0.94 | 0 | 2784 | 0% | 2012-03-06 | 10:18
ENAP REFINERIAS | RET001L002SE007R003 | ENAP ACONCAGUA - S/E Miraflores Barra | 110 | 111
ENAP REFINERIAS | RET001L034SE001L034 | ENAP BIO BIO - S/E Petrox | 66 | 67
FFCC | RET001L011SE003L011 | EFE - Curicó - S/E Curicó | 66 | 67
FFCC | RET002L011SE007L011 | EFE - Jahuel 66 KV - S/E Jahuel | 66 | 67
FFCC | RET003L011SE008L011 | EFE - Laja - S/E Laja | 66 | 67
FFCC | RET005L011SE010L011 | EFE - Monte Aguila - S/E Charrua | 66 | 67
FFCC | RET006L011SE011L011 | EFE - San Fernando - S/E San Fernando | 66 | 67
Forestal y Papelera Concepción | RET001G032SE001G032 | FPC - S/E Fopaco | 154 | 156
frontel | BA01T002SE001G021 | ABANICO | 13.2 | 13.2 | 1.04 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET002R019SE028T005 | ANGOL 13.2 | 13.2 | 13.2 | 1.02 | 0.93 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET001R019SE028T005 | ANGOL 23 | 23 | 23 | 1.05 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET001R019SE003R019 | CABRERO | 23 | 23 | 1.03 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET001R019SE009R019 | CAÑETE 23 kV | 23 | 23
frontel | RET001R019SE033T005 | CARAMPANGUE | 23 | 23 | 1.04 | 0.55 | 1.07 | 0.93 | 1 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET001R019SE004T003 | CHOLGUAN | 13.2 | 13.2 | 1.03 | 1 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET001R019SE043T005 | COLLIPULLI | 13.2 | 13.2 | 1.07 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET001R019SE142T005 | CORONEL | 15 | 15 | 1.01 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET001R019SE013T005 | CURACAUTIN | 13.2 | 13.2 | 1.1 | 0.95 | 1.07 | 0.93 | 79 | 2769 | 3% | 2012-03-20 | 15:46
frontel | RET001R019SE036T005 | CURANILAHUE 13.2 | 13.2 | 13.2 | 1.05 | 0.93 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET002R019SE036T005 | CURANILAHUE 23 | 23 | 23 | 1.13 | 0.53 | 1.07 | 0.93 | 934 | 2784 | 34% | 2012-03-20 | 15:46
frontel | RET001R019SE004R019 | ENACAR | 13.2 | 13.2 | 1.04 | 0.52 | 1.07 | 0.93 | 1 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET001R019SE022T002 | LAJA | 13.2 | 13.2 | 1.08 | 1 | 1.07 | 0.93 | 20 | 2784 | 1% | 2012-03-20 | 15:46
frontel | RET001R019SE058T005 | LAUTARO | 13.2 | 13.2 | 107 | 97 | 1.07 | 0.93 | 2784 | 2784 | 100% | 2012-03-06 | 12:06
frontel | RET002R019SE058T005 | LAUTARO 23 | 23 | 23 | 1.06 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET001R019SE011T005 | LEBU | 13.2 | 13.2 | 1.09 | 0.92 | 1.07 | 0.93 | 12 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET002R019SE001R019 | LICANCO | 23 | 23 | 1.05 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET001R019SE076T005 | LOS ANGELES | 13.2 | 13.2 | 1.04 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET001R019SE005R019 | LOTA | 13.2 | 13.2 | 1.05 | 0.29 | 1.07 | 0.93 | 2 | 2780 | 0% | 2012-03-20 | 15:46
frontel | RET001R019SE002R019 | NEGRETE | 23 | 23 | 1.03 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET001R019SE006R019 | NUEVA IMPERIAL | 23 | 23 | 1 | 0.02 | 1.07 | 0.93 | 6 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET001R019SE091T005 | PILLANLELBUN | 13.2 | 13.2 | 1.07 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET001R019SE092T005 | PITRUFQUEN | 13.2 | 13.2 | 1.02 | 0.92 | 1.07 | 0.93 | 2 | 2784 | 0% | 2012-03-20 | 15:46
frontel | RET001R019SE064T005 | TRAIGUEN | 13.2 | 13.2 | 1.07 | 0.92 | 1.07 | 0.93 | 1 | 2776 | 0% | 2012-03-20 | 15:46
frontel | RET002R019SE065T005 | TRES PINOS 13.2 | 13.2 | 13.2 | 1.1 | 0.98 | 1.07 | 0.93 | 166 | 2784 | 6% | 2012-03-20 | 15:46
frontel | RET001R019SE065T005 | TRES PINOS 23 | 23 | 23 | 1.1 | 0.96 | 1.07 | 0.93 | 143 | 2780 | 5% | 2012-03-20 | 15:46
frontel | RET001R019SE068T005 | VICTORIA | 13.2 | 13.2 | 108 | 95 | 1.07 | 0.93 | 2783 | 2783 | 100% | 2012-03-06 | 12:06
fundtalleres | RET001L064SE033T002 | FUNDICION TALLERES-Maestranza - S/E Maestranza | 66 | 67
Grupo Emel | RET001R017SE001R017 | S/E Alcones | 23 | 23 | 1 | 0.96 | 1.07 | 0.93 | 0 | 2775 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE002R017 | S/E Bajo Melipilla | 13.2 | 13.2 | 1.04 | 1 | 1.08 | 0.94 | 0 | 2757 | 0% | 2012-03-15 | 10:22
Grupo Emel | RET001R017SE003R017 | S/E Bollenar | 13.2 | 13.2 | 1 | 0.96 | 1.07 | 0.93 | 0 | 2755 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE004R017 | S/E Cauquenes | 13.2 | 13.2 | 1.02 | 0.95 | 1.07 | 0.93 | 0 | 2782 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE005R017 | S/E Chocalán | 13.2 | 13.2 | 1.06 | 0.98 | 1.07 | 0.93 | 0 | 2772 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE006R017 | S/E Cocharcas (Emelectric) | 33 | 33 | 1.04 | 1.02 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE007R017 | S/E Constitución | 23 | 23 | 1.06 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE008R017 | S/E El Maitén | 13.2 | 13.2 | 1.03 | 0.98 | 1.07 | 0.93 | 0 | 2746 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE009R017 | S/E El Monte | 13.2 | 13.2 | 1.02 | 0.96 | 1.07 | 0.93 | 0 | 2774 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE010R017 | S/E El Paico | 13.2 | 13.2 | 1.07 | 0.95 | 1.07 | 0.93 | 0 | 2744 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE011R017 | S/E El Peumo | 13.2 | 13.2 | 1.06 | 0.96 | 1.07 | 0.93 | 0 | 2773 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE012R017 | S/E El Retiro | 13.2 | 13.2 | 1.06 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE013R017 | S/E Hualañe | 13.2 | 13.2 | 1.03 | 0.38 | 1.07 | 0.93 | 2 | 2783 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE020T002 | S/E Itahue | 13.2 | 13.2 | 1.06 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE015R017 | S/E La Esperanza (Emelectric) | 13.2 | 13.2 | 1.02 | 0.62 | 1.07 | 0.93 | 1 | 2775 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE036R017 | S/E La Manga | 13.2 | 13.2 | 1.03 | 0.98 | 1.07 | 0.93 | 0 | 2781 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE016R017 | S/E Las Arañas | 13.2 | 13.2 | 1.02 | 0.95 | 1.07 | 0.93 | 0 | 2772 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET004R017SE016R017 | S/E Las Arañas 23 | 23 | 23 | 1.04 | 0.96 | 1.07 | 0.93 | 0 | 2772 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE046R017 | S/E Leyda | 13.2 | 13.2 | 1.02 | 0.99 | 1.07 | 0.93 | 0 | 2757 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET002R017SE018R017 | S/E Licanten | 13.8 | 13.8 | 1.01 | 0.91 | 1.07 | 0.93 | 2 | 2783 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE017R017 | S/E Lihueimo | 13.2 | 13.2 | 1.07 | 1.01 | 1.07 | 0.93 | 0 | 2777 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET002R017SE017R017 | S/E Lihueimo 2 | 13.2 | 13.2 | 1.04 | 0.99 | 1.07 | 0.93 | 0 | 2777 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE019R017 | S/E Mandinga | 13.2 | 13.2 | 1.06 | 0.96 | 1.07 | 0.93 | 0 | 2772 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE020R017 | S/E Marchigüe | 13.2 | 13.2 | 1.06 | 0.98 | 1.07 | 0.93 | 0 | 2778 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE022R017 | S/E Nancagua | 13.2 | 13.2 | 1.06 | 0.99 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE023R017 | S/E Paniahue | 13.2 | 13.2 | 1.04 | 0.98 | 1.07 | 0.93 | 0 | 2779 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE130T005 | S/E Parral | 13.2 | 13.2 | 1.01 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE025R017 | S/E Parronal | 13.2 | 13.2 | 1.02 | 0.97 | 1.07 | 0.93 | 0 | 2783 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE026R017 | S/E Placilla | 13.2 | 13.2 | 1.03 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE039R017 | S/E Quelentaro | 13.2 | 13.2 | 1.04 | 0.98 | 1.07 | 0.93 | 0 | 2780 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE028R017 | S/E San Carlos | 13.2 | 13.2 | 1.03 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE029R017 | S/E San Javier | 23 | 23 | 1.1 | 0.94 | 1.07 | 0.93 | 230 | 2782 | 8% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE030R017 | S/E Santa Rosa | 23 | 23 | 1.03 | 0.99 | 1.07 | 0.93 | 0 | 2772 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE061T005 | S/E Talca | 15 | 15 | 1.06 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE063T005 | S/E Tomé | 23 | 23 | 1.04 | 0.85 | 1.07 | 0.93 | 2 | 2784 | 0% | 2012-09-24 | 10:50
Grupo Emel | RET001R017SE031R017 | S/E Villa Prat | 13.2 | 13.2 | 1.09 | 0.93 | 1.07 | 0.93 | 12 | 2782 | 0% | 2012-09-24 | 10:50
INCHALAM | RET001L005SE035T002 | INCHALAM - S/E San Vicente | 13 | 13
INDURA | RET001L004SE002L004 | Indura - Graneros | 66 | 67
INDURA | RET001L004SE001L004 | Indura - Lirquen | 66 | 67
LUZLINARES y LUZPARRAL | RET003R021SE001R021 | Barrio Industrial | 13.2 | 13.2 | 1.1 | 0.91 | 1.07 | 0.93 | 84 | 2782 | 3% | 2012-03-13 | 18:19
LUZLINARES y LUZPARRAL | RET003R021SE002R021 | Colbún | 13.2 | 13.2 | 1.01 | 0.93 | 1.07 | 0.93 | 0 | 2782 | 0% | 2012-03-13 | 18:19
LUZLINARES y LUZPARRAL | RET002R021SE002R021 | Las Cañas | 23 | 23 | 1.02 | 0.99 | 1.07 | 0.93 | 0 | 2782 | 0% | 2012-03-13 | 18:19
LUZLINARES y LUZPARRAL | RET001R021SE001R021 | Linares Norte | 13.2 | 13.2 | 1.1 | 0.91 | 1.07 | 0.93 | 97 | 2782 | 3% | 2012-03-13 | 18:19
LUZLINARES y LUZPARRAL | RET002R021SE001R021 | Linares Sur | 13.2 | 13.2 | 1.1 | 0.91 | 1.07 | 0.93 | 84 | 2782 | 3% | 2012-03-13 | 18:19
LUZLINARES y LUZPARRAL | RET001R021SE002R021 | Panimávida | 13.2 | 13.2 | 1.01 | 0.94 | 1.07 | 0.93 | 0 | 2782 | 0% | 2012-03-13 | 18:19
LUZLINARES y LUZPARRAL | RET001R021SE003R021 | Yerbas buenas | 13.2 | 13.2
LUZOSORNO | RET001R024SE011T003 | AIHUAPI | 23 | 23 | 1.03 | 0.25 | 1.07 | 0.93 | 2 | 2761 | 0% | 2012-03-21 | 9:43
LUZOSORNO | RET001R008SE012T003 | LA UNION 13.2 | 13.2 | 13.2 | 1.04 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-21 | 9:43
LUZOSORNO | RET002R008SE012T003 | LA UNION 23 | 23 | 23
LUZOSORNO | RET001R008SE007T003 | LOS NEGROS | 23 | 23 | 1.05 | 1 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-21 | 9:43
LUZOSORNO | RET001R024SE016T003 | OSORNO | 23 | 23 | 1.04 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-21 | 9:43
LUZOSORNO | RET001R008SE001G008 | PILMAIQUEN | 13.2 | 13.2 | 1.07 | 0.99 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-05 | 10:10
LUZOSORNO | RET001R024SE022T003 | PURRANQUE | 13.2 | 13.2 | 1.03 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-21 | 9:43
LUZPARRAL | RET003R022SE130T005 | Bullileo | 13.2 | 13.2 | 1.03 | 0.98 | 1.07 | 0.93 | 0 | 2782 | 0% | 2012-03-13 | 18:21
LUZPARRAL | RET001R022SE001R022 | Longaví | 13.2 | 13.2 | 1.04 | 0.96 | 1.07 | 0.93 | 0 | 2782 | 0% | 2012-03-13 | 18:21
LUZPARRAL | RET001R017SE012R017 | Retiro | 13.2 | 13.2 | 1.06 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-24 | 10:50
LUZPARRAL | RET001R017SE028R017 | San Carlos | 13.2 | 13.2 | 1.03 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-09-24 | 10:50
MASISA | RET001L044SE001L044 | MASISA-Mapal - S/E Mapal | 154 | 156
MASISA | RET001L044SE003L044 | MASISA-Masonite - S/E FAM | 66 | 67
MASISA | RET001L044SE007R019 | MASISA-Masonite - S/E MASISA Cabrero | 13.2 | 13.2
mblancos | RET001L064SE001L064 | FUNDICION TALLERES-Rancagua - S/E Rancagua | 13 | 13
METRO | RET002R002SE033R002 | METRO - S/E Ochagavia | 110 | 111 | 1.05 | 0.98 | 1.08 | 0.94 | 0 | 2976 | 0% | 2012-04-15 | 12:39
METRO | RET001L014SE087R002 | METRO - S/E Renca | 110 | 111 | 1.05 | 0.98 | 1.08 | 0.94 | 0 | 2976 | 0% | 2012-04-15 | 12:39
MOLY - COP CHILE | RET001L031SE035T002 | MOLY-COP - S/E San Vicente | 13 | 13 | 1.02 | 0.41 | 1.07 | 0.93 | 1 | 2749 | 0% | 2012-03-13 | 9:00
OXY | RET001L043SE001L043 | OXY - S/E Oxy | 154 | 156 | 1.04 | 1 | 1.08 | 0.94 | 0 | 2785 | 0% | 2012-06-04 | 11:44
PAP. BIO BIO | RET002L041SE001L041 | PAP. BIO BIO - S/E San Pedro | 66 | 67 | 1.01 | 0.97 | 1.09 | 0.94 | 0 | 2784 | 0% | 2012-03-09 | 19:11
PETRODOW | RET001L038SE001L038 | PETRODOW - S/E Petrodow | 154 | 156 | 1.04 | 1 | 1.08 | 0.94 | 0 | 2783 | 0% | 2012-03-07 | 10:34
PETROQUIM | RET001L035SE001L035 | PETROQUIM - S/E Petropower | 66 | 67
SAESA | RET001R024SE011T003 | AIHUAPI | 23 | 23 | 1.03 | 0.25 | 1.07 | 0.93 | 2 | 2761 | 0% | 2012-03-21 | 9:43
SAESA | RET001R024SE002T003 | ANCUD | 23 | 23 | 1.07 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE027T003 | CALBUCO | 23 | 23 | 1.02 | 0.64 | 1.07 | 0.93 | 1 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET002R024SE005T003 | CHONCHI | 23 | 23 | 1.06 | 0.93 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE006T003 | COLACO | 23 | 23 | 1.04 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE001T003 | CORRAL | 13.2 | 13.2 | 1.05 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET003R024SE001G033 | DEGAN | 23 | 23 | 1.08 | 0.97 | 1.07 | 0.93 | 16 | 2784 | 1% | 2012-03-20 | 15:26
SAESA | RET001R024SE008T003 | EMPALME | 66 | 67 | 1.04 | 0.65 | 1.09 | 0.94 | 1 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE010T003 | FRUTILLAR | 13.2 | 13.2 | 1.04 | 0.99 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE007T003 | L.NEGROS | 23 | 23 | 1.05 | 1 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET002R024SE012T003 | LA UNION 13.2 | 13.2 | 13.2 | 1.04 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE012T003 | LA UNION 23 | 23 | 23 | 1.02 | 0.99 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET002R024SE129T005 | LONCOCHE 13.2 | 13.2 | 13.2 | 1.08 | 0.94 | 1.07 | 0.93 | 3 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE129T005 | LONCOCHE 23 | 23 | 23 | 1.03 | 0.92 | 1.07 | 0.93 | 1 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE014T003 | LOS LAGOS | 13.2 | 13.2 | 1 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE013T003 | MELIPULLI | 23 | 23 | 1 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE016T003 | OSORNO | 23 | 23 | 1.04 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-21 | 9:43
SAESA | RET002R024SE021T003 | P. VARAS 13.2 | 13.2 | 13.2 | 1.05 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE021T003 | P. VARAS 23 | 23 | 23 | 0.99 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE017T003 | PANGUIPULLI | 23 | 23 | 1.02 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET002R024SE018T003 | PICARTE 13.2 | 13.2 | 13.2 | 1.07 | 1.01 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE018T003 | PICARTE 23 | 23 | 23 | 1.07 | 1.01 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET002R024SE019T003 | PICHIRROPULLI 13.2 | 13.2 | 13.2 | 1.04 | 0.99 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE019T003 | PICHIRROPULLI 23 | 23 | 23 | 1.06 | 0.99 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE015T003 | PID PID | 23 | 23 | 1.07 | 0.94 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE001G008 | PILMAIQUEN | 13.2 | 13.2 | 1.06 | 0.99 | 1.07 | 0.93 | 0 | 2765 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE031T002 | PTO. MONTT | 23 | 23 | 1.01 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET002R024SE031T002 | PTO. MONTT T44 | 23 | 23
SAESA | RET001R024SE022T003 | PURRANQUE | 13.2 | 13.2 | 1.03 | 0.96 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-21 | 9:43
SAESA | RET002R024SE022T003 | PURRANQUE 23 kV | 23 | 23 | 1.02 | 0.97 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-21 | 16:38
SAESA | RET001R024SE026T003 | QUELLON | 23 | 23 | 1.06 | 0.95 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET001R024SE032T003 | S/E MARIQUINA | 23 | 23
SAESA | RET001R024SE038T002 | VALDIVIA | 13.2 | 13.2 | 1.05 | 1 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SAESA | RET002R024SE038T002 | VALDIVIA 23 kV | 23 | 23
SOCOEPA | RET001R024SE014T003 | Los Lagos | 13.2 | 13.2 | 1 | 0.98 | 1.07 | 0.93 | 0 | 2784 | 0% | 2012-03-20 | 15:26
SOCOEPA | RET001R014SE001R014 | Paillaco | 13.2 | 13.2 | 303 | 295 | 1.07 | 0.93 | 2784 | 2784 | 100% | 2012-03-13 | 15:14
TRANSNET | RET002R012SE022T005 | S/E Alameda | 15 | 15
TRANSNET | RET001R012SE022T005 | S/E Alameda | 15 | 15
TRANSNET | RET002R015SE026T005 | S/E Andacollo | 13.2 | 13.2
TRANSNET | RET001R015SE026T005 | S/E Andacollo | 66 | 67
TRANSNET | RET002R012SE027T005 | S/E Andali | 15 | 15
TRANSNET | RET003R012SE027T005 | S/E Andali | 15 | 15
TRANSNET | RET002R012SE030T005 | S/E Buin (C.G.E.) | 15 | 15
TRANSNET | RET004R012SE030T005 | S/E Buin (C.G.E.) | 15 | 15
TRANSNET | RET002R015SE031T005 | S/E Cabildo | 23 | 23
TRANSNET | RET003R015SE031T005 | S/E Cabildo | 23 | 23
TRANSNET | RET005R012SE032T005 | S/E Cachapoal | 15 | 15
TRANSNET | RET002R012SE032T005 | S/E Cachapoal | 15 | 15
TRANSNET | RET003R019SE033T005 | S/E Carampangue | 13.2 | 13.2
TRANSNET | RET004R015SE047T005 | S/E Casas Viejas | 13.2 | 13.2
TRANSNET | RET001A002SE002A002 | S/E Celulosa Arauco | 66 | 67
TRANSNET | RET002R005SE100T005 | S/E Chacahu | 13.2 | 13.2
TRANSNET | RET001R005SE100T005 | S/E Chacahu | 13.2 | 13.2
TRANSNET | RET002R012SE035T005 | S/E Chiguayante | 15 | 15
TRANSNET | RET006R012SE035T005 | S/E Chiguayante | 15 | 15
TRANSNET | RET008R012SE024T005 | S/E Chill | 15 | 15
TRANSNET | RET007R012SE024T005 | S/E Chill | 15 | 15
TRANSNET | RET009R012SE037T005 | S/E Chimbarongo | 15 | 15
TRANSNET | RET010R012SE038T005 | S/E Chivilc | 15 | 15
TRANSNET | RET002R012SE038T005 | S/E Chivilc | 15 | 15
TRANSNET | RET011R012SE040T005 | S/E Chumaquito | 15 | 15
TRANSNET | RET012R012SE128T005 | S/E Cocharcas (C.G.E) | 15 | 15
TRANSNET | RET002R012SE041T005 | S/E Colchagua | 15 | 15
TRANSNET | RET014R012SE042T005 | S/E Colcura | 13.2 | 13.2
TRANSNET | RET006R019SE043T005 | S/E Collipulli | 13.2 | 13.2
TRANSNET | RET002R012SE044T005 | S/E Colo Colo | 15 | 15
TRANSNET | RET015R012SE044T005 | S/E Colo Colo | 15 | 15
TRANSNET | RET016R012SE013T002 | S/E Coronel | 15 | 15
TRANSNET | RET007R019SE013T002 | S/E Coronel | 15 | 15
TRANSNET | RET009R019SE036T005 | S/E Curanilahue | 23 | 23
TRANSNET | RET002R005SE126T005 | S/E Curicó | 13.2 | 13.2
TRANSNET | RET003R005SE126T005 | S/E Curicó | 13.2 | 13.2
TRANSNET | RET002R012SE002T005 | S/E Ejército | 15 | 15
TRANSNET | RET019R012SE002T005 | S/E Ejército | 15 | 15
TRANSNET | RET020R012SE003T005 | S/E El Avellano | 23 | 23
TRANSNET | RET022R012SE115T005 | S/E El Manzano (C.G.E.) | 15 | 15
TRANSNET | RET006R015SE005T005 | S/E El Peñon | 23 | 23
TRANSNET | RET023R012SE007T005 | S/E Escuadr?n (C.G.E.) | 15 | 15
TRANSNET | RET024R012SE023T005 | S/E F?tima | 15 | 15
TRANSNET | RET025R012SE012T005 | S/E Graneros | 15 | 15
TRANSNET | RET009R015SE001T005 | S/E Guayac | 13.2 | 13.2
TRANSNET | RET010R015SE001T005 | S/E Guayac | 13.2 | 13.2
TRANSNET | RET026R012SE015T005 | S/E Hospital | 15 | 15
TRANSNET | RET011R015SE016T005 | S/E Illapel | 23 | 23
TRANSNET | RET003R005SE010T005 | S/E La Palma | 13.2 | 13.2
TRANSNET | RET023R012SE018T005 | S/E La Ronda | 15 | 15
TRANSNET | RET028R012SE019T005 | S/E Las Cabras | 15 | 15
TRANSNET | RET014R015SE020T005 | S/E Las Compa??as | 13.2 | 13.2
TRANSNET | RET029R012SE021T005 | S/E Latorre | 15 | 15
TRANSNET | RET002R012SE021T005 | S/E Latorre | 15 | 15
TRANSNET | RET030R012SE058T005 | S/E Lautaro | 15 | 15
TRANSNET | RET031R012SE072T005 | S/E Lirqu | 15 | 15
TRANSNET | RET002R012SE073T005 | S/E Lo Miranda | 15 | 15
TRANSNET | RET032R012SE073T005 | S/E Lo Miranda | 15 | 15
TRANSNET | RET033R012SE074T005 | S/E Loma Colorada | 15 | 15
TRANSNET | RET002R004SE129T005 | S/E Loncoche | 13.2 | 13.2
TRANSNET | RET016R024SE129T005 | S/E Loncoche | 13.2 | 13.2
TRANSNET | RET034R012SE129T005 | S/E Loncoche | 23 | 23
TRANSNET | RET008R024SE129T005 | S/E Loncoche | 13.2 | 13.2
TRANSNET | RET007R024SE129T005 | S/E Loncoche | 13.2 | 13.2
TRANSNET | RET035R012SE075T005 | S/E Loreto | 15 | 15
TRANSNET | RET036R012SE076T005 | S/E Los Angeles | 15 | 15
TRANSNET | RET001R011SE076T005 | S/E Los Angeles | 13 | 13
TRANSNET | RET037R012SE076T005 | S/E Los Angeles | 13.2 | 13.2
TRANSNET | RET001L007SE076T005 | S/E Los Angeles | 13 | 13
TRANSNET | RET016R019SE076T005 | S/E Los Angeles | 13.2 | 13.2
TRANSNET | RET015R015SE025T002 | S/E Los Vilos | 23 | 23
TRANSNET | RET001R012SE147T005 | S/E Machalí | 15 | 15
TRANSNET | RET002R012SE077T005 | S/E Mahns | 15 | 15
TRANSNET | RET038R012SE077T005 | S/E Mahns | 15 | 15
TRANSNET | RET039R012SE078T005 | S/E Malloa | 15 | 15
TRANSNET | RET041R012SE079T005 | S/E Manso de Velasco | 15 | 15
TRANSNET | RET017R015SE080T005 | S/E Marquesa_1 | 23 | 23
TRANSNET | RET018R015SE080T005 | S/E Marquesa_2 | 23 | 23
TRANSNET | RET019R015SE080T005 | S/E Marquesa_3 | 23 | 23
TRANSNET | RET002R005SE009T005 | S/E Molina | 13.2 | 13.2
TRANSNET | RET002R012SE009T005 | S/E Molina | 66 | 67
TRANSNET | RET006R005SE009T005 | S/E Molina | 13.2 | 13.2
TRANSNET | RET001R009SE082T005 | S/E Monte Patria | 13.2 | 13.2
TRANSNET | RET018R015SE082T005 | S/E Monte Patria | 23 | 23
TRANSNET | RET005A002SE004A002 | S/E Nueva Aldea | 66 | 67
TRANSNET | RET020R015SE071T005 | S/E Ovalle | 23 | 23
TRANSNET | RET021R015SE071T005 | S/E Ovalle | 13.2 | 13.2
TRANSNET | RET043R012SE084T005 | S/E Padre Las Casas | 15 | 15
TRANSNET | RET022R015SE027T002 | S/E Pan de Azúcar | 13.2 | 13.2
TRANSNET | RET044R012SE086T005 | S/E Panguilemo | 15 | 15
TRANSNET | RET045R012SE087T005 | S/E Pelequ | 15 | 15
TRANSNET | RET046R012SE088T005 | S/E Penco | 15 | 15
TRANSNET | RET047R012SE089T005 | S/E Perales | 15 | 15
TRANSNET | RET030R017SE090T005 | S/E Piduco | 15 | 15
TRANSNET | RET048R012SE090T005 | S/E Piduco | 15 | 15
TRANSNET | RET049R012SE091T005 | S/E Pillanlelb?n | 15 | 15
TRANSNET | RET050R012SE117T005 | S/E Pirque | 13.2 | 13.2
TRANSNET | RET051R012SE092T005 | S/E Pitrufqu | 13.2 | 13.2
TRANSNET | RET053R012SE083T005 | S/E Pumahue | 15 | 15
TRANSNET | RET002R009SE081T005 | S/E Punitaqui | 13.2 | 13.2
TRANSNET | RET024R015SE051T005 | S/E Qu?nquimo | 23 | 23
TRANSNET | RET001R012SE154T005 | S/E Quinta de Tilcoco | 15 | 15
TRANSNET | RET007R005SE008T005 | S/E Rauqu | 13.2 | 13.2
TRANSNET | RET056R012SE052T005 | S/E Rengo | 15 | 15
TRANSNET | RET069R005SE053T005 | S/E Salamanca | 23 | 23
TRANSNET | RET002L040SE055T005 | S/E San Francisco de Mostazal | 15 | 15
TRANSNET | RET003L040SE055T005 | S/E San Francisco de Mostazal | 15 | 15
TRANSNET | RET001L040SE055T005 | S/E San Francisco de Mostazal | 15 | 15
TRANSNET | RET058R012SE055T005 | S/E San Francisco de Mostazal | 15 | 15
TRANSNET | RET057R012SE055T005 | S/E San Francisco de Mostazal | 15 | 15
TRANSNET | RET025R015SE056T005 | S/E San Joaqu?n (C.G.E.) | 13.2 | 13.2
TRANSNET | RET002R015SE056T005 | S/E San Joaqu?n (C.G.E.) | 13.2 | 13.2
TRANSNET | RET058R012SE057T005 | S/E San Miguel | 15 | 15
TRANSNET | RET001L041SE120T005 | S/E San Pedro (C.G.E.) | 15 | 15
TRANSNET | RET060R012SE059T005 | S/E San Vicente de Tagua Tagua | 15 | 15
TRANSNET | RET002R012SE059T005 | S/E San Vicente de Tagua Tagua | 15 | 15
TRANSNET | RET002R012SE048T005 | S/E Santa Elvira | 15 | 15
TRANSNET | RET062R012SE061T005 | S/E Talca | 15 | 15
TRANSNET | RET063R012SE061T005 | S/E Talca | 15 | 15
TRANSNET | RET063R012SE062T005 | S/E Talcahuano | 15 | 15
TRANSNET | RET002R012SE062T005 | S/E Talcahuano | 15 | 15
TRANSNET | RET064R012SE127T005 | S/E Teno | 15 | 15
TRANSNET | RET065R012SE127T005 | S/E Teno | 15 | 15
TRANSNET | RET008R005SE134T005 | S/E Teno Empalme | 13.2 | 13.2
TRANSNET | RET066R012SE063T005 | S/E Tom | 23 | 23
TRANSNET | RET036R017SE063T005 | S/E Tom | 23 | 23
TRANSNET | RET067R012SE066T005 | S/E Tumbes | 15 | 15
TRANSNET | RET070R012SE067T005 | S/E Tuniche | 15 | 15
TRANSNET | RET024R019SE068T005 | S/E Victoria | 13.2 | 13.2
TRANSNET | RET006R004SE068T005 | S/E Victoria | 13.2 | 13.2
TRANSNET | RET026R015SE069T005 | S/E Vicuña | 23 | 23
TRANSNET | RET010R005SE133T005 | S/E Villa Alegre | 13.2 | 13.2
TRANSNET | RET001R012SE093T005 | S/E Villarrica | 6.3 | 6.3
TRANSNET | RET068R012SE093T005 | S/E Villarrica | 23 | 23
TRANSNET | RET001R012SE095T005 | Tap Polpaico | 23 | 23