{"text_format":"1","workbook":"xlsx","n_sheets":2,"sheets":["Icc 2019","Icc 2024"],"not_rendered":{"charts":0,"images":1,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Icc 2019","index":0,"n_rows":1173,"n_cols":15,"rows_kept":1173,"cut":false,"hidden":false,"merged":[[1161,1,1162,1],[1161,2,1162,2],[1127,1,1129,1],[1127,2,1129,2],[1130,1,1131,1],[1130,2,1131,2],[1111,1,1116,1],[1111,2,1116,2],[27,1,42,1],[27,2,42,2],[1132,1,1134,1],[1132,2,1134,2],[1136,1,1138,1],[1136,2,1138,2],[1140,1,1142,1],[1140,2,1142,2],[1048,1,1051,1],[1048,2,1051,2],[1053,1,1054,1],[1053,2,1054,2],[1069,1,1070,1],[1069,2,1070,2],[1031,1,1034,1],[1031,2,1034,2],[1020,1,1030,1],[1020,2,1030,2],[959,1,961,1],[959,2,961,2],[962,1,963,1],[962,2,963,2],[950,1,956,1],[950,2,956,2],[957,1,958,1],[957,2,958,2],[964,1,965,1],[964,2,965,2],[966,1,969,1],[966,2,969,2],[970,1,973,1],[970,2,973,2],[1004,1,1008,1],[1004,2,1008,2],[1009,1,1015,1],[1009,2,1015,2],[997,1,1002,1],[997,2,1002,2],[983,1,985,1],[983,2,985,2],[1016,1,1019,1],[1016,2,1019,2],[920,1,925,1],[920,2,925,2],[926,1,929,1],[926,2,929,2],[940,1,946,1],[940,2,946,2],[947,1,949,1],[947,2,949,2],[986,1,996,1],[986,2,996,2],[974,2,982,2],[974,1,982,1],[933,1,939,1],[933,2,939,2],[507,1,510,1],[507,2,510,2],[512,1,517,1],[512,2,517,2],[595,1,596,1],[595,2,596,2],[597,1,599,1],[597,2,599,2],[584,1,586,1],[584,2,586,2],[587,1,588,1],[587,2,588,2],[589,1,594,1],[589,2,594,2],[523,1,526,1],[523,2,526,2],[527,1,531,1],[527,2,531,2],[546,1,554,1],[546,2,554,2],[532,1,538,1],[532,2,538,2],[539,1,543,1],[539,2,543,2],[485,1,493,1],[485,2,493,2],[463,1,469,1],[463,2,469,2],[470,1,474,1],[470,2,474,2],[475,1,477,1],[475,2,477,2],[504,1,506,1],[504,2,506,2],[478,1,480,1],[478,2,480,2],[482,1,484,1],[482,2,484,2],[446,1,453,1],[446,2,453,2],[456,1,462,1],[456,2,462,2],[406,1,408,1],[406,2,408,2],[411,1,423,1],[411,2,423,2],[427,1,428,1],[427,2,428,2],[430,1,438,1],[430,2,438,2],[439,1,442,1],[439,2,442,2],[443,1,444,1],[443,2,444,2],[193,2,194,2],[147,1,151,1],[147,2,151,2],[156,1,159,1],[356,1,363,1],[356,2,363,2],[364,1,367,1],[364,2,367,2],[348,1,349,1],[348,2,349,2],[340,1,342,1],[340,2,342,2],[333,1,339,1],[333,2,339,2],[300,1,306,1],[300,2,306,2],[315,1,319,1],[315,2,319,2],[320,1,321,1],[320,2,321,2],[200,1,204,1],[200,2,204,2],[171,1,172,1],[171,2,172,2],[881,1,886,1],[881,2,886,2],[887,1,889,1],[887,2,889,2],[890,1,893,1],[890,2,893,2],[867,1,870,1],[867,2,870,2],[871,1,873,1],[871,2,873,2],[875,1,880,1],[875,2,880,2],[1117,1,1126,1],[1117,2,1126,2],[1077,1,1082,1],[1077,2,1082,2],[1086,1,1087,1],[1086,2,1087,2],[1073,1,1074,1],[1073,2,1074,2],[1035,2,1040,2],[1035,1,1040,1],[1042,2,1045,2],[1042,1,1045,1],[1107,1,1110,1],[1107,2,1110,2],[1088,1,1090,1],[1088,2,1090,2],[1094,1,1095,1],[1094,2,1095,2],[1102,2,1105,2],[1102,1,1105,1],[902,2,905,2],[906,1,912,1],[906,2,912,2],[913,1,914,1],[913,2,914,2],[894,1,895,1],[894,2,895,2],[896,1,901,1],[896,2,901,2],[902,1,905,1],[832,1,833,1],[832,2,833,2],[836,1,837,1],[836,2,837,2],[856,1,858,1],[856,2,858,2],[865,1,866,1],[865,2,866,2],[838,1,840,1],[838,2,840,2],[841,1,844,1],[841,2,844,2],[845,1,850,1],[845,2,850,2],[851,1,853,1],[851,2,853,2],[854,1,855,1],[854,2,855,2],[860,1,863,1],[860,2,863,2],[827,1,829,1],[827,2,829,2],[821,1,822,1],[821,2,822,2],[823,1,825,1],[823,2,825,2],[814,1,816,1],[814,2,816,2],[817,1,820,1],[817,2,820,2],[798,1,810,1],[798,2,810,2],[811,1,813,1],[811,2,813,2],[795,1,797,1],[795,2,797,2],[787,1,792,1],[787,2,792,2],[777,1,781,1],[777,2,781,2],[784,1,785,1],[784,2,785,2],[769,1,776,1],[769,2,776,2],[763,1,765,1],[763,2,765,2],[766,1,768,1],[766,2,768,2],[760,1,762,1],[760,2,762,2],[747,2,758,2],[747,1,758,1],[745,1,746,1],[745,2,746,2],[718,1,719,1],[718,2,719,2],[720,1,722,1],[720,2,722,2],[694,1,698,1],[694,2,698,2],[699,1,702,1],[699,2,702,2],[724,1,725,1],[724,2,725,2],[727,1,729,1],[727,2,729,2],[703,1,706,1],[703,2,706,2],[707,1,709,1],[707,2,709,2],[711,1,716,1],[711,2,716,2],[730,2,744,2],[730,1,744,1],[691,1,693,1],[691,2,693,2],[655,1,658,1],[655,2,658,2],[659,1,660,1],[659,2,660,2],[639,1,643,1],[639,2,643,2],[644,1,647,1],[644,2,647,2],[649,1,650,1],[649,2,650,2],[651,1,652,1],[651,2,652,2],[653,1,654,1],[653,2,654,2],[680,1,681,1],[680,2,681,2],[683,1,686,1],[683,2,686,2],[676,1,679,1],[676,2,679,2],[661,1,664,1],[661,2,664,2],[581,1,583,1],[581,2,583,2],[570,1,573,1],[570,2,573,2],[574,1,576,1],[574,2,576,2],[600,1,602,1],[600,2,602,2],[688,1,690,1],[688,2,690,2],[618,1,620,1],[618,2,620,2],[631,1,636,1],[631,2,636,2],[637,1,638,1],[637,2,638,2],[667,1,668,1],[667,2,668,2],[669,1,675,1],[669,2,675,2],[603,2,604,2],[577,1,580,1],[250,1,253,1],[250,2,253,2],[254,1,256,1],[254,2,256,2],[257,1,258,1],[257,2,258,2],[260,1,262,1],[260,2,262,2],[291,1,299,1],[291,2,299,2],[284,1,287,1],[284,2,287,2],[277,1,283,1],[277,2,283,2],[264,1,266,1],[264,2,266,2],[267,1,276,1],[267,2,276,2],[375,1,378,1],[375,2,378,2],[386,1,396,1],[386,2,396,2],[379,1,382,1],[379,2,382,2],[368,1,371,1],[368,2,371,2],[372,1,374,1],[372,2,374,2],[403,1,405,1],[403,2,405,2],[47,1,48,1],[47,2,48,2],[96,1,97,1],[96,2,97,2],[98,1,101,1],[98,2,101,2],[102,1,105,1],[102,2,105,2],[397,1,400,1],[397,2,400,2],[222,1,227,1],[222,2,227,2],[231,1,233,1],[231,2,233,2],[234,1,236,1],[234,2,236,2],[383,1,385,1],[383,2,385,2],[350,1,355,1],[350,2,355,2],[343,1,344,1],[343,2,344,2],[345,1,347,1],[345,2,347,2],[7,2,17,2],[175,1,177,1],[175,2,177,2],[197,1,199,1],[197,2,199,2],[49,1,53,1],[49,2,53,2],[54,1,59,1],[54,2,59,2],[185,1,192,1],[156,2,159,2],[160,1,170,1],[160,2,170,2],[139,1,144,1],[139,2,144,2],[145,1,146,1],[145,2,146,2],[115,1,119,1],[115,2,119,2],[121,1,125,1],[121,2,125,2],[185,2,192,2],[193,1,194,1],[43,2,46,2],[217,2,219,2],[5,4,5,5],[5,6,5,7],[5,8,5,9],[5,10,5,11],[5,12,5,14],[86,1,89,1],[86,2,89,2],[90,1,95,1],[90,2,95,2],[80,1,85,1],[80,2,85,2],[62,1,67,1],[62,2,67,2],[68,1,69,1],[68,2,69,2],[70,1,71,1],[70,2,71,2],[72,1,74,1],[72,2,74,2],[77,1,79,1],[77,2,79,2],[43,1,46,1],[7,1,17,1],[577,2,580,2],[18,1,26,1],[18,2,26,2],[288,2,290,2],[288,1,290,1],[322,2,331,2],[322,1,331,1],[308,1,313,1],[308,2,313,2],[106,1,109,1],[106,2,109,2],[111,1,112,1],[111,2,112,2],[126,1,129,1],[126,2,129,2],[130,1,132,1],[130,2,132,2],[137,1,138,1],[137,2,138,2],[211,1,213,1],[211,2,213,2],[237,1,249,1],[237,2,249,2],[217,1,219,1],[1,1,1,12],[1143,1,1160,1],[1143,2,1160,2],[1163,2,1169,2],[1163,1,1169,1],[495,1,500,1],[495,2,500,2],[555,2,560,2],[555,1,560,1],[561,2,569,2],[561,1,569,1],[605,2,616,2],[605,1,616,1],[625,2,627,2],[625,1,627,1],[501,1,503,1],[501,2,503,2],[518,1,519,1],[518,2,519,2],[520,1,522,1],[520,2,522,2],[603,1,604,1]]}
[]
[null,"CORRIENTES DE CORTOCIRCUITO  - AÑO 2019"]
[]
[]
[]
[null,null,null,null,"I''kss 3F [kA] - 2019",null,"I''kss 1F [kA] - 2019",null,"I''kss 2F [kA] - 2019",null,"I''kss 2FT [kA] - 2019",null,"Máximas Corrientes - [kA]"]
[null,"Identificación de la S/E","Nivel de Tensión [kV]","Identificación del paño","En barra","Contribución por paño","En barra","Contribución por paño","En barra","Contribución por paño","En barra","Contribución por paño","I''kss Concentrada",52,"I''kss \nCirculante"]
[null,10,100,"10 100 kV - H21 Línea 100kV 10 - 10A",10.041,5.2380000000000004,11.042,5.9340000000000002,8.5690000000000008,4.4669999999999996,10.746,5.6580000000000004,11.042,5.1079999999999997,5.9340000000000002]
[null,null,null,"10 100 kV - H23 Línea 100kV 10 - K1",10.041,2.1509999999999998,11.042,2.1869999999999998,8.5690000000000008,1.837,10.746,2.21,11.042,8.8550000000000004,8.8550000000000004]
[null,null,null,"10 100 kV - HT1 Transformador TR01 8/10MVA 100/13,8kV",10.041,0,11.042,0,8.5690000000000008,0,10.746,0,11.042,11.042,11.042]
[null,null,null,"10 100 kV - HT2 Transformador TR02 8/10MVA 100/13,8kV",10.041,0,11.042,0,8.5690000000000008,0,10.746,0,11.042,11.042,11.042]
[null,null,null,"10 100 kV - HT3 Transformador TR03 8/10MVA 100/13,8kV",10.041,0,11.042,0,8.5690000000000008,0,10.746,0,11.042,11.042,11.042]
[null,null,null,"10 100 kV - HT4 Transformador TR04 8/10MVA 100/13,8kV",10.041,0,11.042,0,8.5690000000000008,0,10.746,0,11.042,11.042,11.042]
[null,null,null,"10 100 kV - HT5 Transformador TR05 8/10MVA 100/13,8kV",10.041,0,11.042,0,8.5690000000000008,0,10.746,0,11.042,11.042,11.042]
[null,null,null,"10 100 kV - HT6 Transformador TR06 8/10MVA 100/13,8kV",10.041,0,11.042,0,8.5690000000000008,0,10.746,0,11.042,11.042,11.042]
[null,null,null,"10 100 kV - HT7 Transformador TR07 8/10MVA 100/13,8kV",10.041,0,11.042,0,8.5690000000000008,0,10.746,0,11.042,11.042,11.042]
[null,null,null,"10 100 kV - H10 Línea 100kV 10 - Chuquicamata",10.041,2.661,11.042,2.9260000000000002,8.5690000000000008,2.2719999999999998,10.746,2.883,11.042,8.1159999999999997,8.1159999999999997]
[null,null,null,"10 100 kV - HAB Acoplador",10.041,0,11.042,0,8.5690000000000008,0,10.746,0,11.042,11.042,11.042]
[null,"10A",100,"10A 100 kV - H11 Línea 100kV 10A - Chuquicamata",10.041,2.2839999999999998,11.042,2.74,8.5690000000000008,1.9510000000000001,10.747,2.5489999999999999,11.042,8.3019999999999996,8.3019999999999996]
[null,null,null,"10A 100 kV - HT8 Transformador TR08 15/22,4MVA 100/13,8kV",10.041,0,11.042,0,8.5690000000000008,0,10.747,0,11.042,11.042,11.042]
[null,null,null,"10A 100 kV - HT9 Transformador TR09 15/22,4MVA 100/13,8kV",10.041,0,11.042,0,8.5690000000000008,0,10.747,0,11.042,11.042,11.042]
[null,null,null,"10A 100 kV - HT10 Transformador TR10 15/22,4MVA 100/13,8kV",10.041,0,11.042,0,8.5690000000000008,0,10.747,0,11.042,11.042,11.042]
[null,null,null,"10A 100 kV - HT11 Transformador TR11 44,8/59,73MVA 100/13,8kV",10.041,0,11.042,0,8.5690000000000008,0,10.747,0,11.042,11.042,11.042]
[null,null,null,"10A 100 kV - HT12 Transformador TR12 44,8/59,73MVA 100/13,8kV",10.041,0,11.042,0,8.5690000000000008,0,10.747,0,11.042,11.042,11.042]
[null,null,null,"10A 100 kV - HT13 Transformador TR13 45/56MVA 100/13,8kV",10.041,0,11.042,0,8.5690000000000008,0,10.747,0,11.042,11.042,11.042]
[null,null,null,"10A 100 kV - H22 Línea 100kV 10A - KM6",10.041,2.9630000000000001,11.042,3.2029999999999998,8.5690000000000008,2.524,10.747,3.1190000000000002,11.042,7.8390000000000004,7.8390000000000004]
[null,null,null,"10A 100 kV - HAB Acoplador",10.041,0,11.042,0,8.5690000000000008,0,10.747,0,11.042,11.042,11.042]
[null,"A",100,"A 100 kV -  H1 Línea 100 kV A - Central Tocopilla 1",10.403,0.67800000000000005,12.112,0.59099999999999997,8.8729999999999993,0.58099999999999996,11.78,0.626,12.112,11.521000000000001,11.521000000000001]
[null,null,null,"A 100 kV -  H2 Línea 100 kV A - Central Tocopilla 2",10.403,0.66200000000000003,12.112,0.53600000000000003,8.8729999999999993,0.56799999999999995,11.78,0.60299999999999998,12.112,11.576000000000001,11.576000000000001]
[null,null,null,"A 100 kV -  H3 Línea 100 kV A - Central Diesel Tamaya 1",10.403,0.79100000000000004,12.112,0.66300000000000003,8.8729999999999993,0.67600000000000005,11.78,0.72899999999999998,12.112,11.449,11.449]
[null,null,null,"A 100 kV - H14 Línea 100 kV A - Chuquicamata 1",10.403,4.1420000000000003,12.112,4.5289999999999999,8.8729999999999993,3.5289999999999999,11.78,4.62,12.112,7.5830000000000002,7.5830000000000002]
[null,null,null,"A 100 kV - H15 Línea 100 kV A - Chuquicamata 2",10.403,4.1420000000000003,12.112,5.8150000000000004,8.8729999999999993,3.5289999999999999,11.78,5.3879999999999999,12.112,6.3919999999999995,6.3919999999999995]
[null,null,null,"A 100 kV - HT3 Transformador TR03 10 MVA 100/5 kV ",10.403,0,12.112,0,8.8729999999999993,0,11.78,0,12.112,12.112,12.112]
[null,null,null,"A 100 kV - HT4 Transformador TR04 10 MVA 100/5 kV ",10.403,0,12.112,0,8.8729999999999993,0,11.78,0,12.112,12.112,12.112]
[null,null,null,"A 100 kV - HT13 Transformador TR13 20 MVA 100/13,8 kV ",10.403,0,12.112,0,8.8729999999999993,0,11.78,0,12.112,12.112,12.112]
[null,null,null,"A 100 kV - HT14 Transformador TR14 20/25 MVA 100/13,8 kV ",10.403,0,12.112,0,8.8729999999999993,0,11.78,0,12.112,12.112,12.112]
[null,null,null,"A 100 kV - HT15 Transformador TR15 25/33,3 MVA 100/13,8 kV",10.403,0,12.112,0,8.8729999999999993,0,11.78,0,12.112,12.112,12.112]
[null,null,null,"A 100 kV - HT16 Transformador TR16 25/33,3 MVA 100/13,8 kV",10.403,0,12.112,0,8.8729999999999993,0,11.78,0,12.112,12.112,12.112]
[null,null,null,"A 100 kV - HT17 Transformador TR17 40/56 MVA 100/13,8 kV",10.403,0,12.112,0,8.8729999999999993,0,11.78,0,12.112,12.112,12.112]
[null,null,null,"A 100 kV - HT18 Transformador TR18 25/33,3 MVA 100/13,8 kV",10.403,0,12.112,0,8.8729999999999993,0,11.78,0,12.112,12.112,12.112]
[null,null,null,"A 100 kV - HT19 Transformador TR19 40/56 MVA 100/13,8 kV",10.403,0,12.112,0,8.8729999999999993,0,11.78,0,12.112,12.112,12.112]
[null,null,null,"A 100 kV - HC Banco de Condensadores 1",10.403,0,12.112,0,8.8729999999999993,0,11.78,0,12.112,12.112,12.112]
[null,null,null,"A 100 kV - HACOP Acoplador",10.403,0,12.112,0,8.8729999999999993,0,11.78,0,12.112,12.112,12.112]
[null,"Abanico",154,"Abanico 154 kV -  A2 Línea 154 kV Abanico - Charrúa C2",5.0910000000000002,2.4790000000000001,4.5999999999999996,2.14,3.3439999999999999,2.1960000000000002,5.5179999999999998,2.3090000000000002,5.5179999999999998,3.2089999999999996,3.2089999999999996]
[null,null,null,"Abanico 154 kV - AT1 Transformador Abanico N°1 y N°2",5.0910000000000002,0.81599999999999995,4.5999999999999996,0.71,3.3439999999999999,0.40200000000000002,5.5179999999999998,0.95799999999999996,5.5179999999999998,4.5599999999999996,4.5599999999999996]
[null,null,null,"Abanico 154 kV - AT3 Transformador Abanico N°3",5.0910000000000002,0.79,4.5999999999999996,0.67900000000000005,3.3439999999999999,0.39300000000000002,5.5179999999999998,0.92,5.5179999999999998,4.5979999999999999,4.5979999999999999]
[null,null,null,"Abanico 154 kV - AT4 Transformador Abanico N°4",5.0910000000000002,1.038,4.5999999999999996,1.085,3.3439999999999999,0.49199999999999999,5.5179999999999998,1.5049999999999999,5.5179999999999998,4.0529999999999999,4.0529999999999999]
[null,"ACL",100,"ACL 100 kV - H1 Línea 100 kV ACL - KM6 1",5.2069999999999999,5.2069999999999999,4.8769999999999998,4.8769999999999998,4.4749999999999996,4.4749999999999996,5.1369999999999996,5.1369999999999996,5.2069999999999999,0,5.2069999999999999]
[null,null,null,"ACL 100 kV - HT1 Transformador ACL 100/13.8 kV",5.2069999999999999,0,4.8769999999999998,0,4.4749999999999996,0,5.1369999999999996,0,5.2069999999999999,5.2069999999999999,5.2069999999999999]
[null,"Aconcagua ",110,"Aconcagua  110 kV - H1 Transformador TR1 110/12 kV (Unidad 1 - Blanco)",8.3949999999999996,1.0640000000000001,10.358000000000001,3.1280000000000001,7.4530000000000003,1.002,10.071,3.06,10.358000000000001,7.3309999999999995,7.3309999999999995]
[null,null,null,"Aconcagua  110 kV - H2 Transformador TR2 110/12 kV (Unidad 2 - Juncal)",8.3949999999999996,0.55400000000000005,10.358000000000001,0.873,7.4530000000000003,0.442,10.071,0.84299999999999997,10.358000000000001,9.4850000000000012,9.4850000000000012]
[null,null,null,"Aconcagua  110 kV - H3 Línea 110 kV Aconcagua - Los Maquis/San Rafael 1",8.3949999999999996,3.1349999999999998,10.358000000000001,2.8860000000000001,7.4530000000000003,2.7839999999999998,10.071,3.0430000000000001,10.358000000000001,7.4720000000000004,7.4720000000000004]
[null,null,null,"Aconcagua  110 kV - H4 Línea 110 kV Aconcagua - Los Maquis/Totoralillo 2",8.3949999999999996,3.1360000000000001,10.358000000000001,2.8889999999999998,7.4530000000000003,2.7869999999999999,10.071,3.044,10.358000000000001,7.4690000000000012,7.4690000000000012]
[null,null,null,"Aconcagua  110 kV - HT Transformador TR03 110/66/12 kV ",8.3949999999999996,0.52800000000000002,10.358000000000001,0.60299999999999998,7.4530000000000003,0.46500000000000002,10.071,0.58499999999999996,10.358000000000001,9.7550000000000008,9.7550000000000008]
[null,"Agua Santa ",110,"Agua Santa  110 kV -  H7 Línea 110 kV Agua Santa - Miraflores 2",20.231999999999999,4.8929999999999998,19.635999999999999,3.7189999999999999,17.579000000000001,4.2640000000000002,20.228999999999999,4.49,20.231999999999999,15.917,15.917]
[null,null,null,"Agua Santa  110 kV -  H8 Línea 110 kV Agua Santa - Miraflores 1",20.231999999999999,4.8929999999999998,19.635999999999999,3.7189999999999999,17.579000000000001,4.2640000000000002,20.228999999999999,4.49,20.231999999999999,15.917,15.917]
[null,null,null,"Agua Santa  110 kV -  H9 Línea 110 kV Agua Santa - Tap Los Placeres 2",20.231999999999999,0.93899999999999995,19.635999999999999,0.89200000000000002,17.579000000000001,0.81200000000000006,20.228999999999999,0.90700000000000003,20.231999999999999,19.321999999999999,19.321999999999999]
[null,null,null,"Agua Santa  110 kV - H10 Línea 110 kV Agua Santa - Tap Los Placeres 1",20.231999999999999,0.80400000000000005,19.635999999999999,0.85,17.579000000000001,0.69599999999999995,20.228999999999999,0.85899999999999999,20.231999999999999,19.428000000000001,19.428000000000001]
[null,null,null,"Agua Santa  110 kV - H11 Línea 110 kV Agua Santa - Placilla ",20.231999999999999,0.193,19.635999999999999,0.125,17.579000000000001,0.16500000000000001,20.228999999999999,0.16900000000000001,20.231999999999999,20.059999999999999,20.059999999999999]
[null,null,null,"Agua Santa  110 kV - HT1 Transformador TR1 300 MVA 220/110/66 kV ",20.231999999999999,8.5890000000000004,19.635999999999999,10.38,17.579000000000001,7.4450000000000003,20.228999999999999,9.4649999999999999,20.231999999999999,11.642999999999999,11.642999999999999]
[null,"Aihuapi ",110,"Aihuapi  110 kV - HT3 Transformador TR3 27/40 MVA 110/66 kV ",4.1230000000000002,0,3.91,6.0000000000000001E-3,3.6280000000000001,0,4.0590000000000002,6.0000000000000001E-3,4.1230000000000002,4.1230000000000002,4.1230000000000002]
[null,"Algarrobo ",110,"Algarrobo  110 kV - H1 TR 1 110/4,6 kV 6 MVA ",3.6619999999999999,0,2.613,0,3.17,0,3.4780000000000002,0,3.6619999999999999,3.6619999999999999,3.6619999999999999]
[null,"Alonso de Córdova ",110,"Alonso de Córdova  110 kV - H1 Línea 110 kV Alonso de Córdova - Los Almendros (Apoquindo)/El Salto (Vitacura) 1",29.655000000000001,14.837,17.765000000000001,8.8859999999999992,25.681000000000001,12.849,26.622,13.32,29.655000000000001,14.818000000000001,14.837]
[null,null,null,"Alonso de Córdova  110 kV - H2 Línea 110 kV Alonso de Córdova - Los Almendros (Apoquindo) /El Salto (Vitacura 2",29.655000000000001,14.817,17.765000000000001,8.8780000000000001,25.681000000000001,12.832000000000001,26.622,13.302,29.655000000000001,14.838000000000001,14.838000000000001]
[null,null,null,"Alonso de Córdova  110 kV - HT1 Transformador TR01 50 MVA 110/12,5 kV ",29.655000000000001,0,17.765000000000001,0,25.681000000000001,0,26.622,0,29.655000000000001,29.655000000000001,29.655000000000001]
[null,null,null,"Alonso de Córdova  110 kV - HT2 Transformador TR02 50 MVA 110/12,5 kV ",29.655000000000001,0,17.765000000000001,0,25.681000000000001,0,26.622,0,29.655000000000001,29.655000000000001,29.655000000000001]
[null,null,null,"Alonso de Córdova  110 kV - HT3 Transformador TR03 50 MVA 110/12,5 kV ",29.655000000000001,0,17.765000000000001,0,25.681000000000001,0,26.622,0,29.655000000000001,29.655000000000001,29.655000000000001]
[null,null,null,"Alonso de Córdova  110 kV - H4 Transformador TR04 50 MVA 110/12,5 kV ",29.655000000000001,0,17.765000000000001,0,25.681000000000001,0,26.622,0,29.655000000000001,29.655000000000001,29.655000000000001]
[null,"Alonso de Ribera",154,"Alonso de Ribera 154 kV - AT1 Transformador Alonso de Ribera TR1 75MVA 154/66/14,8kV",14.444000000000001,0.28699999999999998,19.285,0.25600000000000001,12.456,0.248,19.576000000000001,0.26900000000000002,19.576000000000001,19.307000000000002,19.307000000000002]
[null,null,null,"Alonso de Ribera 154 kV - AT2 Transformador Alonso de Ribera TR2 75MVA 154/66/14,8kV",14.444000000000001,0.27500000000000002,19.285,0.246,12.456,0.23799999999999999,19.576000000000001,0.25900000000000001,19.576000000000001,19.317,19.317]
[null,"Altamirano ",110,"Altamirano  110 kV -  H1 Línea 110 kV Altamirano - Cerro Navia/Renca 1 ",46.216000000000001,23.108000000000001,35.414000000000001,17.707000000000001,39.936,19.968,42.691000000000003,21.344999999999999,46.216000000000001,23.108000000000001,23.108000000000001]
[null,null,null,"Altamirano  110 kV -  H2 Línea 110 kV Altamirano - Cerro Navia/Renca 2",46.216000000000001,23.108000000000001,35.414000000000001,17.707000000000001,39.936,19.968,42.691000000000003,21.344999999999999,46.216000000000001,23.108000000000001,23.108000000000001]
[null,"Alto Bonito ",110,"Alto Bonito  110 kV - H1 Línea 110 kV Alto Bonito - Melipulli ",4.4219999999999997,1.9610000000000001,4.07,2.2400000000000002,3.7909999999999999,1.6819999999999999,4.2869999999999999,2.1240000000000001,4.4219999999999997,2.4609999999999994,2.4609999999999994]
[null,null,null,"Alto Bonito  110 kV -  H2 Línea 110 kV Alto Bonito - Molinos ",4.4219999999999997,2.4620000000000002,4.07,1.83,3.7909999999999999,2.11,4.2869999999999999,2.242,4.4219999999999997,2.2400000000000002,2.4620000000000002]
[null,null,null,"Alto Bonito  110 kV - HT1 Transformador TR1 30 MVA 115/24,5 kV ",4.4219999999999997,0,4.07,0,3.7909999999999999,0,4.2869999999999999,0,4.4219999999999997,4.4219999999999997,4.4219999999999997]
[null,"Alto del Carmen ",110,"Alto del Carmen  110 kV -  En Barra",1.758,0,1.3460000000000001,0,1.5249999999999999,0,1.742,0,1.758,1.758,1.758]
[null,"Alto Hospicio ",110,"Alto Hospicio  110 kV - HT1 Transformador T1 15/12,5/10 MVA 110/13,8 kV ",3.1230000000000002,0,3.4529999999999998,0,2.681,0,3.34,0,3.4529999999999998,3.4529999999999998,3.4529999999999998]
[null,"Alto Jahuel",154,"Alto Jahuel 154 kV - A1 Línea 154 kV Alto Jahuel - Fátima/ Rancagua 1/ Tingiuririca 1",14.106999999999999,2.4700000000000002,16.902999999999999,2.1890000000000001,12.252000000000001,2.1480000000000001,16.303000000000001,2.335,16.902999999999999,14.713999999999999,14.713999999999999]
[null,null,null,"Alto Jahuel 154 kV - A2 Línea 154 kV Alto Jahuel - Fátima/ Rancagua 2/ Tingiuririca 2",14.106999999999999,2.4700000000000002,16.902999999999999,2.1880000000000002,12.252000000000001,2.1480000000000001,16.303000000000001,2.335,16.902999999999999,14.714999999999998,14.714999999999998]
[null,null,null,"Alto Jahuel 154 kV - AT6 Transformador Alto Jahuel ATR6 220/154 kV ",14.106999999999999,9.2100000000000009,16.902999999999999,12.558,12.252000000000001,7.9909999999999997,16.303000000000001,11.773999999999999,16.902999999999999,4.8969999999999985,12.558]
[null,"Alto Jahuel ",110,"Alto Jahuel  110 kV - HT1 Transformador ATR1 30 MVA 110/66/13,8 kV ",41.353000000000002,1.0620000000000001,47.74,0.96399999999999997,35.859000000000002,0.92500000000000004,46.335000000000001,1.0349999999999999,47.74,46.776000000000003,46.776000000000003]
[null,null,null,"Alto Jahuel  110 kV -  H2 Línea 110 kV Alto Jahuel - Sauzal 1",41.353000000000002,1.4359999999999999,47.74,1.2629999999999999,35.859000000000002,1.246,46.335000000000001,1.365,47.74,46.477000000000004,46.477000000000004]
[null,null,null,"Alto Jahuel  110 kV - HT2 Transformador ATR2 390 MVA 220/110/13,2 kV ",41.353000000000002,9.6660000000000004,47.74,17.858000000000001,35.859000000000002,8.4009999999999998,46.335000000000001,16.568000000000001,47.74,31.687000000000001,31.687000000000001]
[null,null,null,"Alto Jahuel  110 kV -  H1 Línea 110 kV Alto Jahuel - Sauzal 2",41.353000000000002,1.4359999999999999,47.74,1.2629999999999999,35.859000000000002,1.246,46.335000000000001,1.365,47.74,46.477000000000004,46.477000000000004]
[null,null,null,"Alto Jahuel  110 kV -  H5 Línea 110 kV Alto Jahuel - Florida (Buin) 1",41.353000000000002,13.923999999999999,47.74,13.236000000000001,35.859000000000002,12.061999999999999,46.335000000000001,13.603,47.74,34.504000000000005,34.504000000000005]
[null,null,null,"Alto Jahuel  110 kV -  H6 Línea 110 kV Alto Jahuel - Florida (Buin) 2",41.353000000000002,13.923999999999999,47.74,13.236000000000001,35.859000000000002,12.061999999999999,46.335000000000001,13.603,47.74,34.504000000000005,34.504000000000005]
[null,"Alto Melipilla ",110,"Alto Melipilla  110 kV - HT1 Transformador TR1 150 MVA 220/110/13,2 kV ",6.0389999999999997,5.2919999999999998,6.468,5.8419999999999996,5.2290000000000001,4.5839999999999996,6.3289999999999997,5.6029999999999998,6.468,0.74699999999999989,5.8419999999999996]
[null,null,null,"Alto Melipilla  110 kV -  H2 Línea 110 kV Alto Melipilla - San Antonio ",6.0389999999999997,0.34499999999999997,6.468,0.29499999999999998,5.2290000000000001,0.29899999999999999,6.3289999999999997,0.32800000000000001,6.468,6.173,6.173]
[null,null,null,"Alto Melipilla  110 kV -  H4 Línea 110 kV Alto Melipilla - Tap Off Alto Melipilla",6.0389999999999997,8.6999999999999994E-2,6.468,0.06,5.2290000000000001,7.2999999999999995E-2,6.3289999999999997,7.5999999999999998E-2,6.468,6.4080000000000004,6.4080000000000004]
[null,null,null,"Alto Melipilla  110 kV -  H3 Línea 110 kV Alto Melipilla - Leyda",6.0389999999999997,0.34499999999999997,6.468,0.29399999999999998,5.2290000000000001,0.29899999999999999,6.3289999999999997,0.32800000000000001,6.468,6.1740000000000004,6.1740000000000004]
[null,"Alto Norte ",110,"Alto Norte  110 kV -  H3 Línea 110 kV Alto Norte - Antofagasta/Tap Off La Negra ",4.5199999999999996,2.8879999999999999,3.177,1.9790000000000001,3.85,2.4500000000000002,4.1059999999999999,2.613,4.5199999999999996,1.6319999999999997,2.8879999999999999]
[null,null,null,"Alto Norte  110 kV -  H4 Línea 110 kV Alto Norte - Capricornio/Tap Off El Negro ",4.5199999999999996,1.635,3.177,1.1990000000000001,3.85,1.403,4.1059999999999999,1.494,4.5199999999999996,2.8849999999999998,2.8849999999999998]
[null,null,null,"Alto Norte  110 kV - HT1 Transformador TR1 110/13,8 kV ",4.5199999999999996,0,3.177,0,3.85,0,4.1059999999999999,0,4.5199999999999996,4.5199999999999996,4.5199999999999996]
[null,null,null,"Alto Norte  110 kV - HT2 Transformador TR2 110/13,8 kV ",4.5199999999999996,0,3.177,0,3.85,0,4.1059999999999999,0,4.5199999999999996,4.5199999999999996,4.5199999999999996]
[null,null,null,"Alto Norte  110 kV - HT3 Transformador TR3 110/13,8 kV ",4.5199999999999996,0,3.177,0,3.85,0,4.1059999999999999,0,4.5199999999999996,4.5199999999999996,4.5199999999999996]
[null,null,null,"Alto Norte  110 kV - HT4 Transformador TR4 110/13,8 kV ",4.5199999999999996,0,3.177,0,3.85,0,4.1059999999999999,0,4.5199999999999996,4.5199999999999996,4.5199999999999996]
[null,"Ancud ",110,"Ancud  110 kV - HT1 Transformador TR1 110/23 kV ",2.8420000000000001,9.0999999999999998E-2,2.3959999999999999,4.9000000000000002E-2,2.41,6.8000000000000005E-2,2.7029999999999998,7.1999999999999995E-2,2.8420000000000001,2.7509999999999999,2.7509999999999999]
[null,null,null,"Ancud  110 kV - HT2 Transformador TR2 110/110 kV (Línea 110 kV Ancud - Chiloé)",2.8420000000000001,0.79200000000000004,2.3959999999999999,0.69599999999999995,2.41,0.65600000000000003,2.7029999999999998,0.747,2.8420000000000001,2.0499999999999998,2.0499999999999998]
[null,"Andes ",110,"Andes  110 kV - H1 Línea 110 kV Andes - Los Almendros/Florida 1",28.67,14.335000000000001,20.404,10.202,24.821999999999999,12.411,26.074999999999999,13.037000000000001,28.67,14.335000000000001,14.335000000000001]
[null,null,null,"Andes  110 kV - H2 Línea 110 kV Andes - Los Almendros/Florida 2",28.67,14.335000000000001,20.404,10.202,24.821999999999999,12.411,26.074999999999999,13.037000000000001,28.67,14.335000000000001,14.335000000000001]
[null,null,null,"Andes  110 kV - HT1 Transformador TR01 50 MVA 110/12,5 kV ",28.67,0,20.404,0,24.821999999999999,0,26.074999999999999,0,28.67,28.67,28.67]
[null,null,null,"Andes  110 kV - HT4 Transformador TR04 22,4 MVA 110/12,5 kV ",28.67,0,20.404,0,24.821999999999999,0,26.074999999999999,0,28.67,28.67,28.67]
[null,"Antillanca ",110,"Antillanca  110 kV - HT1 Transformador T1 220/110/23 kV ",5.2430000000000003,3.7949999999999999,6.03,4.3099999999999996,4.617,3.2770000000000001,5.7489999999999997,4.17,6.03,1.7200000000000006,4.3099999999999996]
[null,null,null,"Antillanca  110 kV - H1 Línea 110 kV Antillanca - Central Licán/Mantilhue ",5.2430000000000003,0.69899999999999995,6.03,0.76200000000000001,4.617,0.59899999999999998,5.7489999999999997,0.72899999999999998,6.03,5.2680000000000007,5.2680000000000007]
[null,null,null,"Antillanca  110 kV - H2 Línea 110 kV Antillanca - Aihuapi ",5.2430000000000003,0.69499999999999995,6.03,0.74,4.617,0.627,5.7489999999999997,0.71399999999999997,6.03,5.29,5.29]
[null,null,null,"Antillanca  110 kV - H3 Línea 110 kV Antillanca - Río Bonito ",5.2430000000000003,5.5E-2,6.03,0.218,4.617,0.12,5.7489999999999997,0.14899999999999999,6.03,5.8120000000000003,5.8120000000000003]
[null,"Antofagasta ",110,"Antofagasta  110 kV - HT1 Transformador TR1 110/13,8 kV ",6.5960000000000001,0,5.7480000000000002,0,5.58,0,6.242,0,6.5960000000000001,6.5960000000000001,6.5960000000000001]
[null,null,null,"Antofagasta  110 kV -  H1 Línea 110 kV Antofagasta -Tap Off Uribe/Capricornio",6.5960000000000001,4,5.7480000000000002,3.7789999999999999,5.58,3.3650000000000002,6.242,3.9550000000000001,6.5960000000000001,2.5960000000000001,4]
[null,null,null,"Antofagasta  110 kV -  H3 Línea 110 kV Antofagasta - Desalant/Mejillones",6.5960000000000001,1.738,5.7480000000000002,1.2729999999999999,5.58,1.4910000000000001,6.242,1.546,6.5960000000000001,4.8580000000000005,4.8580000000000005]
[null,null,null,"Antofagasta  110 kV -  H2 Línea 110 kV Antofagasta - Tap Off La Negra/Alto Norte",6.5960000000000001,0.86799999999999999,5.7480000000000002,0.7,5.58,0.73099999999999998,6.242,0.8,6.5960000000000001,5.7279999999999998,5.7279999999999998]
[null,"Antucoya ",110,"Antucoya  110 kV -  HT Transformador TR01 10/12,5 MVA 110/23 kV ",1.6739999999999999,0.61899999999999999,0.79500000000000004,0.19600000000000001,1.4490000000000001,0.53600000000000003,1.5169999999999999,0.54200000000000004,1.6739999999999999,1.0549999999999999,1.0549999999999999]
[null,"Apoquindo ",110,"Apoquindo  110 kV -  H1 Línea 110 kV Apoquindo - Los Almendros (Los Dominicos) / El Salto  (Alonso de Córdova) 1 ",29.666,15.339,17.896000000000001,9.1509999999999998,25.690999999999999,13.282999999999999,26.649000000000001,13.749000000000001,29.666,14.327,15.339]
[null,null,null,"Apoquindo  110 kV -  H2 Línea 110 kV Apoquindo - Los Almendros  (Los Dominicos) /El Salto (Alonso de Córdova) 2",29.666,14.327999999999999,17.896000000000001,8.7449999999999992,25.690999999999999,12.407999999999999,26.649000000000001,12.901999999999999,29.666,15.338000000000001,15.338000000000001]
[null,"Arica ",110,"Arica  110 kV - HT3 Autotransformador 110/66/13,8 kV ",1.56,1.0429999999999999,2.302,1.7929999999999999,1.337,0.9,2.7010000000000001,2.339,2.7010000000000001,0.51700000000000013,2.339]
[null,"Atacama Kozán ",110,"Atacama Kozán  110 kV -  En Barra",3.7530000000000001,0,2.87,0,3.2469999999999999,0,3.54,0,3.7530000000000001,3.7530000000000001,3.7530000000000001]
[null,"Bajo Melipilla ",110,"Bajo Melipilla  110 kV - HT1 Transformador TR01 25/20/15 MVA 110/13,2 kV ",5.1970000000000001,0,4.9649999999999999,0,4.5,0,5.0910000000000002,0,5.1970000000000001,5.1970000000000001,5.1970000000000001]
[null,null,null,"Bajo Melipilla  110 kV - HT2 Transformador TR02 40/50 MVA 110/66 kV ",5.1970000000000001,8.6999999999999994E-2,4.9649999999999999,5.5E-2,4.5,7.2999999999999995E-2,5.0910000000000002,7.6999999999999999E-2,5.1970000000000001,5.1100000000000003,5.1100000000000003]
[null,null,null,"Bajo Melipilla  110 kV - H3 Línea 110 kV Bajo Melipilla - Tap Alto Melipilla ",5.1970000000000001,5.1100000000000003,4.9649999999999999,4.9109999999999996,4.5,4.4269999999999996,5.0910000000000002,5.0170000000000003,5.1970000000000001,8.6999999999999744E-2,5.1100000000000003]
[null,null,null,"Bajo Melipilla  110 kV - H4 Línea 110 kV Bajo Melipilla - Carga Móvil ",5.1970000000000001,0,4.9649999999999999,0,4.5,0,5.0910000000000002,0,5.1970000000000001,5.1970000000000001,5.1970000000000001]
[null,null,null,"Bajo Melipilla  110 kV - HT3 Transformador TR03 25/20/15 MVA 110/13,2 kV ",5.1970000000000001,0,4.9649999999999999,0,4.5,0,5.0910000000000002,0,5.1970000000000001,5.1970000000000001,5.1970000000000001]
[null,"Baños del Toro ",110,"Baños del Toro  110 kV - H1 Transformador Baños del Toro (El Indio) 110/13.2 kV",0.79800000000000004,0,0.46500000000000002,0,0.69099999999999995,0,0.747,0,0.79800000000000004,0.79800000000000004,0.79800000000000004]
[null,"Batuco ",110,"Batuco  110 kV -  H1 Línea 110 kV Batuco - Tap Off Punta Peuco/Cerro Navia 1",17.370999999999999,8.6850000000000005,11.714,5.8570000000000002,15.026999999999999,7.5140000000000002,15.814,7.907,17.370999999999999,8.6859999999999982,8.6859999999999982]
[null,null,null,"Batuco  110 kV -  H2 Línea 110 kV Batuco - Tap Off Punta Peuco/Cerro Navia 2",17.370999999999999,8.6850000000000005,11.714,5.8570000000000002,15.026999999999999,7.5140000000000002,15.814,7.907,17.370999999999999,8.6859999999999982,8.6859999999999982]
[null,null,null,"Batuco  110 kV - HT1 Transformador TR01 37,5 MVA 110/23,5 kV ",17.370999999999999,0,11.714,0,15.026999999999999,0,15.814,0,17.370999999999999,17.370999999999999,17.370999999999999]
[null,null,null,"Batuco  110 kV - HT2 Transformador TR02 37,5 MVA 110/23,5 kV ",17.370999999999999,0,11.714,0,15.026999999999999,0,15.814,0,17.370999999999999,17.370999999999999,17.370999999999999]
[null,null,null,"Batuco  110 kV - HT3 Transformador TR03 50 MVA 110/23,5 kV ",17.370999999999999,0,11.714,0,15.026999999999999,0,15.814,0,17.370999999999999,17.370999999999999,17.370999999999999]
[null,"Bicentenario ",110,"Bicentenario  110 kV -  H1 Línea 110 kV Bicentenario - Cerro Navia (Santa Marta) /Chena 1",39.369,19.684999999999999,25.782,12.891,34.097999999999999,17.048999999999999,35.665999999999997,17.832999999999998,39.369,19.684000000000001,19.684999999999999]
[null,null,null,"Bicentenario  110 kV -  H2 Línea 110 kV Bicentenario - Cerro Navia (Santa Marta) /Chena 2",39.369,19.684999999999999,25.782,12.891,34.097999999999999,17.048999999999999,35.665999999999997,17.832999999999998,39.369,19.684000000000001,19.684999999999999]
[null,null,null,"Bicentenario  110 kV - HT1 Transformador TR01 25 MVA 110/12,5 kV ",39.369,0,25.782,0,34.097999999999999,0,35.665999999999997,0,39.369,39.369,39.369]
[null,null,null,"Bicentenario  110 kV - HT2 Transformador TR02 25 MVA 110/13,2 kV ",39.369,0,25.782,0,34.097999999999999,0,35.665999999999997,0,39.369,39.369,39.369]
[null,"Bocamina",154,"Bocamina 154 kV - A1 Línea 154 kV Bocamina - Lagunillas",12.144,10.287000000000001,13.696,10.605,10.686999999999999,8.86,13.053000000000001,10.598000000000001,13.696,3.0909999999999993,10.605]
[null,null,null,"Bocamina 154 kV - AT1 Transformador Bocamina TR01 147MVA 161/13.8 kV N°1",12.144,1.8660000000000001,13.696,3.1179999999999999,10.686999999999999,1.86,13.053000000000001,2.6419999999999999,13.696,10.577999999999999,10.577999999999999]
[null,null,null,"Bocamina 154 kV - AT2 Transformador Bocamina 161/13.8 kV SSAA",12.144,0,13.696,0,10.686999999999999,0,13.053000000000001,0,13.696,13.696,13.696]
[null,"Bollenar ",110,"Bollenar  110 kV - HT Transformador TR1 20/16 MVA 110/23-13,8 kV ",3.55,0,2.6520000000000001,0,3.0750000000000002,0,3.3279999999999998,0,3.55,3.55,3.55]
[null,"Bombeo 2 ",110,"Bombeo 2  110 kV - H1 Transformador TR1 110/4.16 kV 10 MVA ",2.0609999999999999,0,1.319,0,1.7829999999999999,0,1.8759999999999999,0,2.0609999999999999,2.0609999999999999,2.0609999999999999]
[null,"Bombeo 1 y Desaladora",110,"Bombeo 1 y Desaladora 110 kV - H2 Transformador N°1 110/4.16 kV Planta Desaladora y Bombeo 1",1.62,0,1.038,0,1.4019999999999999,0,1.4730000000000001,0,1.62,1.62,1.62]
[null,"Bosquemar ",110,"Bosquemar  110 kV - H1 Línea 110 kV Bosquemar - Concon",13.227,13.227,7.84,7.84,11.522,11.522,12.077,12.077,13.227,0,13.227]
[null,"Brasil ",110,"Brasil  110 kV -  H1 Línea 110 kV Brasil - Renca (Carrascal) 1 ",39.89,19.945,24.218,12.109,34.476999999999997,17.239000000000001,35.750999999999998,17.875,39.89,19.945,19.945]
[null,null,null,"Brasil  110 kV -  H2 Línea 110 kV Brasil - Renca (Carrascal)  2",39.89,19.945,24.218,12.109,34.476999999999997,17.239000000000001,35.750999999999998,17.875,39.89,19.945,19.945]
[null,"Buin ",110,"Buin  110 kV -  H1 Línea 110 kV Buin - Lo Espejo (San Bernardo) 2 ",42.084000000000003,5.3159999999999998,47.087000000000003,4.1849999999999996,36.491999999999997,4.6040000000000001,45.753999999999998,4.8310000000000004,47.087000000000003,42.902000000000001,42.902000000000001]
[null,null,null,"Buin  110 kV -  H2 Línea 110 kV Buin - Lo Espejo (San Bernardo)  1 ",42.084000000000003,5.3159999999999998,47.087000000000003,4.1849999999999996,36.491999999999997,4.6040000000000001,45.753999999999998,4.8310000000000004,47.087000000000003,42.902000000000001,42.902000000000001]
[null,null,null,"Buin  110 kV -  H3 Línea 110 kV Buin - Florida (La Pintana)  2",42.084000000000003,9.8580000000000005,47.087000000000003,10.656000000000001,36.491999999999997,8.5419999999999998,45.753999999999998,10.394,47.087000000000003,36.431000000000004,36.431000000000004]
[null,null,null,"Buin  110 kV -  H4 Línea 110 kV Buin - Florida  (La Pintana) 1",42.084000000000003,9.8580000000000005,47.087000000000003,10.656000000000001,36.491999999999997,8.5419999999999998,45.753999999999998,10.394,47.087000000000003,36.431000000000004,36.431000000000004]
[null,null,null,"Buin  110 kV - HT1 Transformador TR01 400 MVA 220/110/13,8 kV ",42.084000000000003,11.821,47.087000000000003,17.478000000000002,36.491999999999997,10.273,45.753999999999998,15.868,47.087000000000003,30.263000000000005,30.263000000000005]
[null,null,null,"Buin  110 kV - CCE1A Banco de Condensadores 1",42.084000000000003,0,47.087000000000003,0,36.491999999999997,0,45.753999999999998,0,47.087000000000003,47.087000000000003,47.087000000000003]
[null,"Cabildo ",110,"Cabildo  110 kV - HT2 Transformador TR2 13/10 MVA 110/24-14,4 kV ",2.0089999999999999,0,1.262,0,1.7370000000000001,0,1.9,0,2.0089999999999999,2.0089999999999999,2.0089999999999999]
[null,null,null,"Cabildo  110 kV - HT1 Transformador TR1 30/24/18 MVA 110/25 kV",2.0089999999999999,0,1.262,0,1.7370000000000001,0,1.9,0,2.0089999999999999,2.0089999999999999,2.0089999999999999]
[null,"Calama ",110,"Calama  110 kV - HT1 Transformador TR01 33/25 MVA 110/23 kV ",4.6749999999999998,5.1999999999999998E-2,5.5259999999999998,4.2999999999999997E-2,3.8340000000000001,4.4999999999999998E-2,5.5410000000000004,4.7E-2,5.5410000000000004,5.4940000000000007,5.4940000000000007]
[null,null,null,"Calama  110 kV - HT4 Transformador TR04 33/25 MVA 110/23 kV ",4.6749999999999998,5.2999999999999999E-2,5.5259999999999998,4.3999999999999997E-2,3.8340000000000001,4.5999999999999999E-2,5.5410000000000004,4.8000000000000001E-2,5.5410000000000004,5.4930000000000003,5.4930000000000003]
[null,null,null,"Calama  110 kV - H3 Línea 110 kV Calama - Valle de los Vientos ",4.6749999999999998,0.41,5.5259999999999998,0.56299999999999994,3.8340000000000001,0.19400000000000001,5.5410000000000004,0.78200000000000003,5.5410000000000004,4.9630000000000001,4.9630000000000001]
[null,null,null,"Calama  110 kV - HT5 Transformador TR1P 55/45/5 MVA 210/110/12,2 kV ",4.6749999999999998,4.2270000000000003,5.5259999999999998,4.9329999999999998,3.8340000000000001,3.637,5.5410000000000004,4.7839999999999998,5.5410000000000004,0.75700000000000056,4.9329999999999998]
[null,null,null,"Calama  110 kV - H2 Línea 110 kV Calama - San Pedro ",4.6749999999999998,0,5.5259999999999998,0,3.8340000000000001,0,5.5410000000000004,0,5.5410000000000004,5.5410000000000004,5.5410000000000004]
[null,"Calbuco ",110,"Calbuco  110 kV - HT1 Transformador TR1 16 MVA 115/69/24 kV ",2.5270000000000001,0,1.794,0,2.1760000000000002,0,2.3460000000000001,0,2.5270000000000001,2.5270000000000001,2.5270000000000001]
[null,"Caldera ",110,"Caldera  110 kV - HT1 Transformador T1 12/10 MVA 110/23-13.2 kV ",1.4970000000000001,0,0.999,0,1.296,0,1.4019999999999999,0,1.4970000000000001,1.4970000000000001,1.4970000000000001]
[null,"Canal Melado ",110,"Canal Melado  110 kV - HT Transformador TR 220/110/13.8 kV 70 MVA ",3.6160000000000001,2.9609999999999999,4.7539999999999996,4.0490000000000004,3.0990000000000002,2.5680000000000001,4.7530000000000001,4.056,4.7539999999999996,0.70499999999999918,4.056]
[null,"CAP Rengo",154,"CAP Rengo 154 kV -  En Barra",10.117000000000001,0,7.7619999999999996,0,8.8140000000000001,0,9.4640000000000004,0,10.117000000000001,10.117000000000001,10.117000000000001]
[null,"Capricornio ",110,"Capricornio  110 kV - HT1 Transformador TR01 80/80/20 MVA 220/110/13,8 kV ",6.1029999999999998,2.8439999999999999,6.36,3.6030000000000002,5.2069999999999999,2.4590000000000001,6.335,3.294,6.36,3.2589999999999999,3.6030000000000002]
[null,null,null,"Capricornio  110 kV - H2 Línea 110 kV Capricornio - Alto Norte/Tap Off El Negro ",6.1029999999999998,0.89200000000000002,6.36,0.73499999999999999,5.2069999999999999,0.752,6.335,0.82599999999999996,6.36,5.625,5.625]
[null,null,null,"Capricornio  110 kV - H1 Línea 110 kV Capricornio - Tap Off Uribe/Antofagasta",6.1029999999999998,2.3929999999999998,6.36,2.0409999999999999,5.2069999999999999,2.0219999999999998,6.335,2.2370000000000001,6.36,4.3190000000000008,4.3190000000000008]
[null,null,null,"Capricornio  110 kV - H3 Línea 110 kV Capricornio - Sierra Miranda ",6.1029999999999998,0,6.36,0,5.2069999999999999,0,6.335,0,6.36,6.36,6.36]
[null,"Cardones ",110,"Cardones  110 kV - H8 Línea 110 kV Cardones - Central Cenizas ",8.3209999999999997,0.497,9.98,0.78300000000000003,7.1840000000000002,0.42899999999999999,9.6940000000000008,0.74199999999999999,9.98,9.197000000000001,9.197000000000001]
[null,null,null,"Cardones  110 kV - H3 Línea 110 kV Cardones - Copiapo",8.3209999999999997,0,9.98,1E-3,7.1840000000000002,0,9.6940000000000008,1E-3,9.98,9.979000000000001,9.979000000000001]
[null,null,null,"Cardones  110 kV - H2 Línea 110 kV Cardones - Maintencillo ",8.3209999999999997,0.96499999999999997,9.98,0.84,7.1840000000000002,0.83399999999999996,9.6940000000000008,0.92200000000000004,9.98,9.14,9.14]
[null,null,null,"Cardones  110 kV - HT1 AutoTransformador ATR1 75 MVA 220/115/13,8 kV ",8.3209999999999997,2.431,9.98,2.84,7.1840000000000002,2.0990000000000002,9.6940000000000008,2.7410000000000001,9.98,7.1400000000000006,7.1400000000000006]
[null,null,null,"Cardones  110 kV - H4 Línea 110 kV Cardones - Copayapu/Cerrillos/Tierra Amarilla ",8.3209999999999997,0,9.98,0.129,7.1840000000000002,0,9.6940000000000008,0.16200000000000001,9.98,9.8510000000000009,9.8510000000000009]
[null,null,null,"Cardones  110 kV - HT2 AutoTransformador ATR2 75 MVA 220/115/13,8 kV ",8.3209999999999997,2.278,9.98,2.7210000000000001,7.1840000000000002,1.9670000000000001,9.6940000000000008,2.605,9.98,7.2590000000000003,7.2590000000000003]
[null,null,null,"Cardones  110 kV - H6 Línea 110 kV Cardones - Fundición Paipote ",8.3209999999999997,0,9.98,0,7.1840000000000002,0,9.6940000000000008,0,9.98,9.98,9.98]
[null,null,null,"Cardones  110 kV - HT3 AutoTransformador ATR3 79 MVA 220/115/13,8 kV ",8.3209999999999997,2.2530000000000001,9.98,2.7559999999999998,7.1840000000000002,1.9450000000000001,9.6940000000000008,2.637,9.98,7.2240000000000002,7.2240000000000002]
[null,null,null,"Cardones  110 kV - H9 Línea 110 kV Cardones - Travesía ",8.3209999999999997,0,9.98,0,7.1840000000000002,0,9.6940000000000008,0,9.98,9.98,9.98]
[null,null,null,"Cardones  110 kV - H7 Línea 110 kV Cardones - Magnetita ",8.3209999999999997,0,9.98,0,7.1840000000000002,0,9.6940000000000008,0,9.98,9.98,9.98]
[null,null,null,"Cardones  110 kV - H1 Línea 110 kV Cardones - Refugio ",8.3209999999999997,0,9.98,3.0000000000000001E-3,7.1840000000000002,0,9.6940000000000008,4.0000000000000001E-3,9.98,9.9770000000000003,9.9770000000000003]
[null,"Carrascal ",110,"Carrascal  110 kV - H1 Línea 110 kV Carrascal - Renca/Brasil 1 ",47.651000000000003,23.824999999999999,38.448999999999998,19.225000000000001,41.17,20.585000000000001,44.445999999999998,22.222999999999999,47.651000000000003,23.826000000000004,23.826000000000004]
[null,null,null,"Carrascal  110 kV - H2 Línea 110 kV Carrascal - Renca/Brasil 2",47.651000000000003,23.824999999999999,38.448999999999998,19.225000000000001,41.17,20.585000000000001,44.445999999999998,22.222999999999999,47.651000000000003,23.826000000000004,23.826000000000004]
[null,"Casas Viejas ",110,"Casas Viejas  110 kV -  En Barra",3.6339999999999999,0,2.3769999999999998,0,3.1419999999999999,0,3.4319999999999999,0,3.6339999999999999,3.6339999999999999,3.6339999999999999]
[null,"Castilla ",110,"Castilla  110 kV -  En Barra",4.0640000000000001,0,2.7909999999999999,0,3.516,0,3.8069999999999999,0,4.0640000000000001,4.0640000000000001,4.0640000000000001]
[null,"Castro ",110,"Castro  110 kV - H1 Línea 110 kV Castro - Gamboa",3.8759999999999999,3.5190000000000001,4.5830000000000002,4.2859999999999996,3.198,2.883,4.66,4.3730000000000002,4.66,0.35699999999999976,4.3730000000000002]
[null,null,null,"Castro  110 kV - H2 Línea 110 kV Castro - Chonchi ",3.8759999999999999,0.35699999999999998,4.5830000000000002,0.29699999999999999,3.198,0.315,4.66,0.32600000000000001,4.66,4.3340000000000005,4.3340000000000005]
[null,null,null,"Castro  110 kV - HT1 Transformador TR1 110/23 kV ",3.8759999999999999,0,4.5830000000000002,0,3.198,0,4.66,0,4.66,4.66,4.66]
[null,"Central Andes Generación ",110,"Central Andes Generación  110 kV - HT Transformador TR1 63 MVA 110/10,5 kV ",9.1479999999999997,0.8,11.657999999999999,1.034,7.8760000000000003,0.68400000000000005,11.564,0.999,11.657999999999999,10.623999999999999,10.623999999999999]
[null,"Central Cenizas ",110,"Central Cenizas  110 kV - HT Transformador TR01 35/30 MVA 110/11 kV ",8.1389999999999993,0.497,9.61,0.80800000000000005,7.0279999999999996,0.435,9.3140000000000001,0.76300000000000001,9.61,8.8019999999999996,8.8019999999999996]
[null,"Central Chacayes",110,"Central Chacayes 110 kV -  En Barra",10.532,0,11.122999999999999,0,9.2430000000000003,0,11.131,0,11.131,11.131,11.131]
[null,"Central Chañares ",110,"Central Chañares  110 kV - HT1 Transformador TR1 72/50 MVA 110/33 kV ",6.37,0,6.5339999999999998,0.70099999999999996,5.4960000000000004,0,6.5419999999999998,0.72599999999999998,6.5419999999999998,6.37,6.37]
[null,"Central Colmito ",110,"Central Colmito  110 kV - H1 Línea 110 kV Colmito - Torquemada",20.562000000000001,19.114000000000001,18.655000000000001,15.785,17.960999999999999,16.75,20.027000000000001,17.891999999999999,20.562000000000001,2.870000000000001,19.114000000000001]
[null,"Central Curillinque",154,"Central Curillinque 154 kV - AT Transformador Central Curillinque 154/13.8 kV",5.99,1.133,5.5640000000000001,1.544,5.0069999999999997,0.998,5.8959999999999999,1.3759999999999999,5.99,4.8570000000000002,4.8570000000000002]
[null,"Central Diesel Enaex ",110,"Central Diesel Enaex  110 kV -  En Barra",6.9340000000000002,0,7.2190000000000003,0,5.8959999999999999,0,7.1680000000000001,0,7.2190000000000003,7.2190000000000003,7.2190000000000003]
[null,"Central Diesel Tamaya ",110,"Central Diesel Tamaya  110 kV - H4 Línea 110 kV Central Diesel Tamaya - Central Tocopilla ",11.045,3.258,14.013,3.07,9.3569999999999993,2.8210000000000002,14.209,3.157,14.209,11.052,11.052]
[null,null,null,"Central Diesel Tamaya  110 kV - H2 Línea 110 kV Central Diesel Tamaya - Central Tocopilla ",11.045,3.665,14.013,3.399,9.3569999999999993,3.173,14.209,3.5190000000000001,14.209,10.69,10.69]
[null,null,null,"Central Diesel Tamaya  110 kV - H1 Línea 110 kV Central Diesel Tamaya - Salar",11.045,0.85299999999999998,14.013,0.76900000000000002,9.3569999999999993,0.73399999999999999,14.209,0.81100000000000005,14.209,13.398,13.398]
[null,null,null,"Central Diesel Tamaya  110 kV - H3 Línea 110 kV Central Diesel Tamaya - A",11.045,0.90800000000000003,14.013,0.83699999999999997,9.3569999999999993,0.78200000000000003,14.209,0.872,14.209,13.337,13.337]
[null,null,null,"Central Diesel Tamaya  110 kV - HT1 Transformador TR1 50/33,3 MVA 110/11 kV ",11.045,0.79500000000000004,14.013,1.9870000000000001,9.3569999999999993,0.621,14.209,2.3119999999999998,14.209,12.026,12.026]
[null,null,null,"Central Diesel Tamaya  110 kV - HT2 Transformador TR2 50/33,3 MVA 110/11 kV ",11.045,0.79500000000000004,14.013,1.9870000000000001,9.3569999999999993,0.621,14.209,2.3119999999999998,14.209,12.026,12.026]
[null,null,null,"Central Diesel Tamaya  110 kV - HT3 Transformador TR3 50/33,3 MVA 110/11 kV ",11.045,0.79500000000000004,14.013,1.9870000000000001,9.3569999999999993,0.621,14.209,2.3119999999999998,14.209,12.026,12.026]
[null,null,null,"Central Diesel Tamaya  110 kV - HT4 Transformador TR04 10,5/9,38/7,5 MVA 110/23 kV ",11.045,0,14.013,0,9.3569999999999993,0,14.209,0,14.209,14.209,14.209]
[null,"Central Emelda ",110,"Central Emelda  110 kV - H1 Transformador TR01 110/10.5 kV",8.6519999999999992,0.73099999999999998,10.179,1.2310000000000001,7.452,0.64,9.9510000000000005,1.1439999999999999,10.179,8.9480000000000004,8.9480000000000004]
[null,null,null,"Central Emelda  110 kV - H2 Transformador TR02 110/11.5 kV",8.6519999999999992,0.73099999999999998,10.179,1.2310000000000001,7.452,0.64,9.9510000000000005,1.1439999999999999,10.179,8.9480000000000004,8.9480000000000004]
[null,"Central Isla B1",154,"Central Isla B1 154 kV -  En Barra",5.8310000000000004,0,5.2619999999999996,0,4.8129999999999997,0,5.64,0,5.8310000000000004,5.8310000000000004,5.8310000000000004]
[null,"Central Isla B2",154,"Central Isla B2 154 kV -  En Barra",5.8310000000000004,0,5.2619999999999996,0,4.8129999999999997,0,5.64,0,5.8310000000000004,5.8310000000000004,5.8310000000000004]
[null,"Central Javiera",110,"Central Javiera 110 kV - H1 Línea 110 kV Central Javiera - Planta de Óxidos",3.84,0,4.5659999999999998,3.0000000000000001E-3,3.3210000000000002,0,4.6970000000000001,3.0000000000000001E-3,4.6970000000000001,4.694,4.694]
[null,null,null,"Central Javiera 110 kV - H2 Línea 110 kV Central Javiera - Diego de Almagro",3.84,3.84,4.5659999999999998,3.4630000000000001,3.3210000000000002,3.3210000000000002,4.6970000000000001,3.7450000000000001,4.6970000000000001,1.1029999999999998,3.84]
[null,null,null,"Central Javiera 110 kV - HT1 Transformador TR1 110/22 kV",3.84,0,4.5659999999999998,1.111,3.3210000000000002,0,4.6970000000000001,1.363,4.6970000000000001,3.84,3.84]
[null,"Central Laguna Verde ",110,"Central Laguna Verde  110 kV - H1 Línea 110 kV Laguna Verde - Agua Santa 1",10.093999999999999,3.9159999999999999,8.6720000000000006,2.7879999999999998,8.7590000000000003,3.4020000000000001,9.9079999999999995,3.613,10.093999999999999,6.2949999999999999,6.2949999999999999]
[null,null,null,"Central Laguna Verde  110 kV - H2 Línea 110 kV Laguna Verde - Agua Santa 2",10.093999999999999,4.2,8.6720000000000006,2.9239999999999999,8.7590000000000003,3.6480000000000001,9.9079999999999995,3.8450000000000002,10.093999999999999,6.0629999999999988,6.0629999999999988]
[null,null,null,"Central Laguna Verde  110 kV - HT3 AutoTransformador ATR 60 MVA 110/66 kV",10.093999999999999,0.74,8.6720000000000006,0.66600000000000004,8.7590000000000003,0.64,9.9079999999999995,0.73799999999999999,10.093999999999999,9.3539999999999992,9.3539999999999992]
[null,null,null,"Central Laguna Verde  110 kV - HT4 Transformador TRTG 28,8 MVA 110/11.5 kV ",10.093999999999999,0.40500000000000003,8.6720000000000006,0.88300000000000001,8.7590000000000003,0.35799999999999998,9.9079999999999995,0.70799999999999996,10.093999999999999,9.6890000000000001,9.6890000000000001]
[null,null,null,"Central Laguna Verde  110 kV - H5 Transformador TR1 30 MVA 110/12 kV  ",10.093999999999999,0.85699999999999998,8.6720000000000006,1.4330000000000001,8.7590000000000003,0.73599999999999999,9.9079999999999995,1.1910000000000001,10.093999999999999,9.2370000000000001,9.2370000000000001]
[null,"Central Las Piedras",110,"Central Las Piedras 110 kV -  En Barra",8.7349999999999994,0,7.0629999999999997,0,7.4720000000000004,0,8.25,0,8.7349999999999994,8.7349999999999994,8.7349999999999994]
[null,"Central Licán",110,"Central Licán 110 kV - H1 Línea 110 kV Central Lican - Mantilhue/Antillanca",3.371,2.9430000000000001,3.536,2.871,2.9380000000000002,2.5649999999999999,3.577,2.9870000000000001,3.577,0.66500000000000004,2.9870000000000001]
[null,"Central Lomas Los Colorados ",110,"Central Lomas Los Colorados  110 kV - HT1 Transformador TR1 110/23 kV",4.9409999999999998,0.47699999999999998,4.2859999999999996,1.0109999999999999,4.2759999999999998,0.41199999999999998,4.9980000000000002,0.81299999999999994,4.9980000000000002,4.4639999999999995,4.4639999999999995]
[null,"Central Los Hierros ",110,"Central Los Hierros  110 kV - H Línea 110 kV Central Los Hierros - Canal Melado ",2.9750000000000001,2.4079999999999999,3.399,2.4889999999999999,2.544,2.0819999999999999,3.3530000000000002,2.5760000000000001,3.399,0.91000000000000014,2.5760000000000001]
[null,"Central Los Hierros II ",110,"Central Los Hierros II  110 kV - H Línea 110 kV Central Los Hierros II - Canal Melado ",3.25,3.1259999999999999,3.806,3.7160000000000002,2.7810000000000001,2.6840000000000002,3.7749999999999999,3.673,3.806,0.12400000000000011,3.7160000000000002]
[null,"Central Los Quilos ",110,"Central Los Quilos  110 kV -  En Barra",10.183,0,11.045,0,9.0820000000000007,0,10.83,0,11.045,11.045,11.045]
[null,"Central Maitenes ",110,"Central Maitenes  110 kV - T4 Transformador TR GE 110/12 kV ",8.1440000000000001,0,6.8179999999999996,0.74,6.9429999999999996,0,8.1219999999999999,0.64800000000000002,8.1440000000000001,8.1440000000000001,8.1440000000000001]
[null,null,null,"Central Maitenes  110 kV - H1 Línea 110 kV Central Maitenes - Tap Off La Laja 1",8.1440000000000001,3.8370000000000002,6.8179999999999996,2.6619999999999999,6.9429999999999996,3.298,8.1219999999999999,3.552,8.1440000000000001,4.57,4.57]
[null,null,null,"Central Maitenes  110 kV - H2 Línea 110 kV Central Maitenes - Tap Off La Laja 2",8.1440000000000001,3.8370000000000002,6.8179999999999996,2.6619999999999999,6.9429999999999996,3.298,8.1219999999999999,3.552,8.1440000000000001,4.57,4.57]
[null,"Central Mejillones ",110,"Central Mejillones  110 kV -  En Barra",6.9930000000000003,0,7.2560000000000002,0,5.9470000000000001,0,7.2329999999999997,0,7.2560000000000002,7.2560000000000002,7.2560000000000002]
[null,"Central Nueva Renca",110,"Central Nueva Renca 110 kV - 52GV Transformador TR01 205MVA 110/15,75kV (UG Vapor)",51.707000000000001,3.8090000000000002,48.497999999999998,5.718,44.664000000000001,3.1920000000000002,50.991999999999997,5.0519999999999996,51.707000000000001,47.898000000000003,47.898000000000003]
[null,"Central Olivos ",110,"Central Olivos  110 kV -  En Barra",8.202,0,9.1370000000000005,0,6.9329999999999998,0,9.173,0,9.173,9.173,9.173]
[null,"Central Parque Solar Los Loros",110,"Central Parque Solar Los Loros 110 kV - H1 Línea 110 kV Central PV Los Loros - Los Loros 1",1.8380000000000001,1.8380000000000001,2.343,1.681,1.591,1.591,2.448,1.8129999999999999,2.448,0.66199999999999992,1.8380000000000001]
[null,null,null,"Central Parque Solar Los Loros 110 kV - HT1 Transformador TR1 24/30 MVA 110/23 kV N°1",1.8380000000000001,0,2.343,0.33100000000000002,1.591,0,2.448,0.45300000000000001,2.448,2.012,2.012]
[null,null,null,"Central Parque Solar Los Loros 110 kV - HT2 Transformador TR2 24/30 MVA 110/23 kV N°2",1.8380000000000001,0,2.343,0.33100000000000002,1.591,0,2.448,0.45300000000000001,2.448,2.012,2.012]
[null,"Central Puntilla ",110,"Central Puntilla  110 kV -  En Barra",8.6549999999999994,0,6.4329999999999998,0,7.4909999999999997,0,8.4529999999999994,0,8.6549999999999994,8.6549999999999994,8.6549999999999994]
[null,"Central PV El Salvador",110,"Central PV El Salvador 110 kV - H1 Línea 110kV Central PV El Salvador - Diego de Almagro/El Salvador",5.3010000000000002,0,4.34,0,4.58,0,5.0149999999999997,0,5.3010000000000002,5.3010000000000002,5.3010000000000002]
[null,"Central Queltehues ",110,"Central Queltehues  110 kV - H1 Línea 110 kV Central Queltehues - Tap Off La Laja 1",6.0129999999999999,2.5030000000000001,5.1319999999999997,1.7290000000000001,5.0830000000000002,2.1619999999999999,6.0359999999999996,2.319,6.0359999999999996,3.7169999999999996,3.7169999999999996]
[null,null,null,"Central Queltehues  110 kV - H2 Línea 110 kV Central Queltehues - Tap Off La Laja 2",6.0129999999999999,2.5030000000000001,5.1319999999999997,1.7290000000000001,5.0830000000000002,2.1619999999999999,6.0359999999999996,2.319,6.0359999999999996,3.7169999999999996,3.7169999999999996]
[null,null,null,"Central Queltehues  110 kV - HT1 Transformador TR1 28 MVA 110/12 kV ",6.0129999999999999,0.22700000000000001,5.1319999999999997,0.53800000000000003,5.0830000000000002,0.16800000000000001,6.0359999999999996,0.45900000000000002,6.0359999999999996,5.7859999999999996,5.7859999999999996]
[null,null,null,"Central Queltehues  110 kV - HT2 Transformador TR2 28 MVA 110/12 kV ",6.0129999999999999,0.222,5.1319999999999997,0.47599999999999998,5.0830000000000002,0.16400000000000001,6.0359999999999996,0.40799999999999997,6.0359999999999996,5.7909999999999995,5.7909999999999995]
[null,null,null,"Central Queltehues  110 kV - HT3 Transformador TR3 28 MVA 110/12 kV ",6.0129999999999999,0.21199999999999999,5.1319999999999997,0.10299999999999999,5.0830000000000002,0.157,6.0359999999999996,0.16800000000000001,6.0359999999999996,5.8679999999999994,5.8679999999999994]
[null,null,null,"Central Queltehues  110 kV - HT5 Transformador TR Aux 5 MVA 110/12 kV ",6.0129999999999999,0.125,5.1319999999999997,6.4000000000000001E-2,5.0830000000000002,9.7000000000000003E-2,6.0359999999999996,0.10199999999999999,6.0359999999999996,5.9339999999999993,5.9339999999999993]
[null,"Central Quintero",110,"Central Quintero 110 kV -  En Barra",25.042000000000002,0,8.3829999999999991,0,21.823,0,22.416,0,25.042000000000002,25.042000000000002,25.042000000000002]
[null,"Central Renca",110,"Central Renca 110 kV - H6 Acoplador de Barras BP1 - BP3",51.707000000000001,2.89,48.497999999999998,6.6,44.664000000000001,2.4700000000000002,50.991999999999997,5.65,51.707000000000001,48.817,48.817]
[null,"Central Río Huasco",110,"Central Río Huasco 110 kV - HT1 Transformador T1 7 MVA 110/6.6 kV",2.6309999999999998,0.127,2.2799999999999998,0.28999999999999998,2.282,0.115,2.7210000000000001,0.22800000000000001,2.7210000000000001,2.5039999999999996,2.5039999999999996]
[null,"Central San Pedro Dalcahue \n",110,"Central San Pedro Dalcahue \n 110 kV - HT-1 Transformador N°2 75 MVA 110/30 kV ",3.2130000000000001,0.78,3.762,0.626,2.395,0.33600000000000002,4.3940000000000001,1.054,4.3940000000000001,3.34,3.34]
[null,null,null,"Central San Pedro Dalcahue \n 110 kV - HT-2 Transformador N°2 40 MVA 110/30 kV ",3.2130000000000001,0,3.762,0.74299999999999999,2.395,0,4.3940000000000001,1.3420000000000001,4.3940000000000001,3.2130000000000001,3.2130000000000001]
[null,null,null,"Central San Pedro Dalcahue \n 110 kV - H1 Línea 110 kV Central San Pedro Dalcahue - Chiloé",3.2130000000000001,2.4380000000000002,3.762,2.3959999999999999,2.395,2.0950000000000002,4.3940000000000001,2.3919999999999999,4.3940000000000001,2.0020000000000002,2.4380000000000002]
[null,"Central Santiago Solar",110,"Central Santiago Solar 110 kV -  H1 Línea 110 kV Central Santiago Solar - Las Vegas ",11.321,3.399,10.426,2.573,9.7799999999999994,2.923,11.163,3.085,11.321,8.0779999999999994,8.0779999999999994]
[null,null,null,"Central Santiago Solar 110 kV -  H2 Línea 110 kV Central Santiago Solar - Tap Off Punta Peuco/Cerro Navia ",11.321,7.9219999999999997,10.426,6.0679999999999996,9.7799999999999994,6.8570000000000002,11.163,7.2190000000000003,11.321,4.3580000000000005,7.9219999999999997]
[null,null,null,"Central Santiago Solar 110 kV - HT1 Transformador TR1 110/30 kV 110 MVA ",11.321,0,10.426,1.796,9.7799999999999994,0,11.163,1.671,11.321,11.321,11.321]
[null,"Central Tocopilla ",110,"Central Tocopilla  110 kV - HR Acoplador ",12.544,4.0000000000000001E-3,12.744,2E-3,10.717000000000001,4.0000000000000001E-3,12.672000000000001,4.0000000000000001E-3,12.744,12.741999999999999,12.741999999999999]
[null,null,null,"Central Tocopilla  110 kV - HT1 Transformador TR1 28/23 MVA 110/11,5 kV ",12.544,0.28599999999999998,12.744,0.22,10.717000000000001,0.27600000000000002,12.672000000000001,0.26800000000000002,12.744,12.523999999999999,12.523999999999999]
[null,null,null,"Central Tocopilla  110 kV - HT2 Transformador TR2 28/23 MVA 110/11,5 kV ",12.544,0.28599999999999998,12.744,0.22,10.717000000000001,0.27600000000000002,12.672000000000001,0.26800000000000002,12.744,12.523999999999999,12.523999999999999]
[null,null,null,"Central Tocopilla  110 kV - H1 Línea 110 kV Central Tocopilla - A 1",12.544,0.61399999999999999,12.744,0.501,10.717000000000001,0.52600000000000002,12.672000000000001,0.55500000000000005,12.744,12.243,12.243]
[null,null,null,"Central Tocopilla  110 kV - H2 Línea 110 kV Central Tocopilla - A 2",12.544,0.60499999999999998,12.744,0.51800000000000002,10.717000000000001,0.51800000000000002,12.672000000000001,0.56599999999999995,12.744,12.225999999999999,12.225999999999999]
[null,null,null,"Central Tocopilla  110 kV - H3 Línea 110 kV Central Tocopilla - Central Diesel Tamaya ",12.544,1.393,12.744,1.6419999999999999,10.717000000000001,1.141,12.672000000000001,1.5289999999999999,12.744,11.151,11.151]
[null,null,null,"Central Tocopilla  110 kV - H4 Línea 110 kV Central Tocopilla - Central Diesel Tamaya ",12.544,1.5669999999999999,12.744,1.6910000000000001,10.717000000000001,1.2829999999999999,12.672000000000001,1.6160000000000001,12.744,11.056000000000001,11.056000000000001]
[null,null,null,"Central Tocopilla  110 kV - HAT1 Autotransformador ATR1 100/100/30 MVA 220/110/13,8 kV ",12.544,3.9079999999999999,12.744,2.6579999999999999,10.717000000000001,3.3620000000000001,12.672000000000001,3.4420000000000002,12.744,10.086,10.086]
[null,null,null,"Central Tocopilla  110 kV - HAT2 Autotransformador ATR2 100/100/30 MVA 220/110/13,8 kV ",12.544,3.9079999999999999,12.744,2.6579999999999999,10.717000000000001,3.3620000000000001,12.672000000000001,3.4420000000000002,12.744,10.086,10.086]
[null,null,null,"Central Tocopilla  110 kV - HG12 Transformador TR12 92/75 MVA 110/13,8 kV ",12.544,0,12.744,1.216,10.717000000000001,0,12.672000000000001,1.27,12.744,12.544,12.544]
[null,null,null,"Central Tocopilla  110 kV - HG13 Transformador TR13 92/75 MVA 110/13,8 kV ",12.544,0,12.744,1.448,10.717000000000001,0,12.672000000000001,1.512,12.744,12.544,12.544]
[null,null,null,"Central Tocopilla  110 kV - HT105 Transformador TR105 15 MVA 115/5 kV ",12.544,4.0000000000000001E-3,12.744,2E-3,10.717000000000001,4.0000000000000001E-3,12.672000000000001,4.0000000000000001E-3,12.744,12.741999999999999,12.741999999999999]
[null,null,null,"Central Tocopilla  110 kV - HT141 Transformador TR141 30 MVA 115/5 kV ",12.544,4.0000000000000001E-3,12.744,8.0000000000000002E-3,10.717000000000001,4.0000000000000001E-3,12.672000000000001,7.0000000000000001E-3,12.744,12.736000000000001,12.736000000000001]
[null,"S/E Yungay 154kV",154,"S/E Yungay 154kV 154 kV - ATG1 Transformador TR01 70MVA 154/11,5kV",19.158000000000001,1.127,19.751000000000001,1.5860000000000001,16.109000000000002,0.91100000000000003,19.696000000000002,1.484,19.751000000000001,18.212000000000003,18.212000000000003]
[null,null,null,"S/E Yungay 154kV 154 kV - ATG2 Transformador TR02 70MVA 154/11,5kV",19.158000000000001,1.127,19.751000000000001,1.5860000000000001,16.109000000000002,0.91100000000000003,19.696000000000002,1.484,19.751000000000001,18.212000000000003,18.212000000000003]
[null,null,null,"S/E Yungay 154kV 154 kV - ATG3 Transformador TR03 70MVA 154/11,5kV",19.158000000000001,1.127,19.751000000000001,1.5860000000000001,16.109000000000002,0.91100000000000003,19.696000000000002,1.484,19.751000000000001,18.212000000000003,18.212000000000003]
[null,null,null,"S/E Yungay 154kV 154 kV - ATG4 Transformador TR04 70MVA 154/11,5kV",19.158000000000001,0.80400000000000005,19.751000000000001,1.1140000000000001,16.109000000000002,0.68799999999999994,19.696000000000002,1.0309999999999999,19.751000000000001,18.665000000000003,18.665000000000003]
[null,"Centro ",110,"Centro  110 kV - H1 Línea 110 kV Centro - Esmeralda ",6.7030000000000003,6.7030000000000003,6.9930000000000003,6.9930000000000003,5.694,5.694,6.9180000000000001,6.9180000000000001,6.9930000000000003,0,6.9930000000000003]
[null,null,null,"Centro  110 kV - HT1 Transformador TR1 110/13,8 kV ",6.7030000000000003,0,6.9930000000000003,0,5.694,0,6.9180000000000001,0,6.9930000000000003,6.9930000000000003,6.9930000000000003]
[null,null,null,"Centro  110 kV - HT1 Transformador TR2 110/23 kV ",6.7030000000000003,0,6.9930000000000003,0,5.694,0,6.9180000000000001,0,6.9930000000000003,6.9930000000000003,6.9930000000000003]
[null,"Cerrillos ",110,"Cerrillos  110 kV - H2 Línea 110 kV Cerrillos - Los Loros 1",3.903,0,3.548,0.36899999999999999,3.3759999999999999,0,3.8639999999999999,0.33900000000000002,3.903,3.903,3.903]
[null,null,null,"Cerrillos  110 kV - HT1 Transformador T1 30/25/20 MVA 110/24-13,8 kV ",3.903,0,3.548,0,3.3759999999999999,0,3.8639999999999999,0,3.903,3.903,3.903]
[null,"Cerro Calera ",110,"Cerro Calera  110 kV - HT Transformador TR 30 MVA 110/60/12 kV ",13.093,0.23499999999999999,10.686,0.442,11.294,0.20200000000000001,12.275,0.35899999999999999,13.093,12.858000000000001,12.858000000000001]
[null,"Cerro Colorado ",110,"Cerro Colorado  110 kV - HL Línea 110 kV Cerro Colorado - Pozo Almonte ",1.657,1.657,1.1299999999999999,1.1319999999999999,1.417,1.417,1.5089999999999999,1.5089999999999999,1.657,0,1.657]
[null,null,null,"Cerro Colorado  110 kV - HT1 Transformador TR1 46/30 MVA 110/12 kV ",1.657,0,1.1299999999999999,0,1.417,0,1.5089999999999999,0,1.657,1.657,1.657]
[null,null,null,"Cerro Colorado  110 kV - HT2 Transformador TR2 46/30 MVA 110/12 kV ",1.657,0,1.1299999999999999,0,1.417,0,1.5089999999999999,0,1.657,1.657,1.657]
[null,"Cerro Dragón ",110,"Cerro Dragón  110 kV - HT1 Transformador Trafo1 110/13.8 kV 33/25 MVA ",2.976,8.3000000000000004E-2,3.1440000000000001,6.2E-2,2.5569999999999999,7.5999999999999998E-2,3.0920000000000001,7.5999999999999998E-2,3.1440000000000001,3.0820000000000003,3.0820000000000003]
[null,"Cerro Navia",110,"Cerro Navia 110 kV - HT3 AutoTransformador ATR03 399 MVA 220/110/13,8 kV ",57.997999999999998,7.9859999999999998,62.881,12.125,50.179000000000002,6.9329999999999998,61.500999999999998,11,62.881,50.756,50.756]
[null,null,null,"Cerro Navia 110 kV - AT2 AutoTransformador ATR02 400 MVA 220/110/13,2 kV ",57.997999999999998,7.9859999999999998,62.881,12.124000000000001,50.179000000000002,6.9329999999999998,61.500999999999998,11,62.881,50.756999999999998,50.756999999999998]
[null,null,null,"Cerro Navia 110 kV - HT5 AutoTransformador ATR5 400 MVA 220/110/13,2 kV ",57.997999999999998,7.9969999999999999,62.881,10.268000000000001,50.179000000000002,6.9429999999999996,61.500999999999998,9.4860000000000007,62.881,52.613,52.613]
[null,"Cerro Navia (Enel)",110,"Cerro Navia (Enel) 110 kV - H2 Línea 110 kV Cerro Navia - Renca 2",57.997999999999998,7.8529999999999998,62.881,6.63,50.179000000000002,6.75,61.500999999999998,7.2460000000000004,62.881,56.250999999999998,56.250999999999998]
[null,null,null,"Cerro Navia (Enel) 110 kV - H11 Línea 110 kV Cerro Navia - Lo Aguirre 1",57.997999999999998,0.104,62.881,7.6999999999999999E-2,50.179000000000002,9.1999999999999998E-2,61.500999999999998,9.2999999999999999E-2,62.881,62.804000000000002,62.804000000000002]
[null,null,null,"Cerro Navia (Enel) 110 kV - H10 Línea 110 kV Cerro Navia - San Pablo",57.997999999999998,0.10100000000000001,62.881,7.3999999999999996E-2,50.179000000000002,8.8999999999999996E-2,61.500999999999998,0.09,62.881,62.807000000000002,62.807000000000002]
[null,null,null,"Cerro Navia (Enel) 110 kV - H3 Línea 110 kV Cerro Navia - Las Vegas/Central Santiago Solar 1",57.997999999999998,1.5569999999999999,62.881,1.349,50.179000000000002,1.345,61.500999999999998,1.452,62.881,61.532000000000004,61.532000000000004]
[null,null,null,"Cerro Navia (Enel) 110 kV - H4 Línea 110 kV Cerro Navia - Las Vegas/Central Santiago Solar 2",57.997999999999998,1.5569999999999999,62.881,1.349,50.179000000000002,1.345,61.500999999999998,1.452,62.881,61.532000000000004,61.532000000000004]
[null,null,null,"Cerro Navia (Enel) 110 kV - H5 Línea 110 kV Cerro Navia - San Cristóbal 1",57.997999999999998,3.22,62.881,2.5960000000000001,50.179000000000002,2.79,61.500999999999998,2.9369999999999998,62.881,60.284999999999997,60.284999999999997]
[null,null,null,"Cerro Navia (Enel) 110 kV - H6 Línea 110 kV Cerro Navia - San Cristóbal 2",57.997999999999998,3.22,62.881,2.5960000000000001,50.179000000000002,2.79,61.500999999999998,2.9369999999999998,62.881,60.284999999999997,60.284999999999997]
[null,null,null,"Cerro Navia (Enel) 110 kV - H7 Línea 110 kV Cerro Navia - Chena 1 ",57.997999999999998,4.3120000000000003,62.881,3.5630000000000002,50.179000000000002,3.7370000000000001,61.500999999999998,3.9550000000000001,62.881,59.317999999999998,59.317999999999998]
[null,null,null,"Cerro Navia (Enel) 110 kV - H8 Línea 110 kV Cerro Navia - Chena 2 ",57.997999999999998,4.3120000000000003,62.881,3.5630000000000002,50.179000000000002,3.7370000000000001,61.500999999999998,3.9550000000000001,62.881,59.317999999999998,59.317999999999998]
[null,null,null,"Cerro Navia (Enel) 110 kV - H1 Línea 110 kV Cerro Navia - Renca 1",57.997999999999998,7.8529999999999998,62.881,6.63,50.179000000000002,6.75,61.500999999999998,7.2460000000000004,62.881,56.250999999999998,56.250999999999998]
[null,"Chacabuco ",110,"Chacabuco  110 kV -  H1 Línea 110 kV Chacabuco - San Cristóbal/Cerro Navia 1 ",27.021000000000001,13.510999999999999,11.484,5.742,23.396999999999998,11.698,23.831,11.916,27.021000000000001,13.510000000000002,13.510999999999999]
[null,null,null,"Chacabuco  110 kV -  H2 Línea 110 kV Chacabuco - San Cristóbal/Cerro Navia 2",27.021000000000001,13.510999999999999,11.484,5.742,23.396999999999998,11.698,23.831,11.916,27.021000000000001,13.510000000000002,13.510999999999999]
[null,null,null,"Chacabuco  110 kV - HT6 Transformador TR06 25 MVA 110/23,5 kV ",27.021000000000001,0,11.484,0,23.396999999999998,0,23.831,0,27.021000000000001,27.021000000000001,27.021000000000001]
[null,null,null,"Chacabuco  110 kV - AT2 Transformador TR02 37,5 MVA 110/23,5 kV ",27.021000000000001,0,11.484,0,23.396999999999998,0,23.831,0,27.021000000000001,27.021000000000001,27.021000000000001]
[null,null,null,"Chacabuco  110 kV - AT4 Transformador TR04 22,4 MVA 110/12,5 kV ",27.021000000000001,0,11.484,0,23.396999999999998,0,23.831,0,27.021000000000001,27.021000000000001,27.021000000000001]
[null,null,null,"Chacabuco  110 kV - HT8 Transformador TR08 50 MVA 110/23,5 kV ",27.021000000000001,0,11.484,0,23.396999999999998,0,23.831,0,27.021000000000001,27.021000000000001,27.021000000000001]
[null,null,null,"Chacabuco  110 kV - HT7 Transformador TR07110/23,5 kV ",27.021000000000001,0,11.484,0,23.396999999999998,0,23.831,0,27.021000000000001,27.021000000000001,27.021000000000001]
[null,"Chacaya ",110,"Chacaya  110 kV - HT4 Transformador TR4 10 MVA 110/33 kV ",3.99,0,4.6529999999999996,0,3.452,0,4.4649999999999999,0,4.6529999999999996,4.6529999999999996,4.6529999999999996]
[null,null,null,"Chacaya  110 kV - HT3 Transformador TR3 220/110/13,8 kV 80/100 MVA ",3.99,3.5590000000000002,4.6529999999999996,4.3179999999999996,3.452,3.0790000000000002,4.4649999999999999,4.0990000000000002,4.6529999999999996,0.43100000000000005,4.3179999999999996]
[null,null,null,"Chacaya  110 kV - H3 Línea 110 kV Chacaya - GNL Mejillones ",3.99,0,4.6529999999999996,0,3.452,0,4.4649999999999999,0,4.6529999999999996,4.6529999999999996,4.6529999999999996]
[null,null,null,"Chacaya  110 kV - H2 Línea 110 kV Chacaya - Muelle ",3.99,0.433,4.6529999999999996,0.33600000000000002,3.452,0.374,4.4649999999999999,0.38900000000000001,4.6529999999999996,4.3169999999999993,4.3169999999999993]
[null,"Chamy ",110,"Chamy  110 kV - H16 Línea 110 kV Chamy - Chuquicamata ",5.9029999999999996,5.9029999999999996,4.5670000000000002,4.5670000000000002,5.0679999999999996,5.0679999999999996,5.4550000000000001,5.4550000000000001,5.9029999999999996,0,5.9029999999999996]
[null,null,null,"Chamy  110 kV - HT1 Transformador TR01 37/33/25 MVA 100/13,8 kV ",5.9029999999999996,0,4.5670000000000002,0,5.0679999999999996,0,5.4550000000000001,0,5.9029999999999996,5.9029999999999996,5.9029999999999996]
[null,null,null,"Chamy  110 kV - Acoplador Barras Acoplador ",5.9029999999999996,0,4.5670000000000002,0,5.0679999999999996,0,5.4550000000000001,0,5.9029999999999996,5.9029999999999996,5.9029999999999996]
[null,"Charrua",154,"Charrua 154 kV - AT1 Transformador ATR Charrúa 220/154 kV N°1",21.992999999999999,11.234999999999999,23.651,12.365,18.457000000000001,9.6669999999999998,23.373999999999999,11.907999999999999,23.651,11.465999999999999,12.365]
[null,null,null,"Charrua 154 kV - A2 Línea 154 kV Charrua - Monterrico",21.992999999999999,1.0940000000000001,23.651,1.0149999999999999,18.457000000000001,0.94499999999999995,23.373999999999999,1.075,23.651,22.635999999999999,22.635999999999999]
[null,null,null,"Charrua 154 kV - ACE1 Banco Condensador Charrua 154 kV 1",21.992999999999999,0,23.651,0,18.457000000000001,0,23.373999999999999,0,23.651,23.651,23.651]
[null,null,null,"Charrua 154 kV - A4 Línea 154 kV Charrúa - Yungay (Ex Campanario)",21.992999999999999,3.9990000000000001,23.651,4.7409999999999997,18.457000000000001,3.2829999999999999,23.373999999999999,4.5069999999999997,23.651,18.91,18.91]
[null,null,null,"Charrua 154 kV - A6 Línea 154 kV Charrúa - Chillán",21.992999999999999,0.497,23.651,0.51500000000000001,18.457000000000001,0.43,23.373999999999999,0.53300000000000003,23.651,23.135999999999999,23.135999999999999]
[null,null,null,"Charrua 154 kV - A7 Transformador Charrúa 154/69/13.8 kV N°2",21.992999999999999,0.67900000000000005,23.651,1.3049999999999999,18.457000000000001,0.627,23.373999999999999,1.242,23.651,22.346,22.346]
[null,null,null,"Charrua 154 kV - A8 Línea 154 kV Charrúa - Abanico 2",21.992999999999999,1.3720000000000001,23.651,0.89600000000000002,18.457000000000001,0.85799999999999998,23.373999999999999,1.1399999999999999,23.651,22.754999999999999,22.754999999999999]
[null,null,null,"Charrua 154 kV - A9 Línea 154 kV Charrúa - Los Angeles",21.992999999999999,1.0469999999999999,23.651,1.04,18.457000000000001,0.88,23.373999999999999,1.0549999999999999,23.651,22.611000000000001,22.611000000000001]
[null,null,null,"Charrua 154 kV - A10 Línea 154 kV Charrúa - Concepción 1",21.992999999999999,2.1930000000000001,23.651,1.8680000000000001,18.457000000000001,1.89,23.373999999999999,2.06,23.651,21.783000000000001,21.783000000000001]
[null,"Chena ",110,"Chena  110 kV - A6 Línea 110 kV Chena - Ochagavía 1 ",50.009,9.7609999999999992,52.000999999999998,7.5810000000000004,43.314999999999998,8.44,51.78,8.8780000000000001,52.000999999999998,44.419999999999995,44.419999999999995]
[null,null,null,"Chena  110 kV - A5 Línea 110 kV Chena - Ochagavía 2",50.009,9.7609999999999992,52.000999999999998,7.5810000000000004,43.314999999999998,8.44,51.78,8.8780000000000001,52.000999999999998,44.419999999999995,44.419999999999995]
[null,null,null,"Chena  110 kV -  H3 Línea 110 kV Chena - Cerro Navia 1",50.009,6.14,52.000999999999998,4.7720000000000002,43.314999999999998,5.3120000000000003,51.78,5.56,52.000999999999998,47.228999999999999,47.228999999999999]
[null,null,null,"Chena  110 kV -  H4 Línea 110 kV Chena - Cerro Navia 2",50.009,6.14,52.000999999999998,4.7720000000000002,43.314999999999998,5.3120000000000003,51.78,5.56,52.000999999999998,47.228999999999999,47.228999999999999]
[null,null,null,"Chena  110 kV - HT1 Transformador TR01 400 MVA 220/110/13,8 kV ",50.009,9.1479999999999997,52.000999999999998,13.677,43.314999999999998,7.944,51.78,12.098000000000001,52.000999999999998,40.861000000000004,40.861000000000004]
[null,null,null,"Chena  110 kV - CCE1A Banco de Condensadores 1",50.009,0,52.000999999999998,0,43.314999999999998,0,51.78,0,52.000999999999998,52.000999999999998,52.000999999999998]
[null,null,null,"Chena  110 kV - AT2 Transformador TR02 400 MVA 220/110/13,8 kV ",50.009,9.1489999999999991,52.000999999999998,13.683,43.314999999999998,7.9450000000000003,51.78,12.148,52.000999999999998,40.86,40.86]
[null,"Chillán",154,"Chillán 154 kV - AT3 Transformador Chillán TR3 75MVA 154/66 kV ",4.3609999999999998,1.2969999999999999,3.496,1.35,3.758,1.1180000000000001,4.1500000000000004,1.3520000000000001,4.3609999999999998,3.0640000000000001,3.0640000000000001]
[null,"Chiloé",110,"Chiloé 110 kV - HT1 Transformador Chiloe 90 MVA 220/110/23 kV",4.3220000000000001,1.716,4.9130000000000003,2.4449999999999998,3.399,1.4950000000000001,5.1609999999999996,2.4140000000000001,5.1609999999999996,2.7469999999999994,2.7469999999999994]
[null,null,null,"Chiloé 110 kV - H1 Línea 110 kV Chiloe - Ancud 1",4.3220000000000001,0.55800000000000005,4.9130000000000003,0.53200000000000003,3.399,0.48499999999999999,5.1609999999999996,0.54700000000000004,5.1609999999999996,4.6139999999999999,4.6139999999999999]
[null,null,null,"Chiloé 110 kV - H2 Línea 110 kV Chiloe - Pid Pid/Dalcahue 1",4.3220000000000001,0.94899999999999995,4.9130000000000003,0.93400000000000005,3.399,0.82799999999999996,5.1609999999999996,0.97599999999999998,5.1609999999999996,4.1849999999999996,4.1849999999999996]
[null,null,null,"Chiloé 110 kV - H3 Línea 110 kV Chiloe - Degañ 1",4.3220000000000001,0.45800000000000002,4.9130000000000003,0.41599999999999998,3.399,0.38900000000000001,5.1609999999999996,0.435,5.1609999999999996,4.726,4.726]
[null,null,null,"Chiloé 110 kV - H4 Línea 110 kV Chiloe - San Pedro 1",4.3220000000000001,0.70599999999999996,4.9130000000000003,0.64,3.399,0.32100000000000001,5.1609999999999996,0.879,5.1609999999999996,4.282,4.282]
[null,null,null,"Chiloé 110 kV - HR1 Acoplador ",4.3220000000000001,0,4.9130000000000003,0,3.399,0,5.1609999999999996,0,5.1609999999999996,5.1609999999999996,5.1609999999999996]
[null,"Chirre",110,"Chirre 110 kV -  En Barra",4.4960000000000004,0,4.4880000000000004,0,3.944,0,4.5039999999999996,0,4.5039999999999996,4.5039999999999996,4.5039999999999996]
[null,"Choapa ",110,"Choapa  110 kV - H4 Línea 110 kV Choapa - Illapel ",8.2319999999999993,1.008,9.1959999999999997,0.873,6.9589999999999996,0.85899999999999999,9.2319999999999993,0.98,9.2319999999999993,8.3230000000000004,8.3230000000000004]
[null,null,null,"Choapa  110 kV - H5 Línea 110 kV Choapa - Central Olivos ",8.2319999999999993,2.0299999999999998,9.1959999999999997,2.2999999999999998,6.9589999999999996,1.6279999999999999,9.2319999999999993,2.278,9.2319999999999993,6.9539999999999988,6.9539999999999988]
[null,null,null,"Choapa  110 kV - HT ATR1 y ATR2 ",8.2319999999999993,4.4370000000000003,9.1959999999999997,5.3650000000000002,6.9589999999999996,3.8330000000000002,9.2319999999999993,5.09,9.2319999999999993,4.1419999999999995,5.3650000000000002]
[null,null,null,"Choapa  110 kV - H1 Línea 110 kV Choapa - Quereo",8.2319999999999993,0,9.1959999999999997,0,6.9589999999999996,0,9.2319999999999993,0,9.2319999999999993,9.2319999999999993,9.2319999999999993]
[null,null,null,"Choapa  110 kV - H3 Línea 110 kV Choapa - Quinquimo ",8.2319999999999993,0.93300000000000005,9.1959999999999997,0.79,6.9589999999999996,0.80600000000000005,9.2319999999999993,0.89600000000000002,9.2319999999999993,8.4059999999999988,8.4059999999999988]
[null,"Chonchi",110,"Chonchi 110 kV - HT1 Transformador TR1 30-24 MVA 115.69/24 kV ",2.7730000000000001,0,2.37,0,2.3290000000000002,0,2.621,0,2.7730000000000001,2.7730000000000001,2.7730000000000001]
[null,null,null,"Chonchi 110 kV - H2 Línea 110 kV Chonchi - Quellon",2.7730000000000001,0.373,2.37,0.22,2.3290000000000002,0.32200000000000001,2.621,0.32600000000000001,2.7730000000000001,2.4000000000000004,2.4000000000000004]
[null,"Chuquicamata",100,"Chuquicamata 100 kV - HATR1 Transformador ATR1 220/110/13.8",10.404,2.617,12.115,3.593,8.8740000000000006,2.2320000000000002,11.782999999999999,3.403,12.115,8.5220000000000002,8.5220000000000002]
[null,null,null,"Chuquicamata 100 kV - HT2 Transformador ATR2 220/110/13.8",10.404,2.617,12.115,3.593,8.8740000000000006,2.2320000000000002,11.782999999999999,3.403,12.115,8.5220000000000002,8.5220000000000002]
[null,null,null,"Chuquicamata 100 kV - HR Acoplador",10.404,0,12.115,0,8.8740000000000006,0,11.782999999999999,0,12.115,12.115,12.115]
[null,null,null,"Chuquicamata 100 kV - H16 Línea 110 kV Chuquicamata - Chamy 1",10.404,0,12.115,0,8.8740000000000006,0,11.782999999999999,0,12.115,12.115,12.115]
[null,null,null,"Chuquicamata 100 kV - H12  Línea 110 kV Chuquicamata - K1 1",10.404,0.56599999999999995,12.115,0.53200000000000003,8.8740000000000006,0.48099999999999998,11.782999999999999,0.55400000000000005,12.115,11.583,11.583]
[null,null,null,"Chuquicamata 100 kV - H10 Línea 110 kV Chuquicamata - 10 1",10.404,0.7,12.115,0.69199999999999995,8.8740000000000006,0.59499999999999997,11.782999999999999,0.70699999999999996,12.115,11.423,11.423]
[null,null,null,"Chuquicamata 100 kV - H11 Línea 110 kV Chuquicamata - 10A 1",10.404,0.60199999999999998,12.115,0.63,8.8740000000000006,0.51200000000000001,11.782999999999999,0.61499999999999999,12.115,11.484999999999999,11.484999999999999]
[null,null,null,"Chuquicamata 100 kV - H13 Línea 110 kV Chuquicamata - KM6 1",10.404,1.1910000000000001,12.115,1.3049999999999999,8.8740000000000006,1.0129999999999999,11.782999999999999,1.272,12.115,10.81,10.81]
[null,null,null,"Chuquicamata 100 kV - H14 Línea 110 kV Chuquicamata - A 1",10.404,1.0660000000000001,12.115,0.873,8.8740000000000006,0.91200000000000003,11.782999999999999,0.97699999999999998,12.115,11.242000000000001,11.242000000000001]
[null,null,null,"Chuquicamata 100 kV - H15 Línea 110 kV Chuquicamata - A 2",10.404,1.0660000000000001,12.115,0.91300000000000003,8.8740000000000006,0.91200000000000003,11.782999999999999,0.97799999999999998,12.115,11.202,11.202]
[null,"Chuschampis ",110,"Chuschampis  110 kV -  En Barra",3.6269999999999998,0,2.391,0,3.1389999999999998,0,3.399,0,3.6269999999999998,3.6269999999999998,3.6269999999999998]
[null,"Cipreses",154,"Cipreses 154 kV - A1 Línea 154 kV Cipreses - Itahue1/Curillinque",6.2709999999999999,2.4119999999999999,6.0039999999999996,2.2330000000000001,5.1539999999999999,2.11,6.2919999999999998,2.3679999999999999,6.2919999999999998,3.9239999999999999,3.9239999999999999]
[null,null,null,"Cipreses 154 kV - A2 Línea 154 kV Cipreses - Itahue 2",6.2709999999999999,1.5569999999999999,6.0039999999999996,1.2330000000000001,5.1539999999999999,1.3460000000000001,6.2919999999999998,1.4410000000000001,6.2919999999999998,4.851,4.851]
[null,null,null,"Cipreses 154 kV - A3 Línea 154 kV Cipreses - Central Isla 1",6.2709999999999999,0.51100000000000001,6.0039999999999996,0.34399999999999997,5.1539999999999999,0.44800000000000001,6.2919999999999998,0.45100000000000001,6.2919999999999998,5.8410000000000002,5.8410000000000002]
[null,null,null,"Cipreses 154 kV - A4 Línea 154 kV Cipreses - Central Isla 2",6.2709999999999999,0.51100000000000001,6.0039999999999996,0.34399999999999997,5.1539999999999999,0.44800000000000001,6.2919999999999998,0.45100000000000001,6.2919999999999998,5.8410000000000002,5.8410000000000002]
[null,null,null,"Cipreses 154 kV - AT1 Transformador Cipreses TR01 32MVA 154/13,8 kV U1",6.2709999999999999,0.47199999999999998,6.0039999999999996,0.69799999999999995,5.1539999999999999,0.32500000000000001,6.2919999999999998,0.67700000000000005,6.2919999999999998,5.7989999999999995,5.7989999999999995]
[null,null,null,"Cipreses 154 kV - AT2 Transformador Cipreses TR02 32MVA154/13.8 kV U2",6.2709999999999999,0.41299999999999998,6.0039999999999996,0.58599999999999997,5.1539999999999999,0.26300000000000001,6.2919999999999998,0.58699999999999997,6.2919999999999998,5.8579999999999997,5.8579999999999997]
[null,null,null,"Cipreses 154 kV - AT3 Transformador Cipreses TR03 161/13.8/6.9 kV U3",6.2709999999999999,0.41299999999999998,6.0039999999999996,0.58599999999999997,5.1539999999999999,0.26300000000000001,6.2919999999999998,0.58699999999999997,6.2919999999999998,5.8579999999999997,5.8579999999999997]
[null,"Club Hípico ",110,"Club Hípico  110 kV - H1 Línea 110 kV Club Hípico - Ochagavia/Florida 1 ",41.262999999999998,20.631,23.245999999999999,11.622999999999999,35.697000000000003,17.847999999999999,36.616,18.308,41.262999999999998,20.631999999999998,20.631999999999998]
[null,null,null,"Club Hípico  110 kV - H2 Línea 110 kV Club Hípico - Ochagavia/Florida 2",41.262999999999998,20.631,23.245999999999999,11.622999999999999,35.697000000000003,17.847999999999999,36.616,18.308,41.262999999999998,20.631999999999998,20.631999999999998]
[null,null,null,"Club Hípico  110 kV - HT3 Transformador TR3 25 MVA 110/12,5 kV ",41.262999999999998,0,23.245999999999999,0,35.697000000000003,0,36.616,0,41.262999999999998,41.262999999999998,41.262999999999998]
[null,"Codelco Ventanas 1 ",110,"Codelco Ventanas 1  110 kV - A12 Transformador TR1 ",21.209,0,22.298999999999999,0.112,18.481000000000002,0,21.88,0.11600000000000001,22.298999999999999,22.187000000000001,22.187000000000001]
[null,null,null,"Codelco Ventanas 1  110 kV - A22 Transformador TR2 ",21.209,0,22.298999999999999,0.21199999999999999,18.481000000000002,0,21.88,0.221,22.298999999999999,22.087,22.087]
[null,"Codelco Ventanas 2 ",110,"Codelco Ventanas 2  110 kV - HT3 Transformador TR3",18.690000000000001,0,19.702999999999999,0.13400000000000001,16.276,0,19.231999999999999,0.14000000000000001,19.702999999999999,19.568999999999999,19.568999999999999]
[null,null,null,"Codelco Ventanas 2  110 kV - HT4 Transformador TR4",18.690000000000001,0,19.702999999999999,0.216,16.276,0,19.231999999999999,0.22600000000000001,19.702999999999999,19.486999999999998,19.486999999999998]
[null,null,null,"Codelco Ventanas 2  110 kV - HT5 Transformador TR5",18.690000000000001,0,19.702999999999999,0.28199999999999997,16.276,0,19.231999999999999,0.29399999999999998,19.702999999999999,19.420999999999999,19.420999999999999]
[null,"Colaco ",110,"Colaco  110 kV - HT1 Transformador TR1 110/24 kV 16 MVA ",4.0919999999999996,0,3.97,0,3.4910000000000001,0,4.0330000000000004,0,4.0919999999999996,4.0919999999999996,4.0919999999999996]
[null,null,null,"Colaco  110 kV - H1 Línea 110 kV Colaco - Pargua",4.0919999999999996,1.8380000000000001,3.97,1.9850000000000001,3.4910000000000001,1.546,4.0330000000000004,1.9059999999999999,4.0919999999999996,2.2539999999999996,2.2539999999999996]
[null,"Colón ",110,"Colón  110 kV -  H1 Línea 110 kV Colón - Minero 1 ",18.606000000000002,9.3030000000000008,19.988,9.9939999999999998,16.193000000000001,8.0960000000000001,19.399000000000001,9.6999999999999993,19.988,9.9939999999999998,9.9939999999999998]
[null,null,null,"Colón  110 kV -  H2 Línea 110 kV Colón - Minero 2",18.606000000000002,9.3030000000000008,19.988,9.9939999999999998,16.193000000000001,8.0960000000000001,19.399000000000001,9.6999999999999993,19.988,9.9939999999999998,9.9939999999999998]
[null,null,null,"Colón  110 kV - HT1 Transformador TR1 20 MVA 110/13,8/4,16 kV ",18.606000000000002,0,19.988,0,16.193000000000001,0,19.399000000000001,0,19.988,19.988,19.988]
[null,null,null,"Colón  110 kV - HT2 Transformador TR2 20 MVA 110/13,8/4,16 kV ",18.606000000000002,0,19.988,0,16.193000000000001,0,19.399000000000001,0,19.988,19.988,19.988]
[null,null,null,"Colón  110 kV - HT3 Transformador TR3 20 MVA 110/13,8/4,16 kV ",18.606000000000002,0,19.988,0,16.193000000000001,0,19.399000000000001,0,19.988,19.988,19.988]
[null,null,null,"Colón  110 kV - HT4 Transformador TR4 20 MVA 110/13,8/4,16 kV ",18.606000000000002,0,19.988,0,16.193000000000001,0,19.399000000000001,0,19.988,19.988,19.988]
[null,"Concepción",154,"Concepción 154 kV - AT1 Transformador Concepción TR1 30MVA 154/66 kV N°1",14.61,0.26400000000000001,19.827000000000002,0.69099999999999995,12.598000000000001,0.22700000000000001,20.463000000000001,0.83299999999999996,20.463000000000001,19.630000000000003,19.630000000000003]
[null,null,null,"Concepción 154 kV - AT2 Transformador Concepción TR2 56MVA 154/66 kV N°2",14.61,0.34100000000000003,19.827000000000002,0.46200000000000002,12.598000000000001,0.29399999999999998,20.463000000000001,0.46800000000000003,20.463000000000001,19.995000000000001,19.995000000000001]
[null,null,null,"Concepción 154 kV - AT3 Transformador Concepción TR3 56MVA154/66 kV N°3",14.61,0.34799999999999998,19.827000000000002,0.56799999999999995,12.598000000000001,0.3,20.463000000000001,0.60099999999999998,20.463000000000001,19.862000000000002,19.862000000000002]
[null,null,null,"Concepción 154 kV - AT7 Transformador Concepción ATR7 261MVA 225/161/13.2 kV N°7",14.61,3.8250000000000002,19.827000000000002,8.43,12.598000000000001,3.3,20.463000000000001,9.8960000000000008,20.463000000000001,11.397000000000002,11.397000000000002]
[null,null,null,"Concepción 154 kV - A3 Línea 154 kV Concepción - San Vicente 1",14.61,3.3940000000000001,19.827000000000002,3.423,12.598000000000001,2.9319999999999999,20.463000000000001,3.3940000000000001,20.463000000000001,17.069000000000003,17.069000000000003]
[null,null,null,"Concepción 154 kV - A4 Línea 154 kV Concepción - Charrúa",14.61,2.52,19.827000000000002,2.3570000000000002,12.598000000000001,2.1629999999999998,20.463000000000001,2.4390000000000001,20.463000000000001,18.024000000000001,18.024000000000001]
[null,null,null,"Concepción 154 kV - A6 Línea 154 kV Concepción - San Vicente 2",14.61,3.3940000000000001,19.827000000000002,3.423,12.598000000000001,2.9319999999999999,20.463000000000001,3.3940000000000001,20.463000000000001,17.069000000000003,17.069000000000003]
[null,null,null,"Concepción 154 kV - A7 Línea 154 kV Concepción - Alonso de Ribera",14.61,0.54100000000000004,19.827000000000002,0.49099999999999999,12.598000000000001,0.46700000000000003,20.463000000000001,0.51300000000000001,20.463000000000001,19.95,19.95]
[null,"Concon ",110,"Concon  110 kV - H3 Línea 110 kV Concon - Tap Off Achupallas/Reñaca ",21.87,2.9039999999999999,19.422999999999998,2.2389999999999999,19.120999999999999,2.5169999999999999,21.135000000000002,2.7770000000000001,21.87,18.966000000000001,18.966000000000001]
[null,null,null,"Concon  110 kV - HT1 Transformador TR1 25 MVA 110/12 kV ",21.87,4.9000000000000002E-2,19.422999999999998,2.9000000000000001E-2,19.120999999999999,4.2000000000000003E-2,21.135000000000002,4.2000000000000003E-2,21.87,21.821000000000002,21.821000000000002]
[null,null,null,"Concon  110 kV - HT2 Transformador TR2 25 MVA 110/12 kV  ",21.87,4.9000000000000002E-2,19.422999999999998,2.9000000000000001E-2,19.120999999999999,4.2000000000000003E-2,21.135000000000002,4.2999999999999997E-2,21.87,21.821000000000002,21.821000000000002]
[null,null,null,"Concon  110 kV - H4 Línea 110 kV Concon - Bosquemar ",21.87,0,19.422999999999998,1E-3,19.120999999999999,0,21.135000000000002,1E-3,21.87,21.87,21.87]
[null,"Cóndores ",110,"Cóndores  110 kV - HT1 Transformador TR01 195/195/39 MVA 220/115/13,8 kV ",3.3580000000000001,3.2759999999999998,4.0129999999999999,3.9430000000000001,2.8820000000000001,2.806,3.8959999999999999,3.83,4.0129999999999999,8.2000000000000295E-2,3.9430000000000001]
[null,null,null,"Cóndores  110 kV - H1 Línea 110 kV Cóndores - Cerro Dragón/Alto Hospicio ",3.3580000000000001,8.2000000000000003E-2,4.0129999999999999,6.9000000000000006E-2,2.8820000000000001,7.5999999999999998E-2,3.8959999999999999,7.4999999999999997E-2,4.0129999999999999,3.944,3.944]
[null,null,null,"Cóndores  110 kV - H3 Línea 110 kV Cóndores - Pacífico ",3.3580000000000001,0,4.0129999999999999,0,2.8820000000000001,0,3.8959999999999999,0,4.0129999999999999,4.0129999999999999,4.0129999999999999]
[null,null,null,"Cóndores  110 kV - H2 Línea 110 kV Cóndores - Palafitos ",3.3580000000000001,0,4.0129999999999999,0,2.8820000000000001,0,3.8959999999999999,0,4.0129999999999999,4.0129999999999999,4.0129999999999999]
[null,"Convento Viejo",154,"Convento Viejo 154 kV - A3 Transformador Convento Viejo TR01 20MVA 154/66 kV ",10.862,0.189,8.11,0.61,9.4239999999999995,0.157,10.004,0.46100000000000002,10.862,10.673,10.673]
[null,null,null,"Convento Viejo 154 kV - A1 Línea 154 kV Convento Viejo - Itahue",10.862,6.0670000000000002,8.11,4.1180000000000003,9.4239999999999995,5.2389999999999999,10.004,5.4560000000000004,10.862,4.7949999999999999,6.0670000000000002]
[null,null,null,"Convento Viejo 154 kV - A2 Línea 154 kV Convento Viejo - Tinguiririca",10.862,4.6070000000000002,8.11,3.3860000000000001,9.4239999999999995,4.0289999999999999,10.004,4.2290000000000001,10.862,6.2549999999999999,6.2549999999999999]
[null,"Copayapu ",110,"Copayapu  110 kV - H1 Línea 110 kV Copayapu - Galleguillos ",8.0779999999999994,7.0999999999999994E-2,9.2530000000000001,9.6000000000000002E-2,6.9749999999999996,6.0999999999999999E-2,8.9290000000000003,8.8999999999999996E-2,9.2530000000000001,9.157,9.157]
[null,null,null,"Copayapu  110 kV - H2 Línea 110 kV Copayapu - Cardones ",8.0779999999999994,8.0069999999999997,9.2530000000000001,9.0020000000000007,6.9749999999999996,6.9139999999999997,8.9290000000000003,8.7569999999999997,9.2530000000000001,0.25099999999999945,9.0020000000000007]
[null,null,null,"Copayapu  110 kV - H3 Línea 110 kV Copayapu - Tierra Amarilla ",8.0779999999999994,0,9.2530000000000001,1E-3,6.9749999999999996,0,8.9290000000000003,1E-3,9.2530000000000001,9.2520000000000007,9.2520000000000007]
[null,null,null,"Copayapu  110 kV - H4 Línea 110 kV Copayapu - Cerrillos ",8.0779999999999994,0,9.2530000000000001,0.158,6.9749999999999996,0,8.9290000000000003,0.187,9.2530000000000001,9.0950000000000006,9.0950000000000006]
[null,"Copiapó ",110,"Copiapó  110 kV - H1 Línea 110 kV Copiapó - Cardones ",5.1740000000000004,4,4.5199999999999996,3.49,4.4729999999999999,3.4580000000000002,4.9409999999999998,3.8610000000000002,5.1740000000000004,1.1740000000000004,4]
[null,null,null,"Copiapó  110 kV - H2 Línea 110 kV Copiapó - Hernán Fuentes ",5.1740000000000004,1.196,4.5199999999999996,1.0389999999999999,4.4729999999999999,1.034,4.9409999999999998,1.097,5.1740000000000004,3.9780000000000006,3.9780000000000006]
[null,null,null,"Copiapó  110 kV - HT3 Transformador T3 24/20/16 MVA 110/24-13,8 kV ",5.1740000000000004,0,4.5199999999999996,0,4.4729999999999999,0,4.9409999999999998,0,5.1740000000000004,5.1740000000000004,5.1740000000000004]
[null,null,null,"Copiapó  110 kV - HT4 Transformador T4 25/20/16 MVA 110/24-13,8 kV ",5.1740000000000004,0,4.5199999999999996,0,4.4729999999999999,0,4.9409999999999998,0,5.1740000000000004,5.1740000000000004,5.1740000000000004]
[null,"Copihues ",110,"Copihues  110 kV - H1 Línea 110 kV Copihues - Aihuapi ",3.0019999999999998,2.2040000000000002,3.0630000000000002,1.843,2.6459999999999999,1.9119999999999999,3.181,2.1230000000000002,3.181,1.2200000000000002,2.2040000000000002]
[null,null,null,"Copihues  110 kV - HT1 Transformador TR1 30 MVA 115/69/13,8 kV ",3.0019999999999998,0.442,3.0630000000000002,0.98699999999999999,2.6459999999999999,0.42199999999999999,3.181,0.81799999999999995,3.181,2.5599999999999996,2.5599999999999996]
[null,null,null,"Copihues  110 kV - H2 Línea 110 kV Copihues - Central Correntoso",3.0019999999999998,0.378,3.0630000000000002,0.253,2.6459999999999999,0.33200000000000002,3.181,0.33900000000000002,3.181,2.8420000000000001,2.8420000000000001]
[null,"Cordillera ",110,"Cordillera  110 kV - H1 Línea 110 kV Cordillera - Minero 1 ",17.355,8.6780000000000008,17.823,8.9109999999999996,15.1,7.55,17.675000000000001,8.8379999999999992,17.823,8.9120000000000008,8.9120000000000008]
[null,null,null,"Cordillera  110 kV - H2 Línea 110 kV Cordillera - Minero 2",17.355,8.6780000000000008,17.823,8.9109999999999996,15.1,7.55,17.675000000000001,8.8379999999999992,17.823,8.9120000000000008,8.9120000000000008]
[null,null,null,"Cordillera  110 kV - HT39 Transformador TR39 110/33 kV",17.355,0,17.823,0,15.1,0,17.675000000000001,0,17.823,17.823,17.823]
[null,null,null,"Cordillera  110 kV - HT40 Transformador TR40 110/33 kV",17.355,0,17.823,0,15.1,0,17.675000000000001,0,17.823,17.823,17.823]
[null,null,null,"Cordillera  110 kV - HT41 Transformador TR41 110/33 kV",17.355,0,17.823,0,15.1,0,17.675000000000001,0,17.823,17.823,17.823]
[null,null,null,"Cordillera  110 kV - HT42 Transformador TR42 110/33 kV",17.355,0,17.823,0,15.1,0,17.675000000000001,0,17.823,17.823,17.823]
[null,null,null,"Cordillera  110 kV - HT43 Transformador TR43 110/13,8 kV",17.355,0,17.823,0,15.1,0,17.675000000000001,0,17.823,17.823,17.823]
[null,null,null,"Cordillera  110 kV - HT44 Transformador TR44 110/13,8 kV",17.355,0,17.823,0,15.1,0,17.675000000000001,0,17.823,17.823,17.823]
[null,null,null,"Cordillera  110 kV - HT45 Transformador TR46 110/33 kV",17.355,0,17.823,0,15.1,0,17.675000000000001,0,17.823,17.823,17.823]
[null,null,null,"Cordillera  110 kV - HT46 Transformador TR45 110/33 kV",17.355,0,17.823,0,15.1,0,17.675000000000001,0,17.823,17.823,17.823]
[null,null,null,"Cordillera  110 kV - HCE1 Condensador N°1",17.355,0,17.823,0,15.1,0,17.675000000000001,0,17.823,17.823,17.823]
[null,"Coronel",154,"Coronel 154 kV - AT3-4 Transformador Coronel TR4 60/60/20MVA 154/66/13.8 kV ",13.102,0.69699999999999995,15.359,0.70299999999999996,11.472,0.59799999999999998,14.561999999999999,0.73799999999999999,15.359,14.656000000000001,14.656000000000001]
[null,null,null,"Coronel 154 kV - AT5 Transformador Coronel TR5 40/56MVA 154/69/13.2 kV ",13.102,0.52600000000000002,15.359,0.84299999999999997,11.472,0.45100000000000001,14.561999999999999,0.84499999999999997,15.359,14.516,14.516]
[null,null,null,"Coronel 154 kV - AT6 Transformador Coronel TR6 40/56MVA154/69/13.2 kV",13.102,0.42099999999999999,15.359,0.74399999999999999,11.472,0.36099999999999999,14.561999999999999,0.747,15.359,14.615,14.615]
[null,null,null,"Coronel 154 kV - A1 Línea 154 kV Coronel - Bocamina",13.102,10.887,15.359,12.178000000000001,11.472,9.5749999999999993,14.561999999999999,11.458,15.359,3.1809999999999992,12.178000000000001]
[null,"Costanera ",110,"Costanera  110 kV -  En Barra",8.4809999999999999,0,5.9820000000000002,0,7.3390000000000004,0,8.1739999999999995,0,8.4809999999999999,8.4809999999999999,8.4809999999999999]
[null,"Cristalerías",110,"Cristalerías 110 kV - HT1  Línea 110 kV Cristalerías - Las Vegas ",10.404999999999999,10.404999999999999,7.3079999999999998,7.3079999999999998,8.9440000000000008,8.9440000000000008,9.7170000000000005,9.7170000000000005,10.404999999999999,0,10.404999999999999]
[null,"Cunco ",110,"Cunco  110 kV -  H1 Línea 110 kV Cunco - Río Toltén ",1.952,1.6120000000000001,1.6779999999999999,1.2130000000000001,1.675,1.3959999999999999,1.8520000000000001,1.4730000000000001,1.952,0.46499999999999986,1.6120000000000001]
[null,null,null,"Cunco  110 kV -  H2 Línea 110 kV Cunco - Melipeuco ",1.952,0.34,1.6779999999999999,0.46600000000000003,1.675,0.28000000000000003,1.8520000000000001,0.42299999999999999,1.952,1.6119999999999999,1.6119999999999999]
[null,null,null,"Cunco  110 kV - HT1 Transformador TR1 16 MVA 110/23 kV",1.952,0,1.6779999999999999,0,1.675,0,1.8520000000000001,0,1.952,1.952,1.952]
[null,"Dalcahue ",110,"Dalcahue  110 kV -  H1 Línea 110 kV Dalcahue - Chiloe ",3.6930000000000001,1.7809999999999999,3.5590000000000002,1.5620000000000001,3.0150000000000001,1.4039999999999999,3.6560000000000001,1.6879999999999999,3.6930000000000001,1.9970000000000001,1.9970000000000001]
[null,null,null,"Dalcahue  110 kV -  H2 Línea 110 kV Dalcahue - Pid Pid ",3.6930000000000001,1.9159999999999999,3.5590000000000002,1.9990000000000001,3.0150000000000001,1.6120000000000001,3.6560000000000001,1.9690000000000001,3.6930000000000001,1.7770000000000001,1.9990000000000001]
[null,null,null,"Dalcahue  110 kV - HT1 Transformador TR1 110/23 kV",3.6930000000000001,0,3.5590000000000002,0,3.0150000000000001,0,3.6560000000000001,0,3.6930000000000001,3.6930000000000001,3.6930000000000001]
[null,"Degañ ",110,"Degañ  110 kV - HT1  Transformador Degañ TR1 110/23 kV",4.3079999999999998,0.45800000000000002,4.8739999999999997,0.41499999999999998,3.3889999999999998,0.377,5.1059999999999999,0.434,5.1059999999999999,4.6719999999999997,4.6719999999999997]
[null,"Desalant",110,"Desalant 110 kV -  H1 Línea 110 kV Desalant - Mejillones/Antofagasta ",5.2919999999999998,5.2919999999999998,3.7160000000000002,3.7160000000000002,4.51,4.51,4.8170000000000002,4.8170000000000002,5.2919999999999998,0,5.2919999999999998]
[null,"Diego de Almagro",110,"Diego de Almagro 110 kV - HT1 Transformador TR1 28 MVA ",9.548,0.52400000000000002,12.951000000000001,0.67300000000000004,8.218,0.44900000000000001,13.234,0.66400000000000003,13.234,12.57,12.57]
[null,null,null,"Diego de Almagro 110 kV -  H5 Línea 110 kV Diego de Almagro - Central Javiera/Tal Tal (ELECDA)",9.548,0,12.951000000000001,0.13500000000000001,8.218,0,13.234,0.214,13.234,13.02,13.02]
[null,null,null,"Diego de Almagro 110 kV -  H3 Línea 110 kV Diego de Almagro - Llanta 2 ",9.548,0,12.951000000000001,0,8.218,0,13.234,0,13.234,13.234,13.234]
[null,null,null,"Diego de Almagro 110 kV - HT2 Transformador TR2 ",9.548,0.52400000000000002,12.951000000000001,0.67300000000000004,8.218,0.44900000000000001,13.234,0.66400000000000003,13.234,12.57,12.57]
[null,null,null,"Diego de Almagro 110 kV -  H1 Línea 110 kV Diego de Almagro - Central PV El Salvador",9.548,0,12.951000000000001,1E-3,8.218,0,13.234,1E-3,13.234,13.233000000000001,13.233000000000001]
[null,null,null,"Diego de Almagro 110 kV -  H2 Línea 110 kV Diego de Almagro - Llanta 1",9.548,0,12.951000000000001,0,8.218,0,13.234,0,13.234,13.234,13.234]
[null,null,null,"Diego de Almagro 110 kV - HT3 Autotransformador ATR3 120 MVA 220/110/13,8 kV ",9.548,3.1349999999999998,12.951000000000001,5.702,8.218,2.7040000000000002,13.234,6.3,13.234,7.2490000000000006,7.2490000000000006]
[null,null,null,"Diego de Almagro 110 kV -  H8 Línea 110 kV Diego de Almagro - Central Emelda ",9.548,1.429,12.951000000000001,1.6830000000000001,8.218,1.2270000000000001,13.234,1.6910000000000001,13.234,11.542999999999999,11.542999999999999]
[null,null,null,"Diego de Almagro 110 kV -  H6 Línea 110 kV Diego de Almagro - Manto Verde ",9.548,0,12.951000000000001,0,8.218,0,13.234,0,13.234,13.234,13.234]
[null,null,null,"Diego de Almagro 110 kV -  H9 Línea 110 kV Diego de Almagro - Tap Off Chañares/El Salado",9.548,0,12.951000000000001,0.14299999999999999,8.218,0,13.234,0.22600000000000001,13.234,13.007999999999999,13.007999999999999]
[null,null,null,"Diego de Almagro 110 kV - HT4 Autotransformador ATR4 120/90 MVA 220/110/13,8 kV ",9.548,3.1389999999999998,12.951000000000001,3.02,8.218,2.7080000000000002,13.234,3.0790000000000002,13.234,10.154999999999999,10.154999999999999]
[null,null,null,"Diego de Almagro 110 kV -  H7 Línea 110 kV Diego de Almagro - Minera Franke",9.548,0,12.951000000000001,0,8.218,0,13.234,0,13.234,13.234,13.234]
[null,null,null,"Diego de Almagro 110 kV - H10 Línea 110 kV Diego de Almagro - Central Andes Generación ",9.548,0.79700000000000004,12.951000000000001,0.92400000000000004,8.218,0.68100000000000005,13.234,0.92300000000000004,13.234,12.311,12.311]
[null,"Dos Amigos ",110,"Dos Amigos  110 kV -  En Barra",2.8039999999999998,0,2.21,0,2.4279999999999999,0,2.7690000000000001,0,2.8039999999999998,2.8039999999999998,2.8039999999999998]
[null,"EB2",110,"EB2 110 kV - HT1 Transformador TR1 7,5MVA 110/4,16kV",2.7709999999999999,0,1.74,0,2.3980000000000001,0,2.5070000000000001,0,2.7709999999999999,2.7709999999999999,2.7709999999999999]
[null,"EKA Chile ",154,"EKA Chile  154 kV -  En Barra",13.385999999999999,0,14.414,0,11.553000000000001,0,14.124000000000001,0,14.414,14.414,14.414]
[null,"El Bato",110,"El Bato 110 kV - HX Línea 110kV El bato - Ventanas",32.646000000000001,32.646000000000001,35.712000000000003,35.712000000000003,28.553000000000001,28.553000000000001,34.414999999999999,34.414999999999999,35.712000000000003,0,35.712000000000003]
[null,null,null,"El Bato 110 kV - HTX Transformador 110/12kV",32.646000000000001,0,35.712000000000003,0,28.553000000000001,0,34.414999999999999,0,35.712000000000003,35.712000000000003,35.712000000000003]
[null,"El Cobre ",110,"El Cobre  110 kV -  H1 Línea 110 kV El Cobre - La Calera ",4.5339999999999998,4.5339999999999998,3.0009999999999999,3.0019999999999998,3.9209999999999998,3.9209999999999998,4.1390000000000002,4.1399999999999997,4.5339999999999998,0,4.5339999999999998]
[null,"El Cobre (Codelco)",110,"El Cobre (Codelco) 110 kV -  H1 Línea 110 kV El Cobre (Codelco) - Minero 1",16.978999999999999,8.49,16.611000000000001,8.3049999999999997,14.771000000000001,7.3860000000000001,16.849,8.4250000000000007,16.978999999999999,8.488999999999999,8.49]
[null,null,null,"El Cobre (Codelco) 110 kV -  H2 Línea 110 kV El Cobre (Codelco) - Minero 2",16.978999999999999,8.49,16.611000000000001,8.3049999999999997,14.771000000000001,7.3860000000000001,16.849,8.4250000000000007,16.978999999999999,8.488999999999999,8.49]
[null,null,null,"El Cobre (Codelco) 110 kV - HT1 Transformador TR3 110/13,8 kV ",16.978999999999999,0,16.611000000000001,0,14.771000000000001,0,16.849,0,16.978999999999999,16.978999999999999,16.978999999999999]
[null,null,null,"El Cobre (Codelco) 110 kV - HT2 Transformador TR4 110/13,8 kV ",16.978999999999999,0,16.611000000000001,0,14.771000000000001,0,16.849,0,16.978999999999999,16.978999999999999,16.978999999999999]
[null,null,null,"El Cobre (Codelco) 110 kV - HT3 Transformador TR2 110/13,8 kV ",16.978999999999999,0,16.611000000000001,0,14.771000000000001,0,16.849,0,16.978999999999999,16.978999999999999,16.978999999999999]
[null,null,null,"El Cobre (Codelco) 110 kV - HT4 Transformador TR1 110/13,8 kV ",16.978999999999999,0,16.611000000000001,0,14.771000000000001,0,16.849,0,16.978999999999999,16.978999999999999,16.978999999999999]
[null,null,null,"El Cobre (Codelco) 110 kV - HT7 Transformador T7 40-45-50MVA, 110/13,8kV",16.978999999999999,0,16.611000000000001,0,14.771000000000001,0,16.849,0,16.978999999999999,16.978999999999999,16.978999999999999]
[null,null,null,"El Cobre (Codelco) 110 kV - HT8 Transformador T8 40-45-50MVA, 110/13,8kV",16.978999999999999,0,16.611000000000001,0,14.771000000000001,0,16.849,0,16.978999999999999,16.978999999999999,16.978999999999999]
[null,null,null,"El Cobre (Codelco) 110 kV - T9 Transformador T9 40-45-50MVA, 110/13,8kV",16.978999999999999,0,16.611000000000001,0,14.771000000000001,0,16.849,0,16.978999999999999,16.978999999999999,16.978999999999999]
[null,"El Empalme ",110,"El Empalme  110 kV -  H1 Línea 110 kV El Empalme - Molinos (Enlasa)",3.9159999999999999,2.3410000000000002,3.3279999999999998,1.921,3.3559999999999999,2.0190000000000001,3.6779999999999999,2.1739999999999999,3.9159999999999999,1.5749999999999997,2.3410000000000002]
[null,null,null,"El Empalme  110 kV -  H2 Línea 110 kV El Empalme - Calbuco ",3.9159999999999999,0,3.3279999999999998,0,3.3559999999999999,0,3.6779999999999999,0,3.9159999999999999,3.9159999999999999,3.9159999999999999]
[null,null,null,"El Empalme  110 kV -  H3 Línea 110 kV El Empalme - Colaco",3.9159999999999999,1.5760000000000001,3.3279999999999998,1.407,3.3559999999999999,1.3380000000000001,3.6779999999999999,1.508,3.9159999999999999,2.34,2.34]
[null,null,null,"El Empalme  110 kV - HT1 Transformador TR1 16/11 MVA 115/24 kV ",3.9159999999999999,0,3.3279999999999998,0,3.3559999999999999,0,3.6779999999999999,0,3.9159999999999999,3.9159999999999999,3.9159999999999999]
[null,"El Espino",110,"El Espino 110 kV - HX1 Línea 110kV El Espino-Combarbalá",3.5579999999999998,2.069,2.8519999999999999,1.7430000000000001,3.03,1.738,3.4550000000000001,2.016,3.5579999999999998,1.4889999999999999,2.069]
[null,null,null,"El Espino 110 kV - HX2 Línea 110kV Illapel - El Espino",3.5579999999999998,1.5029999999999999,2.8519999999999999,1.115,3.03,1.3029999999999999,3.4550000000000001,1.4419999999999999,3.5579999999999998,2.0549999999999997,2.0549999999999997]
[null,"El Lince",110,"El Lince 110 kV - HT  Línea 110 kV El Lince - Mejillones ",1.76,1.76,1.012,1.014,1.5169999999999999,1.5169999999999999,1.599,1.6,1.76,0,1.76]
[null,"El Peñón ",110,"El Peñón  110 kV - HT1 Transformador T1 30/24/18 MVA 115/25 kV ",8.7680000000000007,0,7.1159999999999997,0,7.5010000000000003,0,8.2889999999999997,0,8.7680000000000007,8.7680000000000007,8.7680000000000007]
[null,null,null,"El Peñón  110 kV -  H3 Línea 110 kV El Peñón -  Minera Teck CDA",8.7680000000000007,0,7.1159999999999997,1E-3,7.5010000000000003,0,8.2889999999999997,1E-3,8.7680000000000007,8.7680000000000007,8.7680000000000007]
[null,null,null,"El Peñón  110 kV -  H1 Línea 110 kV El Peñón - Ovalle 1 ",8.7680000000000007,0.62,7.1159999999999997,0.51600000000000001,7.5010000000000003,0.52800000000000002,8.2889999999999997,0.61599999999999999,8.7680000000000007,8.1480000000000015,8.1480000000000015]
[null,null,null,"El Peñón  110 kV -  H2 Línea 110 kV El Peñón - Pan de Azúcar  ",8.7680000000000007,2.9390000000000001,7.1159999999999997,2.4180000000000001,7.5010000000000003,2.5369999999999999,8.2889999999999997,2.8,8.7680000000000007,5.8290000000000006,5.8290000000000006]
[null,null,null,"El Peñón  110 kV -  H4 Línea 110 kV El Peñón - Central Las Piedras ",8.7680000000000007,1.7070000000000001,7.1159999999999997,0.89400000000000002,7.5010000000000003,1.4370000000000001,8.2889999999999997,1.4359999999999999,8.7680000000000007,7.0610000000000008,7.0610000000000008]
[null,null,null,"El Peñón  110 kV -  H5 Línea 110 kV El Peñón - Ovalle 2",8.7680000000000007,0.625,7.1159999999999997,0.51600000000000001,7.5010000000000003,0.53200000000000003,8.2889999999999997,0.61499999999999999,8.7680000000000007,8.1430000000000007,8.1430000000000007]
[null,null,null,"El Peñón  110 kV -  H7 Línea 110 kV El Peñón - Pan de Azúcar ",8.7680000000000007,2.9390000000000001,7.1159999999999997,2.4180000000000001,7.5010000000000003,2.5369999999999999,8.2889999999999997,2.8,8.7680000000000007,5.8290000000000006,5.8290000000000006]
[null,null,null,"El Peñón  110 kV - HT3 Transformador TR3 30 MVA 110/69/13,8 kV ",8.7680000000000007,0,7.1159999999999997,0.40300000000000002,7.5010000000000003,0,8.2889999999999997,0.34599999999999997,8.7680000000000007,8.7680000000000007,8.7680000000000007]
[null,"El Romeral (CMP)",110,"El Romeral (CMP) 110 kV - L1 Línea 110 kV Romeral - Tap Off El Romeral ",3.8730000000000002,0,2.8380000000000001,0,3.351,0,3.6789999999999998,0,3.8730000000000002,3.8730000000000002,3.8730000000000002]
[null,"El Salado ",110,"El Salado  110 kV - HT1 Transformador TR1 110/23 kV ",3.63,0,2.4279999999999999,0,3.1379999999999999,0,3.3220000000000001,0,3.63,3.63,3.63]
[null,"El Salto ",110,"El Salto  110 kV - H1 Línea 110 kV El Salto - Los Almendros 1",34.527000000000001,4.9820000000000002,33.136000000000003,3.6749999999999998,29.902000000000001,4.3129999999999997,34.363999999999997,4.4859999999999998,34.527000000000001,29.877999999999997,29.877999999999997]
[null,null,null,"El Salto  110 kV - H2 Línea 110 kV El Salto - Los Almendros 2",34.527000000000001,4.9820000000000002,33.136000000000003,3.6749999999999998,29.902000000000001,4.3120000000000003,34.363999999999997,4.4859999999999998,34.527000000000001,29.877999999999997,29.877999999999997]
[null,null,null,"El Salto  110 kV - H5 Línea 110 kV El Salto - San Cristóbal 1 ",34.527000000000001,5.6559999999999997,33.136000000000003,3.9870000000000001,29.902000000000001,4.8970000000000002,34.363999999999997,5.0720000000000001,34.527000000000001,29.291999999999998,29.291999999999998]
[null,null,null,"El Salto  110 kV - H6 Línea 110 kV El Salto - San Cristóbal 2",34.527000000000001,5.6559999999999997,33.136000000000003,3.9870000000000001,29.902000000000001,4.8970000000000002,34.363999999999997,5.0720000000000001,34.527000000000001,29.291999999999998,29.291999999999998]
[null,null,null,"El Salto  110 kV - HT1 Transformador TR1 400 MVA 220/110/13,2 kV ",34.527000000000001,6.6609999999999996,33.136000000000003,8.9290000000000003,29.902000000000001,5.7720000000000002,34.363999999999997,7.9429999999999996,34.527000000000001,27.866,27.866]
[null,null,null,"El Salto  110 kV - HT2 Transformador TR2 400 MVA 220/110/13,2 kV ",34.527000000000001,6.6609999999999996,33.136000000000003,8.9290000000000003,29.902000000000001,5.7720000000000002,34.363999999999997,7.9429999999999996,34.527000000000001,27.866,27.866]
[null,null,null,"El Salto  110 kV - HCE Banco de CCEE 80 MVAr",34.527000000000001,0,33.136000000000003,0,29.902000000000001,0,34.363999999999997,0,34.527000000000001,34.527000000000001,34.527000000000001]
[null,"El Salvador ",110,"El Salvador  110 kV -  H1 Línea 110 kV El Salvador - Diego de Almagro",4.8840000000000003,1.694,4.2530000000000001,1.373,4.22,1.4630000000000001,4.633,1.5189999999999999,4.8840000000000003,3.1900000000000004,3.1900000000000004]
[null,null,null,"El Salvador  110 kV -  H2 Línea 110 kV El Salvador  - Llanta 1",4.8840000000000003,1.571,4.2530000000000001,1.417,4.22,1.357,4.633,1.542,4.8840000000000003,3.3130000000000006,3.3130000000000006]
[null,null,null,"El Salvador  110 kV - HT3 Transformador TR3 20/15 MVA 110/12,5 kV ",4.8840000000000003,1.6E-2,4.2530000000000001,0.01,4.22,1.4E-2,4.633,1.4E-2,4.8840000000000003,4.8680000000000003,4.8680000000000003]
[null,null,null,"El Salvador  110 kV - HT1 Transformador TR1 20/15 MVA 110/12,5 kV ",4.8840000000000003,3.2000000000000001E-2,4.2530000000000001,1.7999999999999999E-2,4.22,2.7E-2,4.633,2.8000000000000001E-2,4.8840000000000003,4.8520000000000003,4.8520000000000003]
[null,null,null,"El Salvador  110 kV -  H3 Línea 110 kV El Salvador - Llanta 2",4.8840000000000003,1.6359999999999999,4.2530000000000001,1.4690000000000001,4.22,1.4139999999999999,4.633,1.599,4.8840000000000003,3.2480000000000002,3.2480000000000002]
[null,null,null,"El Salvador  110 kV - HT2 Transformador TR2 20/15 MVA 110/12,5 kV ",4.8840000000000003,1.6E-2,4.2530000000000001,0.01,4.22,1.4E-2,4.633,1.4E-2,4.8840000000000003,4.8680000000000003,4.8680000000000003]
[null,null,null,"El Salvador  110 kV - H4 Línea 110 kV El Salvador - Línea Lixiviación",4.8840000000000003,0,4.2530000000000001,0,4.22,0,4.633,0,4.8840000000000003,4.8840000000000003,4.8840000000000003]
[null,"Esmeralda ",110,"Esmeralda  110 kV - HT1 Transformador ATR Esmeralda 220/110 kV",6.8869999999999996,3.6080000000000001,7.33,4.3810000000000002,5.8470000000000004,3.1080000000000001,7.2249999999999996,4.1440000000000001,7.33,3.2789999999999995,4.3810000000000002]
[null,null,null,"Esmeralda  110 kV -  H2 Línea 110 kV Esmeralda - Centro ",6.8869999999999996,0,7.33,0,5.8470000000000004,0,7.2249999999999996,0,7.33,7.33,7.33]
[null,null,null,"Esmeralda  110 kV -  H3 Línea 110 kV Esmeralda - La Portada ",6.8869999999999996,2.1000000000000001E-2,7.33,1.4E-2,5.8470000000000004,1.7000000000000001E-2,7.2249999999999996,1.7999999999999999E-2,7.33,7.3159999999999998,7.3159999999999998]
[null,null,null,"Esmeralda  110 kV -  H1 Línea 110 kV Esmeralda - Sur",6.8869999999999996,0,7.33,0,5.8470000000000004,0,7.2249999999999996,0,7.33,7.33,7.33]
[null,null,null,"Esmeralda  110 kV -  H4 Línea 110 kV Esmeralda - Tap Off Uribe/Uribe ",6.8869999999999996,3.27,7.33,2.95,5.8470000000000004,2.734,7.2249999999999996,3.0760000000000001,7.33,4.38,4.38]
[null,"Esperanza (HASA)",110,"Esperanza (HASA) 110 kV -  HT Transformador TR2 30 MVA 110/66 kV",17.649999999999999,8.5000000000000006E-2,15.37,0.34399999999999997,15.114000000000001,7.3999999999999996E-2,16.911999999999999,0.28499999999999998,17.649999999999999,17.564999999999998,17.564999999999998]
[null,null,null,"Esperanza (HASA) 110 kV - H1 Línea 110 kV  Esperanza (HASA) - Fundición Chagres/Aconcagua 1 ",17.649999999999999,1.3560000000000001,15.37,0.995,15.114000000000001,1.2130000000000001,16.911999999999999,1.2569999999999999,17.649999999999999,16.293999999999997,16.293999999999997]
[null,null,null,"Esperanza (HASA) 110 kV -  H2 Línea 110 kV  Esperanza (HASA) -  Fundición Chagres 2 ",17.649999999999999,1.3540000000000001,15.37,0.99299999999999999,15.114000000000001,1.2110000000000001,16.911999999999999,1.2549999999999999,17.649999999999999,16.295999999999999,16.295999999999999]
[null,"Estación de Bombeo Sierra Gorda N°1",110,"Estación de Bombeo Sierra Gorda N°1 110 kV - HT1  Transformador TR01 70/70/12 MVA 220/110/13,8 kV y Transformador TR Reserva 70/70/12 MVA 220/110/13,8 kV ",2.9180000000000001,2.9180000000000001,4.173,4.173,2.5289999999999999,2.5289999999999999,4.601,4.601,4.601,0,4.601]
[null,null,null,"Estación de Bombeo Sierra Gorda N°1 110 kV - HT2  Transformador TR02 37,5 MVA 110/6,9 kV ",2.9180000000000001,0,4.173,0,2.5289999999999999,0,4.601,0,4.601,4.601,4.601]
[null,null,null,"Estación de Bombeo Sierra Gorda N°1 110 kV - H3 Línea 110 kV Estación de Bombeo Sierra Gorda N° 1 - Estación de Bombeo Sierra Gorda N° 2",2.9180000000000001,0,4.173,0,2.5289999999999999,0,4.601,1E-3,4.601,4.5999999999999996,4.5999999999999996]
[null,"Estación de Bombeo Sierra Gorda N°2",110,"Estación de Bombeo Sierra Gorda N°2 110 kV - HT1 Transformador TR01 37,5 MVA 110/6,9 kV ",1.5760000000000001,0,1.454,0,1.365,0,1.5720000000000001,0,1.5760000000000001,1.5760000000000001,1.5760000000000001]
[null,"Fatima",154,"Fatima 154 kV - A1 Línea 154kV Fatima - Tap Tuniche/Itahue/Alto Jahuel",13.036,5.7460000000000004,10.760999999999999,4.6079999999999997,11.327,4.9950000000000001,12.234999999999999,5.3860000000000001,13.036,7.2899999999999991,7.2899999999999991]
[null,null,null,"Fatima 154 kV - A2 Línea 154kV Fatima - Alto Jahuel/Paine",13.036,6.593,10.760999999999999,5.77,11.327,5.7279999999999998,12.234999999999999,6.2720000000000002,13.036,6.4429999999999996,6.593]
[null,null,null,"Fatima 154 kV - AT3 Transformador Fatima 75MVA 154/66 kV",13.036,0.7,10.760999999999999,0.38500000000000001,11.327,0.60699999999999998,12.234999999999999,0.61399999999999999,13.036,12.336,12.336]
[null,"Florida ",110,"Florida  110 kV -  H1 Línea 110 kV  Florida - Buin 1",33.286000000000001,5.0309999999999997,19.286999999999999,2.7730000000000001,28.745000000000001,4.37,29.635999999999999,4.4790000000000001,33.286000000000001,28.255000000000003,28.255000000000003]
[null,null,null,"Florida  110 kV -  H2 Línea 110 kV  Florida - Buin 2",33.286000000000001,5.0309999999999997,19.286999999999999,2.7730000000000001,28.745000000000001,4.37,29.635999999999999,4.4790000000000001,33.286000000000001,28.255000000000003,28.255000000000003]
[null,null,null,"Florida  110 kV -  H3 Línea 110 kV  Florida - Los Almendros 2",33.286000000000001,4.109,19.286999999999999,2.2730000000000001,28.745000000000001,3.5659999999999998,29.635999999999999,3.6480000000000001,33.286000000000001,29.177,29.177]
[null,null,null,"Florida  110 kV -  H4 Línea 110 kV  Florida - Los Almendros 1",33.286000000000001,4.109,19.286999999999999,2.2730000000000001,28.745000000000001,3.5659999999999998,29.635999999999999,3.6480000000000001,33.286000000000001,29.177,29.177]
[null,null,null,"Florida  110 kV -  H5 Línea 110 kV  Florida - Ochagavía 1 ",33.286000000000001,6.3440000000000003,19.286999999999999,3.1920000000000002,28.745000000000001,5.5010000000000003,29.635999999999999,5.5750000000000002,33.286000000000001,26.942,26.942]
[null,null,null,"Florida  110 kV -  H6 Línea 110 kV  Florida - Ochagavía 2 ",33.286000000000001,6.3440000000000003,19.286999999999999,3.1920000000000002,28.745000000000001,5.5010000000000003,29.635999999999999,5.5750000000000002,33.286000000000001,26.942,26.942]
[null,null,null,"Florida  110 kV - HT1 Transformador TR01 25 MVA 110/12 kV ",33.286000000000001,0.47,19.286999999999999,0.20799999999999999,28.745000000000001,0.46200000000000002,29.635999999999999,0.46100000000000002,33.286000000000001,32.816000000000003,32.816000000000003]
[null,null,null,"Florida  110 kV -  H7 Línea 110 kV  Florida - Las Vizcachas 1",33.286000000000001,0.83499999999999996,19.286999999999999,1.115,28.745000000000001,0.624,29.635999999999999,0.97899999999999998,33.286000000000001,32.451000000000001,32.451000000000001]
[null,null,null,"Florida  110 kV -  H8 Línea 110 kV  Florida - Las Vizcachas 2",33.286000000000001,1.026,19.286999999999999,1.496,28.745000000000001,0.80200000000000005,29.635999999999999,1.2649999999999999,33.286000000000001,32.26,32.26]
[null,"FPC",110,"FPC 154 kV - A1 acoplador ",13.02,0.26,13.09,0.18,11.31,0.23,13.42,0.24,13.42,13.18,13.18]
[null,"Fundición Chagres ",110,"Fundición Chagres  110 kV -  H2 Línea 110 kV Fundición Chagres - San Felipe 1\nLínea 110 kV Fundición Chagres - Esperanza (HASA) 1",13.787000000000001,6.6909999999999998,8.9049999999999994,4.3230000000000004,11.895,5.774,12.461,6.0430000000000001,13.787000000000001,7.096000000000001,7.096000000000001]
[null,null,null,"Fundición Chagres  110 kV -  H1 Línea 110 kV Fundición Chagres - San Felipe 2",13.787000000000001,1.476,8.9049999999999994,0.92600000000000005,11.895,1.327,12.461,1.3620000000000001,13.787000000000001,12.311,12.311]
[null,null,null,"Fundición Chagres  110 kV -  H3 Línea 110 kV Fundición Chagres - Esperanza (HASA) 2",13.787000000000001,5.6219999999999999,8.9049999999999994,3.6579999999999999,11.895,4.798,12.461,5.056,13.787000000000001,8.1650000000000009,8.1650000000000009]
[null,null,null,"Fundición Chagres  110 kV - HT11 Transformador TR1 110/12 kV ",13.787000000000001,0,8.9049999999999994,0,11.895,0,12.461,0,13.787000000000001,13.787000000000001,13.787000000000001]
[null,null,null,"Fundición Chagres  110 kV - HT12 Transformador TR2 110/12 kV ",13.787000000000001,0,8.9049999999999994,0,11.895,0,12.461,0,13.787000000000001,13.787000000000001,13.787000000000001]
[null,null,null,"Fundición Chagres  110 kV - A Paño Acoplador",13.787000000000001,0,8.9049999999999994,0,11.895,0,12.461,0,13.787000000000001,13.787000000000001,13.787000000000001]
[null,"Fundición Paipote",110,"Fundición Paipote 110 kV -  HL Línea 110 kV Fundición Paipote - Cardones ",4.1779999999999999,4.1779999999999999,3.262,3.262,3.6139999999999999,3.6139999999999999,3.9849999999999999,3.9849999999999999,4.1779999999999999,0,4.1779999999999999]
[null,null,null,"Fundición Paipote 110 kV - HT1 Autotransformador ATR1",4.1779999999999999,0,3.262,0,3.6139999999999999,0,3.9849999999999999,0,4.1779999999999999,4.1779999999999999,4.1779999999999999]
[null,null,null,"Fundición Paipote 110 kV - HT2 Autotransformador ATR2",4.1779999999999999,0,3.262,0,3.6139999999999999,0,3.9849999999999999,0,4.1779999999999999,4.1779999999999999,4.1779999999999999]
[null,"Galleguillos ",110,"Galleguillos  110 kV -  H1 Línea 110 kV Galleguillos - Copayapu 1",4.359,2.3559999999999999,3.6339999999999999,1.952,3.77,2.0379999999999998,4.09,2.2879999999999998,4.359,2.0030000000000001,2.3559999999999999]
[null,null,null,"Galleguillos  110 kV -  H2 Línea 110 kV Galleguillos - Hernán Fuentes ",4.359,2.0779999999999998,3.6339999999999999,1.716,3.77,1.7969999999999999,4.09,1.8620000000000001,4.359,2.2810000000000001,2.2810000000000001]
[null,null,null,"Galleguillos  110 kV -  H3 Línea 110 kV Galleguillos - Impulsión/Caldera",4.359,0,3.6339999999999999,3.0000000000000001E-3,3.77,0,4.09,3.0000000000000001E-3,4.359,4.359,4.359]
[null,"Gamboa",110,"Gamboa 110 kV - HX1 Línea 110kV Pid Pid - Gamboa",3.952,1.198,4.8179999999999996,1.04,3.2559999999999998,0.93200000000000005,4.9889999999999999,1.1619999999999999,4.9889999999999999,3.827,3.827]
[null,null,null,"Gamboa 110 kV - HX2 Línea 110kV Gamboa-Castro",3.952,0.35599999999999998,4.8179999999999996,0.30599999999999999,3.2559999999999998,0.314,4.9889999999999999,0.32900000000000001,4.9889999999999999,4.66,4.66]
[null,null,null,"Gamboa 110 kV - HXT1 Transformador 90 MVA 220/110/23 kV Gamboa 1",3.952,1.226,4.8179999999999996,1.756,3.2559999999999998,1.0209999999999999,4.9889999999999999,1.77,4.9889999999999999,3.2189999999999999,3.2189999999999999]
[null,null,null,"Gamboa 110 kV - HXT2 Transformador 90 MVA 220/110/23 kV Gamboa 2",3.952,1.226,4.8179999999999996,1.756,3.2559999999999998,1.0209999999999999,4.9889999999999999,1.77,4.9889999999999999,3.2189999999999999,3.2189999999999999]
[null,"GNL Mejillones",110,"GNL Mejillones 110 kV - H1 Línea GNL Mejillones 110kV - Chacaya",3.157,3.157,2.8940000000000001,2.8940000000000001,2.7309999999999999,2.7309999999999999,3.141,3.141,3.157,0,3.157]
[null,"GNL Quintero",110,"GNL Quintero 110 kV - HA2 Línea 110 kV GNL Quintero - Ventanas",26.629000000000001,21.295999999999999,11.221,11.590999999999999,23.224,18.611999999999998,24.021000000000001,19.128,26.629000000000001,5.333000000000002,21.295999999999999]
[null,null,null,"GNL Quintero 110 kV - HB2 Línea 110 kV GNL Quintero - Central Quintero",26.629000000000001,5.367,11.221,2.7850000000000001,23.224,4.6369999999999996,24.021000000000001,5.0839999999999996,26.629000000000001,21.262,21.262]
[null,null,null,"GNL Quintero 110 kV - HA1 Transformador TR1 30/50 MVA 110/6.6 kV",26.629000000000001,0,11.221,0,23.224,0,24.021000000000001,0,26.629000000000001,26.629000000000001,26.629000000000001]
[null,null,null,"GNL Quintero 110 kV - HB1 Transformador TR2 30/50 MVA 110/6.6 kV",26.629000000000001,0,11.221,0,23.224,0,24.021000000000001,0,26.629000000000001,26.629000000000001,26.629000000000001]
[null,null,null,"GNL Quintero 110 kV - HA3 Línea 110 kV GNL Quintero - ENAP 1",26.629000000000001,0,11.221,0,23.224,0,24.021000000000001,0,26.629000000000001,26.629000000000001,26.629000000000001]
[null,null,null,"GNL Quintero 110 kV - HB3 Línea 110 kV GNL Quintero - ENAP 2",26.629000000000001,0,11.221,0,23.224,0,24.021000000000001,0,26.629000000000001,26.629000000000001,26.629000000000001]
[null,"Guayaques ",110,"Guayaques  110 kV - HT3 Transformador TR02 37,5 MVA 110/3,45 kV ",1.7430000000000001,0,0.88200000000000001,0,1.5089999999999999,0,1.5860000000000001,0,1.7430000000000001,1.7430000000000001,1.7430000000000001]
[null,null,null,"Guayaques  110 kV - HT1 Transformador TR01 37,5 MVA 110/3,45 kV ",1.7430000000000001,0,0.88200000000000001,0,1.5089999999999999,0,1.5860000000000001,0,1.7430000000000001,1.7430000000000001,1.7430000000000001]
[null,"Hernán Fuentes ",110,"Hernán Fuentes  110 kV - HT1 Transformador T1 12/10 MVA 110/23 kV ",4.5789999999999997,0,3.8330000000000002,0,3.9590000000000001,0,4.3209999999999997,0,4.5789999999999997,4.5789999999999997,4.5789999999999997]
[null,null,null,"Hernán Fuentes  110 kV -  H3 Línea 110 kV Hernán Fuentes - Impulsión/Caldera/Galleguillos",4.5789999999999997,1.6930000000000001,3.8330000000000002,1.41,3.9590000000000001,1.464,4.3209999999999997,1.538,4.5789999999999997,2.8859999999999997,2.8859999999999997]
[null,null,null,"Hernán Fuentes  110 kV -  H1 Línea 110 kV Hernán Fuentes - Copiapo",4.5789999999999997,2.923,3.8330000000000002,2.4380000000000002,3.9590000000000001,2.528,4.3209999999999997,2.8119999999999998,4.5789999999999997,1.6559999999999997,2.923]
[null,"Huachipato",154,"Huachipato 154 kV - AT1 Transformador TR1 50MVA 154/13.8 kV ",14.396000000000001,0,16.689,0,12.419,0,16.085000000000001,0,16.689,16.689,16.689]
[null,null,null,"Huachipato 154 kV - AT2 Transformador TR2 50MVA 154/13.8 kV ",14.396000000000001,0,16.689,0,12.419,0,16.085000000000001,0,16.689,16.689,16.689]
[null,null,null,"Huachipato 154 kV - AT3 Transformador TR3 50MVA 154/13.8 kV ",14.396000000000001,0,16.689,0,12.419,0,16.085000000000001,0,16.689,16.689,16.689]
[null,null,null,"Huachipato 154 kV - AT5 Transformador TR4 50MVA 154/13,8 kV ",14.396000000000001,0,16.689,0,12.419,0,16.085000000000001,0,16.689,16.689,16.689]
[null,"Hualpen",154,"Hualpen 154 kV - A1 Línea 154 kV Hualpen - San Vicente 1",15.395,2.9550000000000001,19.402999999999999,3.238,13.282,2.5449999999999999,19.050999999999998,3.1850000000000001,19.402999999999999,16.164999999999999,16.164999999999999]
[null,null,null,"Hualpen 154 kV - A2 Línea 154 kV Hualpen - San Vicente 2",15.395,2.9550000000000001,19.402999999999999,3.2320000000000002,13.282,2.5449999999999999,19.050999999999998,3.18,19.402999999999999,16.170999999999999,16.170999999999999]
[null,null,null,"Hualpen 154 kV - A3 Línea 154 kV Hualpen - Petropower",15.395,0.79300000000000004,19.402999999999999,0.83199999999999996,13.282,0.65800000000000003,19.050999999999998,0.83799999999999997,19.402999999999999,18.570999999999998,18.570999999999998]
[null,null,null,"Hualpen 154 kV - A4 Línea 154 kV Hualpen - Mapal",15.395,3.8759999999999999,19.402999999999999,3.7829999999999999,13.282,3.3860000000000001,19.050999999999998,3.7370000000000001,19.402999999999999,15.62,15.62]
[null,null,null,"Hualpen 154 kV - AT1 Transformador Hualpen ATR1 300MVA 225/15/66 kV",15.395,4.8639999999999999,19.402999999999999,8.3780000000000001,13.282,4.1870000000000003,19.050999999999998,8.423,19.402999999999999,11.024999999999999,11.024999999999999]
[null,"Huasco",110,"Huasco 110 kV - H1 Línea 110 kV Central Huasco - Maintencillo 1 ",5.6130000000000004,2.0390000000000001,6.3769999999999998,1.8080000000000001,4.8499999999999996,1.758,6.444,1.98,6.444,4.569,4.569]
[null,null,null,"Huasco 110 kV - H2 Línea 110 kV Central Huasco - Maintencillo 2",5.6130000000000004,2.0670000000000002,6.3769999999999998,1.8360000000000001,4.8499999999999996,1.7809999999999999,6.444,2.0070000000000001,6.444,4.5409999999999995,4.5409999999999995]
[null,null,null,"Huasco 110 kV - H3 Línea 110 kV Central Huasco - Pellets 2",5.6130000000000004,0,6.3769999999999998,0,4.8499999999999996,0,6.444,0,6.444,6.444,6.444]
[null,null,null,"Huasco 110 kV - H4 Línea 110 kV Central Huasco - Pellets 1",5.6130000000000004,0,6.3769999999999998,0,4.8499999999999996,0,6.444,0,6.444,6.444,6.444]
[null,null,null,"Huasco 110 kV - HT3 Transformador 110/11.5KV 28MVA 2",5.6130000000000004,0.52200000000000002,6.3769999999999998,0.92700000000000005,4.8499999999999996,0.45700000000000002,6.444,0.84399999999999997,6.444,5.6,5.6]
[null,null,null,"Huasco 110 kV - HT4 Transformador 110/11.5KV 28MVA 3",5.6130000000000004,0.52300000000000002,6.3769999999999998,0.92800000000000005,4.8499999999999996,0.45700000000000002,6.444,0.84499999999999997,6.444,5.5990000000000002,5.5990000000000002]
[null,null,null,"Huasco 110 kV - HT5 Transformador 110/11.5KV 28MVA 1",5.6130000000000004,0.52300000000000002,6.3769999999999998,0.92800000000000005,4.8499999999999996,0.45700000000000002,6.444,0.84499999999999997,6.444,5.5990000000000002,5.5990000000000002]
[null,"Illapel ",110,"Illapel  110 kV - HT2 Transformador TR02 13 MVA 110/24/13,8 kV ",3.6579999999999999,0,2.7839999999999998,0,3.1309999999999998,0,3.5329999999999999,0,3.6579999999999999,3.6579999999999999,3.6579999999999999]
[null,null,null,"Illapel  110 kV - HT1 Transformador TR01 25 MVA 110/66 kV",3.6579999999999999,0.17399999999999999,2.7839999999999998,0.24199999999999999,3.1309999999999998,0.15,3.5329999999999999,0.25800000000000001,3.6579999999999999,3.484,3.484]
[null,null,null,"Illapel  110 kV -  H3 Línea 110 kV Illapel - Punitaqui/Ovalle ",3.6579999999999999,1.4419999999999999,2.7839999999999998,1.0840000000000001,3.1309999999999998,1.228,3.5329999999999999,1.373,3.6579999999999999,2.2160000000000002,2.2160000000000002]
[null,null,null,"Illapel  110 kV -  H1 Línea 110 kV Illapel - Salamanca ",3.6579999999999999,0,2.7839999999999998,1E-3,3.1309999999999998,0,3.5329999999999999,1E-3,3.6579999999999999,3.6579999999999999,3.6579999999999999]
[null,null,null,"Illapel  110 kV -  H2 Línea 110 kV Illapel - Choapa ",3.6579999999999999,2.0499999999999998,2.7839999999999998,1.4610000000000001,3.1309999999999998,1.7589999999999999,3.5329999999999999,1.9319999999999999,3.6579999999999999,1.6080000000000001,2.0499999999999998]
[null,"Impulsión",110,"Impulsión 110 kV - HT Transformador TR1 110/23 kV ",3.4140000000000001,0,2.58,0,2.9529999999999998,0,3.1749999999999998,0,3.4140000000000001,3.4140000000000001,3.4140000000000001]
[null,"Incahuasi ",110,"Incahuasi  110 kV - H1 Línea 110 kV Incahuasi - Las Compañias/Tap Off El Romeral",2.5009999999999999,1.2669999999999999,1.7929999999999999,0.85299999999999998,2.165,1.097,2.42,1.2030000000000001,2.5009999999999999,1.234,1.2669999999999999]
[null,"Itahue",154,"Itahue 154 kV - A1 Línea 154 kV Itahue - Cipreses C1",14.821999999999999,0.999,18.75,0.88900000000000001,12.76,0.81899999999999995,18.622,0.94099999999999995,18.75,17.861000000000001,17.861000000000001]
[null,null,null,"Itahue 154 kV - A2 Línea 154 kV Itahue - Cipreses C2",14.821999999999999,0.92400000000000004,18.75,0.81399999999999995,12.76,0.751,18.622,0.86799999999999999,18.75,17.936,17.936]
[null,null,null,"Itahue 154 kV - A3 Línea 154 kV Itahue - Tinguiririca 1",14.821999999999999,2.1829999999999998,18.75,1.948,12.76,1.8979999999999999,18.622,2.0590000000000002,18.75,16.802,16.802]
[null,null,null,"Itahue 154 kV - A4 Línea 154 kV Itahue - Tinguiririca 2/Convento Viejo",14.821999999999999,2.1829999999999998,18.75,1.948,12.76,1.8979999999999999,18.622,2.0590000000000002,18.75,16.802,16.802]
[null,null,null,"Itahue 154 kV - A5 Línea 154 kV Itahue - Charrúa (Parral/Linares)",14.821999999999999,2.2890000000000001,18.75,2.1760000000000002,12.76,1.9830000000000001,18.622,2.2389999999999999,18.75,16.573999999999998,16.573999999999998]
[null,null,null,"Itahue 154 kV - AT Transformador Itahue TR01 75MVA 154/13.8 kV N°1",14.821999999999999,0.42399999999999999,18.75,0.51900000000000002,12.76,0.36699999999999999,18.622,0.54700000000000004,18.75,18.231000000000002,18.231000000000002]
[null,null,null,"Itahue 154 kV - AT2 Transformador Itahue TR02 56MVA 154/69/13.8 kV N°2",14.821999999999999,0.27400000000000002,18.75,0.38500000000000001,12.76,0.23699999999999999,18.622,0.41299999999999998,18.75,18.364999999999998,18.364999999999998]
[null,null,null,"Itahue 154 kV - AT4 Transformador ATR Itahue N°4",14.821999999999999,5.0529999999999999,18.75,8.4589999999999996,12.76,4.383,18.622,8.3870000000000005,18.75,10.291,10.291]
[null,null,null,"Itahue 154 kV - AT5 Transformador Itahue TR05N 154/66/13.2 kV N°5",14.821999999999999,0.55500000000000005,18.75,1.6479999999999999,12.76,0.48,18.622,1.9690000000000001,18.75,17.102,17.102]
[null,"K1 ",100,"K1  100 kV - H12 Línea 100 kV K1 - Chuquicamata",9.8149999999999995,4.3559999999999999,10.335000000000001,4.3230000000000004,8.3780000000000001,3.72,10.162000000000001,4.2969999999999997,10.335000000000001,6.0120000000000005,6.0120000000000005]
[null,null,null,"K1  100 kV - H23 Línea 100 kV K1 - 10",9.8149999999999995,5.4710000000000001,10.335000000000001,6.0170000000000003,8.3780000000000001,4.6689999999999996,10.162000000000001,5.9029999999999996,10.335000000000001,4.3439999999999994,6.0170000000000003]
[null,null,null,"K1  100 kV - HT1 Transformador TR01 26,6/20 MVA 100/13,8 kV ",9.8149999999999995,0,10.335000000000001,0,8.3780000000000001,0,10.162000000000001,0,10.335000000000001,10.335000000000001,10.335000000000001]
[null,null,null,"K1  100 kV - HT2 Transformador TR02 26,6/20 MVA 100/13,8 kV ",9.8149999999999995,0,10.335000000000001,0,8.3780000000000001,0,10.162000000000001,0,10.335000000000001,10.335000000000001,10.335000000000001]
[null,null,null,"K1  100 kV - HT3 Transformador TR03 25/20 MVA 100/13,8 kV ",9.8149999999999995,0,10.335000000000001,0,8.3780000000000001,0,10.162000000000001,0,10.335000000000001,10.335000000000001,10.335000000000001]
[null,null,null,"K1  100 kV - HAB Paño Acoplador ",9.8149999999999995,0,10.335000000000001,0,8.3780000000000001,0,10.162000000000001,0,10.335000000000001,10.335000000000001,10.335000000000001]
[null,"KM6",100,"KM6 100 kV - H13 Línea 100 kV KM6 - Chuquicamata",9.8620000000000001,2.4889999999999999,10.811999999999999,2.8879999999999999,8.4160000000000004,2.1269999999999998,10.534000000000001,2.746,10.811999999999999,7.9239999999999995,7.9239999999999995]
[null,null,null,"KM6 100 kV - H22 Línea 100 kV KM6 - 10A",9.8620000000000001,3.8969999999999998,10.811999999999999,3.988,8.4160000000000004,3.33,10.534000000000001,3.984,10.811999999999999,6.8239999999999998,6.8239999999999998]
[null,null,null,"KM6 100 kV - H24 Línea 100 kV KM6 - Sopladores",9.8620000000000001,0,10.811999999999999,0,8.4160000000000004,0,10.534000000000001,0,10.811999999999999,10.811999999999999,10.811999999999999]
[null,null,null,"KM6 100 kV - H25 Línea 100 kV KM6 - Salar C1",9.8620000000000001,1.7390000000000001,10.811999999999999,1.9690000000000001,8.4160000000000004,1.48,10.534000000000001,1.907,10.811999999999999,8.843,8.843]
[null,null,null,"KM6 100 kV - H26 Línea 100 kV KM6 - Salar C2",9.8620000000000001,1.7390000000000001,10.811999999999999,1.9690000000000001,8.4160000000000004,1.48,10.534000000000001,1.907,10.811999999999999,8.843,8.843]
[null,null,null,"KM6 100 kV - HT1 Transformador KM6 TR01 25/20 MVA 100/13.8 kV ",9.8620000000000001,0,10.811999999999999,0,8.4160000000000004,0,10.534000000000001,0,10.811999999999999,10.811999999999999,10.811999999999999]
[null,null,null,"KM6 100 kV - HT2 Transformador KM6 TR02 33/25 MVA 100/13.8 kV",9.8620000000000001,0,10.811999999999999,0,8.4160000000000004,0,10.534000000000001,0,10.811999999999999,10.811999999999999,10.811999999999999]
[null,null,null,"KM6 100 kV - HT3 Transformador KM6 TR03 25/20 MVA 100/13.8 kV",9.8620000000000001,0,10.811999999999999,0,8.4160000000000004,0,10.534000000000001,0,10.811999999999999,10.811999999999999,10.811999999999999]
[null,null,null,"KM6 100 kV - HACOP Paño Acoplador ",9.8620000000000001,0,10.811999999999999,0,8.4160000000000004,0,10.534000000000001,0,10.811999999999999,10.811999999999999,10.811999999999999]
[null,"La Calera",110,"La Calera 110 kV - H5 Línea 110 kV La Calera - El Cobre",13.093,0,10.686,1E-3,11.294,0,12.275,1E-3,13.093,13.093,13.093]
[null,null,null,"La Calera 110 kV - HT1 Transformador TR1 30 MVA 115/44 kV",13.093,0.247,10.686,0.13400000000000001,11.294,0.21199999999999999,12.275,0.215,13.093,12.846,12.846]
[null,null,null,"La Calera 110 kV - HT2 Transformador TR2 22,5 MVA 115/12 kV",13.093,0,10.686,0,11.294,0,12.275,0,13.093,13.093,13.093]
[null,null,null,"La Calera 110 kV - HT3 Transformador TR3 25 MVA 115/12 kV",13.093,0,10.686,0,11.294,0,12.275,0,13.093,13.093,13.093]
[null,"La Cisterna",110,"La Cisterna 110 kV - H1 Línea 110 kV La Cisterna - Chena/Ochagavía 1",37.481000000000002,18.741,20.937000000000001,10.468,32.448999999999998,16.224,33.454999999999998,16.727,37.481000000000002,18.740000000000002,18.741]
[null,null,null,"La Cisterna 110 kV - H2 Línea 110 kV La Cisterna - Chena/Ochagavía 2",37.481000000000002,18.741,20.937000000000001,10.468,32.448999999999998,16.224,33.454999999999998,16.727,37.481000000000002,18.740000000000002,18.741]
[null,null,null,"La Cisterna 110 kV - HT5 Transformador TR05 50 MVA 110/13.2 kV",37.481000000000002,0,20.937000000000001,0,32.448999999999998,0,33.454999999999998,0,37.481000000000002,37.481000000000002,37.481000000000002]
[null,"La Dehesa",110,"La Dehesa 110 kV - HT1 Transformador TR01 25MVA 110/13.2 kV ",21.687999999999999,0,11.113,0,18.785,0,19.327000000000002,0,21.687999999999999,21.687999999999999,21.687999999999999]
[null,null,null,"La Dehesa 110 kV - HT2 Transformador TR02 50MVA 110/12.5 kV",21.687999999999999,0,11.113,0,18.785,0,19.327000000000002,0,21.687999999999999,21.687999999999999,21.687999999999999]
[null,null,null,"La Dehesa 110 kV - HT3 Transformador TR03 50MVA 110/23.5 kV",21.687999999999999,0,11.113,0,18.785,0,19.327000000000002,0,21.687999999999999,21.687999999999999,21.687999999999999]
[null,null,null,"La Dehesa 110 kV - H4 Transformador TR04 20MVA  110/23 kV ",21.687999999999999,0,11.113,0,18.785,0,19.327000000000002,0,21.687999999999999,21.687999999999999,21.687999999999999]
[null,"La Pintana",110,"La Pintana 110 kV - H1 Línea 110 kV La Pintana - Buin / Florida 1",29.978000000000002,14.989000000000001,15.696999999999999,7.8490000000000002,25.95,12.975,26.606999999999999,13.304,29.978000000000002,14.989000000000001,14.989000000000001]
[null,null,null,"La Pintana 110 kV - H2 Línea 110 kV La Pintana - Buin / Florida 2",29.978000000000002,14.989000000000001,15.696999999999999,7.8490000000000002,25.95,12.975,26.606999999999999,13.304,29.978000000000002,14.989000000000001,14.989000000000001]
[null,null,null,"La Pintana 110 kV - A-T4 Transformador TR04 25MVA 110/12.5 kV",29.978000000000002,0,15.696999999999999,0,25.95,0,26.606999999999999,0,29.978000000000002,29.978000000000002,29.978000000000002]
[null,"La Portada",110,"La Portada 110 kV - H1 Línea 110 kV La Portada - Esmeralda",4.0419999999999998,4.0209999999999999,3.109,3.0990000000000002,3.46,3.4430000000000001,3.7,3.6829999999999998,4.0419999999999998,2.0999999999999908E-2,4.0209999999999999]
[null,null,null,"La Portada 110 kV - HT1 Transformador TR1 110/23 kV ",4.0419999999999998,2.1000000000000001E-2,3.109,0.01,3.46,1.7000000000000001E-2,3.7,1.7999999999999999E-2,4.0419999999999998,4.0209999999999999,4.0209999999999999]
[null,null,null,"La Portada 110 kV - HT3 Transformador TR3 110/23 kV",4.0419999999999998,0,3.109,0,3.46,0,3.7,0,4.0419999999999998,4.0419999999999998,4.0419999999999998]
[null,"La Reina",110,"La Reina 110 kV -  H1 Línea 110 kV La Reina - Florida/Los Almendros 1",19.777000000000001,9.8889999999999993,8.35,4.1749999999999998,17.117000000000001,8.5589999999999993,17.337,8.6690000000000005,19.777000000000001,9.8880000000000017,9.8889999999999993]
[null,null,null,"La Reina 110 kV -  H2 Línea 110 kV La Reina - Florida/Los Almendros 2",19.777000000000001,9.8889999999999993,8.35,4.1749999999999998,17.117000000000001,8.5589999999999993,17.337,8.6690000000000005,19.777000000000001,9.8880000000000017,9.8889999999999993]
[null,"Lagunillas",154,"Lagunillas 154 kV -  A2 Línea 154kV Lagunillas - Hualpén ",14.659000000000001,3.9790000000000001,18.62,5.0129999999999999,12.789,3.544,18.059000000000001,4.9210000000000003,18.62,5.0129999999999999,5.0129999999999999]
[null,null,null,"Lagunillas 154 kV -  A3 Línea 154kV Lagunillas - Hualpén ",14.659000000000001,7.5810000000000004,18.62,9.5960000000000001,12.789,6.4850000000000003,18.059000000000001,9.1769999999999996,18.62,9.5960000000000001,9.5960000000000001]
[null,null,null,"Lagunillas 154 kV -  A4 ATR Lagunilla 220/154 kV",14.659000000000001,10.689,18.62,14.318,12.789,9.2539999999999996,18.059000000000001,13.933,18.62,14.318,14.318]
[null,null,null,"Lagunillas 154 kV -  A5 ATR Lagunilla 220/154 kV",14.659000000000001,3.9790000000000001,18.62,5.0129999999999999,12.789,3.544,18.059000000000001,4.9210000000000003,18.62,5.0129999999999999,5.0129999999999999]
[null,null,null,"Lagunillas 154 kV - A5 Línea 154kV Lagunillas - Bocamina",14.659000000000001,3.9790000000000001,18.62,5.0129999999999999,12.789,3.544,18.059000000000001,4.9210000000000003,18.62,5.0129999999999999,5.0129999999999999]
[null,null,null,"Lagunillas 154 kV -  A6 Línea 154kV Lagunillas - Bocamina",14.659000000000001,7.5810000000000004,18.62,9.5960000000000001,12.789,6.4850000000000003,18.059000000000001,9.1769999999999996,18.62,9.5960000000000001,9.5960000000000001]
[null,"Las Acacias",110,"Las Acacias 110 kV -  H1 Línea 110 kV Las Acacias - Buin/Lo Espejo 1",39.725000000000001,19.863,20.530999999999999,10.265000000000001,34.414000000000001,17.207000000000001,35.194000000000003,17.597000000000001,39.725000000000001,19.862000000000002,19.863]
[null,null,null,"Las Acacias 110 kV -  H2 Línea 110 kV Las Acacias - Buin/Lo Espejo 2",39.725000000000001,19.863,20.530999999999999,10.265000000000001,34.414000000000001,17.207000000000001,35.194000000000003,17.597000000000001,39.725000000000001,19.862000000000002,19.863]
[null,"Las Arañas ",110,"Las Arañas  110 kV - HL1 Línea 110 kV Las Arañas - Quelentaro",3.2330000000000001,3.2330000000000001,3.4870000000000001,3.0209999999999999,2.8,2.8,3.3980000000000001,3.2429999999999999,3.4870000000000001,0.46600000000000019,3.2429999999999999]
[null,null,null,"Las Arañas  110 kV - HT2 AutoTransformador ATR2 40/40/8 MVA 110/66/13.8 kV",3.2330000000000001,0,3.4870000000000001,0.24,2.8,0,3.3980000000000001,0.26,3.4870000000000001,3.2469999999999999,3.2469999999999999]
[null,null,null,"Las Arañas  110 kV - HT1 AutoTransformador ATR1 40/40/8 MVA 110/66/13.8 kV",3.2330000000000001,0,3.4870000000000001,0.24,2.8,0,3.3980000000000001,0.26,3.4870000000000001,3.2469999999999999,3.2469999999999999]
[null,"Las Compañias ",110,"Las Compañias  110 kV - H2 Línea 110 kV Las Compañias - Maintencillo/Tap Off Romeral 1",5.3529999999999998,0.7,4.5460000000000003,0.52200000000000002,4.6289999999999996,0.60599999999999998,5.1360000000000001,0.67100000000000004,5.3529999999999998,4.6529999999999996,4.6529999999999996]
[null,null,null,"Las Compañias  110 kV - H1 Línea 110 kV Las Compañias - Pan de Azucar 1",5.3529999999999998,4.6790000000000003,4.5460000000000003,4.0359999999999996,4.6289999999999996,4.0449999999999999,5.1360000000000001,4.4740000000000002,5.3529999999999998,0.67399999999999949,4.6790000000000003]
[null,null,null,"Las Compañias  110 kV - HT Transformador TR1 110/14.2 kV",5.3529999999999998,0,4.5460000000000003,0,4.6289999999999996,0,5.1360000000000001,0,5.3529999999999998,5.3529999999999998,5.3529999999999998]
[null,"Las Luces",110,"Las Luces 110 kV - HT1 Transformador Las Luces 110/33 kV N°1",1.3089999999999999,0,0.97099999999999997,0,1.133,0,1.266,0,1.3089999999999999,1.3089999999999999,1.3089999999999999]
[null,null,null,"Las Luces 110 kV - H2 Línea 110 kV Las Luces - Tal Tal (ELECDA)  1",1.3089999999999999,0,0.97099999999999997,2E-3,1.133,0,1.266,2E-3,1.3089999999999999,1.3089999999999999,1.3089999999999999]
[null,"Las Vegas",110,"Las Vegas 110 kV -  H1 Línea 110 kV Las Vegas - San Pedro/Cerro Calera/Calera 1",18.042000000000002,3.8559999999999999,16.161999999999999,3.081,15.439,3.331,17.495999999999999,3.4969999999999999,18.042000000000002,14.186000000000002,14.186000000000002]
[null,null,null,"Las Vegas 110 kV -  H3 Línea 110 kV Las Vegas - Central Santiago Solar 1",18.042000000000002,2.097,16.161999999999999,1.6719999999999999,15.439,1.8089999999999999,17.495999999999999,1.931,18.042000000000002,15.945000000000002,15.945000000000002]
[null,null,null,"Las Vegas 110 kV -  H4 Línea 110 kV Las Vegas - Cerro Navia (Enel)/Tap Off Punta Peuco 2",18.042000000000002,2.097,16.161999999999999,1.6060000000000001,15.439,1.8089999999999999,17.495999999999999,1.909,18.042000000000002,15.945000000000002,15.945000000000002]
[null,null,null,"Las Vegas 110 kV -  H6 Línea 110 kV Las Vegas - Esperanza (HASA) C1",18.042000000000002,2.766,16.161999999999999,2.3210000000000002,15.439,2.4710000000000001,17.495999999999999,2.6989999999999998,18.042000000000002,15.276000000000002,15.276000000000002]
[null,null,null,"Las Vegas 110 kV -  H2 Línea 110 kV Las Vegas - San Pedro/Cerro Calera/Calera 2",18.042000000000002,3.8559999999999999,16.161999999999999,3.081,15.439,3.331,17.495999999999999,3.4969999999999999,18.042000000000002,14.186000000000002,14.186000000000002]
[null,null,null,"Las Vegas 110 kV - HR Acoplador",18.042000000000002,0,16.161999999999999,0,15.439,0,17.495999999999999,0,18.042000000000002,18.042000000000002,18.042000000000002]
[null,null,null,"Las Vegas 110 kV - HT4 Transformador TR4 160 MVA 110/15 kV",18.042000000000002,3.2080000000000002,16.161999999999999,4.3109999999999999,15.439,2.5150000000000001,17.495999999999999,3.956,18.042000000000002,14.834000000000001,14.834000000000001]
[null,null,null,"Las Vegas 110 kV - HT1 Transformador TR1 28 MVA 110/44 kV",18.042000000000002,7.3999999999999996E-2,16.161999999999999,4.4999999999999998E-2,15.439,6.4000000000000001E-2,17.495999999999999,6.5000000000000002E-2,18.042000000000002,17.968,17.968]
[null,null,null,"Las Vegas 110 kV - HT2 Transformador TR2 30 MVA 110/44 kV",18.042000000000002,7.1999999999999995E-2,16.161999999999999,4.2999999999999997E-2,15.439,6.2E-2,17.495999999999999,6.3E-2,18.042000000000002,17.970000000000002,17.970000000000002]
[null,null,null,"Las Vegas 110 kV - HT3 Tranaformador TR3 25 MVA 110/13.2 kV",18.042000000000002,9.1999999999999998E-2,16.161999999999999,5.6000000000000001E-2,15.439,7.8E-2,17.495999999999999,0.08,18.042000000000002,17.950000000000003,17.950000000000003]
[null,null,null,"Las Vegas 110 kV - HT5 Transformador TR5 30 MVA 115/13.2 kV",18.042000000000002,0,16.161999999999999,0,15.439,0,17.495999999999999,0,18.042000000000002,18.042000000000002,18.042000000000002]
[null,null,null,"Las Vegas 110 kV - H7 Línea 110 kV Las Vegas - Cristalerías (Llay Llay)",18.042000000000002,0,16.161999999999999,0,15.439,0,17.495999999999999,0,18.042000000000002,18.042000000000002,18.042000000000002]
[null,"Las Vizcachas",110,"Las Vizcachas 110 kV - H1 Línea 110kV Las Vizcachas - Puente Alto (EEPA)",16.835999999999999,0.34100000000000003,11.583,0.76900000000000002,14.494999999999999,0.32600000000000001,15.579000000000001,0.56499999999999995,16.835999999999999,16.494999999999997,16.494999999999997]
[null,"Leyda",110,"Leyda 110 kV - HT1 Transformador TR1 12,5/10 MVA 115/13.8 kV",4.0359999999999996,0,3.3559999999999999,0,3.4950000000000001,0,3.7839999999999998,0,4.0359999999999996,4.0359999999999996,4.0359999999999996]
[null,null,null,"Leyda 110 kV - H1 Línea 110 kV Leyda - Alto Melipilla C2",4.0359999999999996,2.5070000000000001,3.3559999999999999,2.1080000000000001,3.4950000000000001,2.1709999999999998,3.7839999999999998,2.37,4.0359999999999996,1.5289999999999995,2.5070000000000001]
[null,null,null,"Leyda 110 kV - H2 Línea 110 kV Leyda - San Antonio C2",4.0359999999999996,1.5309999999999999,3.3559999999999999,1.25,3.4950000000000001,1.3260000000000001,3.7839999999999998,1.4179999999999999,4.0359999999999996,2.5049999999999999,2.5049999999999999]
[null,"Linares",154,"Linares 154 kV - AT1 Transformador TR01 60/75MVA",5.6369999999999996,0.69699999999999995,5.5149999999999997,1.0640000000000001,4.8680000000000003,0.59699999999999998,5.77,1.026,5.77,4.9399999999999995,4.9399999999999995]
[null,"Llanta C1",110,"Llanta C1 110 kV -  En Barra",4.8899999999999997,0,4.8609999999999998,0,4.2240000000000002,0,5.0880000000000001,0,5.0880000000000001,5.0880000000000001,5.0880000000000001]
[null,"Llanta C2",110,"Llanta C2 110 kV -  En Barra",5.0220000000000002,0,5.0460000000000003,0,4.3369999999999997,0,5.2649999999999997,0,5.2649999999999997,5.2649999999999997,5.2649999999999997]
[null,"Lo Aguirre",110,"Lo Aguirre 110 kV - H1 Línea 110 kV Lo Aguirre - Cerro Navia (Enel)/Lo Prado 2",7.1820000000000004,7.1820000000000004,4.4749999999999996,4.4749999999999996,6.2220000000000004,6.2220000000000004,6.7320000000000002,6.7320000000000002,7.1820000000000004,0,7.1820000000000004]
[null,"Lo Boza",110,"Lo Boza 110 kV - H1 Línea 110 kV Lo Boza - San Cristóbal/Cerro Navia (Enel) 1",34.159999999999997,17.079999999999998,17.501000000000001,8.7509999999999994,29.571999999999999,14.786,30.265000000000001,15.132,34.159999999999997,17.079999999999998,17.079999999999998]
[null,null,null,"Lo Boza 110 kV - H2 Línea 110 kV Lo Boza - San Cristóbal/Cerro Navia (Enel) 2",34.159999999999997,17.079999999999998,17.501000000000001,8.7509999999999994,29.571999999999999,14.786,30.265000000000001,15.132,34.159999999999997,17.079999999999998,17.079999999999998]
[null,null,null,"Lo Boza 110 kV - HT3 Transformador TR03 12,5 MVA 110/23.5 kV ",34.159999999999997,0,17.501000000000001,0,29.571999999999999,0,30.265000000000001,0,34.159999999999997,34.159999999999997,34.159999999999997]
[null,"Lo Espejo",110,"Lo Espejo 110 kV -  En Barra",48.628,0,39.569000000000003,0,42.113,0,45.536000000000001,0,48.628,48.628,48.628]
[null,"Lo Espejo (FFCC)",110,"Lo Espejo (FFCC) 110 kV -  En Barra",44.302,0,27.652000000000001,0,38.345999999999997,0,39.911000000000001,0,44.302,44.302,44.302]
[null,"Lo Prado",110,"Lo Prado 110 kV - H1 Línea 110 kV Lo Prado - Lo Aguirre",7.202,7.008,4.59,4.5069999999999997,6.2389999999999999,6.0659999999999998,6.7690000000000001,6.6130000000000004,7.202,0.19399999999999995,7.008]
[null,"Lo Valledor",110,"Lo Valledor 110 kV - H1 Línea 110 kV Lo Valledor - Cerro Navia (Enel)/Chena 1",27.937000000000001,13.968,12.785,6.3929999999999998,24.196000000000002,12.098000000000001,24.771000000000001,12.385999999999999,27.937000000000001,13.969000000000001,13.969000000000001]
[null,null,null,"Lo Valledor 110 kV - HT1 Transformador TR01 25 MVA 110/13.2 kV",27.937000000000001,0,12.785,0,24.196000000000002,0,24.771000000000001,0,27.937000000000001,27.937000000000001,27.937000000000001]
[null,null,null,"Lo Valledor 110 kV - HT4 Transformador TR04 110/12.5 kV",27.937000000000001,0,12.785,0,24.196000000000002,0,24.771000000000001,0,27.937000000000001,27.937000000000001,27.937000000000001]
[null,null,null,"Lo Valledor 110 kV - HT3 Transformador TR03 50 MVA 110/12.5 kV",27.937000000000001,0,12.785,0,24.196000000000002,0,24.771000000000001,0,27.937000000000001,27.937000000000001,27.937000000000001]
[null,null,null,"Lo Valledor 110 kV - HT2 Transformador TR02 25 MVA 110/12.5 kV",27.937000000000001,0,12.785,0,24.196000000000002,0,24.771000000000001,0,27.937000000000001,27.937000000000001,27.937000000000001]
[null,null,null,"Lo Valledor 110 kV - H2 Línea 110 kV Lo Valledor - Cerro Navia (Enel)/ Chena 2",27.937000000000001,13.968,12.785,6.3929999999999998,24.196000000000002,12.098000000000001,24.771000000000001,12.385999999999999,27.937000000000001,13.969000000000001,13.969000000000001]
[null,"Lord Cochrane",110,"Lord Cochrane 110 kV - HT1 Transformador TR01 44,7 MVA 110/12.5 kV ",45.648000000000003,0,37.354999999999997,0,39.469000000000001,0,43.792000000000002,0,45.648000000000003,45.648000000000003,45.648000000000003]
[null,null,null,"Lord Cochrane 110 kV - HT2 Transformador TR02 44,7 MVA 110/12.5 kV ",45.648000000000003,0,37.354999999999997,0,39.469000000000001,0,43.792000000000002,0,45.648000000000003,45.648000000000003,45.648000000000003]
[null,"Los Almendros",110,"Los Almendros 110 kV -  H1 Línea 110 kV Los Almendros - Los Dominicos/El Salto 1",30.96,6.3410000000000002,28.273,4.4080000000000004,26.81,5.4950000000000001,30.158000000000001,5.6669999999999998,30.96,24.619,24.619]
[null,null,null,"Los Almendros 110 kV -  H2 Línea 110 kV Los Almendros - El Salto C2",30.96,5.6349999999999998,28.273,3.9769999999999999,26.81,4.883,30.158000000000001,5.0410000000000004,30.96,25.325000000000003,25.325000000000003]
[null,null,null,"Los Almendros 110 kV -  H3 Línea 110 kV Los Almendros - Florida C1",30.96,4.4279999999999999,28.273,3.06,26.81,3.8260000000000001,30.158000000000001,3.9750000000000001,30.96,26.532,26.532]
[null,null,null,"Los Almendros 110 kV -  H4 Línea 110 kV Los Almendros - Andes/Florida C2",30.96,4.4279999999999999,28.273,3.06,26.81,3.8260000000000001,30.158000000000001,3.9750000000000001,30.96,26.532,26.532]
[null,null,null,"Los Almendros 110 kV - HT1 Transformador TR01 400 MVA 220/110 kV",30.96,10.231999999999999,28.273,13.83,26.81,8.8710000000000004,30.158000000000001,12.057,30.96,20.728000000000002,20.728000000000002]
[null,"Los Angeles",154,"Los Angeles 154 kV - AT3 Transformador Los Ángeles TR03 56MVA 154/66 kV N°3",5.6550000000000002,0.60699999999999998,5.6680000000000001,0.9,4.8390000000000004,0.51200000000000001,5.9729999999999999,0.82099999999999995,5.9729999999999999,5.1520000000000001,5.1520000000000001]
[null,null,null,"Los Angeles 154 kV - AT4 Transformador Los Ángeles TR04 56MVA 154/66 kV N°4",5.6550000000000002,0.91200000000000003,5.6680000000000001,1.22,4.8390000000000004,0.76900000000000002,5.9729999999999999,1.1379999999999999,5.9729999999999999,4.835,4.835]
[null,null,null,"Los Angeles 154 kV - A1 Línea 154 kV Los Ángeles - Charrúa",5.6550000000000002,4.1589999999999998,5.6680000000000001,3.2559999999999998,4.8390000000000004,3.5760000000000001,5.9729999999999999,3.8839999999999999,5.9729999999999999,2.4120000000000004,4.1589999999999998]
[null,null,null,"Los Angeles 154 kV - A2 Línea 154 kV Los Ángeles - Negrete Cuel /Tap Santa Luisa/Santa Fe",5.6550000000000002,0,5.6680000000000001,0.307,4.8390000000000004,0,5.9729999999999999,0.314,5.9729999999999999,5.6589999999999998,5.6589999999999998]
[null,"Los Colorados",110,"Los Colorados 110 kV - H1 Transformador TR01 110/13.2 kV ",2.9529999999999998,0,1.976,0,2.556,0,2.839,0,2.9529999999999998,2.9529999999999998,2.9529999999999998]
[null,"Los Dominicos",110,"Los Dominicos 110 kV - H1 Línea 110 kV Los Dominicos - Los Almendros/El Salto 1",21.503,10.795999999999999,11.571,5.8019999999999996,18.623999999999999,9.3510000000000009,19.231000000000002,9.657,21.503,10.707000000000001,10.795999999999999]
[null,null,null,"Los Dominicos 110 kV - H2 Línea 110 kV Los Dominicos - Los Almendros/ El Salto 2",21.503,10.707000000000001,11.571,5.77,18.623999999999999,9.2729999999999997,19.231000000000002,9.5749999999999993,21.503,10.795999999999999,10.795999999999999]
[null,"Los Libertadores",110,"Los Libertadores 110 kV - HX1 Línea 110kV TO Libertadores-Libertadores C2",27.753,13.877000000000001,18.274000000000001,9.1370000000000005,24.018000000000001,12.009,25.297999999999998,12.648999999999999,27.753,13.875999999999999,13.877000000000001]
[null,null,null,"Los Libertadores 110 kV - HX2 Línea 110kV TO Libertadores-Libertadores C1",27.753,13.877000000000001,18.274000000000001,9.1370000000000005,24.018000000000001,12.009,25.297999999999998,12.648999999999999,27.753,13.875999999999999,13.877000000000001]
[null,"Los Loros",110,"Los Loros 110 kV - HT1 Transformador T1 20/16/12 MVA 110/24-13,8 kV",1.996,0,2.37,0,1.728,0,2.4340000000000002,0,2.4340000000000002,2.4340000000000002,2.4340000000000002]
[null,null,null,"Los Loros 110 kV - H1 Línea 110 kV Los Loros - Central PV Los Loros 1",1.996,0,2.37,0.61199999999999999,1.728,0,2.4340000000000002,0.748,2.4340000000000002,1.996,1.996]
[null,"Los Maquis",110,"Los Maquis 110 kV - H3 Línea 110 kV Los Maquis - Aconcagua/Fundición Chagres 1",10.228999999999999,2.5920000000000001,11.305999999999999,2.5110000000000001,9.1240000000000006,2.2919999999999998,11.016,2.6160000000000001,11.305999999999999,8.7949999999999982,8.7949999999999982]
[null,null,null,"Los Maquis 110 kV - H4 Línea 110 kV Los Maquis - Aconcagua / Totoralillo / Esperanza (HASA) 2",10.228999999999999,2.6070000000000002,11.305999999999999,2.6429999999999998,9.1240000000000006,2.4359999999999999,11.016,2.6619999999999999,11.305999999999999,8.6630000000000003,8.6630000000000003]
[null,null,null,"Los Maquis 110 kV - H5 Línea 110 kV Los Maquis - Central Los Quilos 1",10.228999999999999,0.59,11.305999999999999,0.88800000000000001,9.1240000000000006,0.51600000000000001,11.016,0.76200000000000001,11.305999999999999,10.417999999999999,10.417999999999999]
[null,null,null,"Los Maquis 110 kV - HS Transformador TR01 95 MVA 220/110/12 kV",10.228999999999999,4.53,11.305999999999999,5.3230000000000004,9.1240000000000006,3.9369999999999998,11.016,4.984,11.305999999999999,6.032,6.032]
[null,"Los Placeres (Placeres)",110,"Los Placeres (Placeres) 110 kV - HT1 Transformador TR1 110/12 kV ",12.747,0,8.2059999999999995,0,11.065,0,11.612,0,12.747,12.747,12.747]
[null,null,null,"Los Placeres (Placeres) 110 kV - HT2 Transformador TR2 110/12 kV ",12.747,0,8.2059999999999995,0,11.065,0,11.612,0,12.747,12.747,12.747]
[null,"Macul",110,"Macul 110 kV - H1 Línea 110 kV Macul - Ochagavia/Florida 1",30.943999999999999,15.472,14.465,7.2320000000000002,26.747,13.372999999999999,27.206,13.603,30.943999999999999,15.472,15.472]
[null,null,null,"Macul 110 kV - H2 Línea 110 kV Macul - Ochagavia/Florida 2",30.943999999999999,15.472,14.465,7.2320000000000002,26.747,13.372999999999999,27.206,13.603,30.943999999999999,15.472,15.472]
[null,null,null,"Macul 110 kV - H4 Transformador TR04 50 MVA 110/12.5 kV ",30.943999999999999,0,14.465,0,26.747,0,27.206,0,30.943999999999999,30.943999999999999,30.943999999999999]
[null,null,null,"Macul 110 kV - H6 Transformador TR06 50 MVA 110/20.4 kV",30.943999999999999,0,14.465,0,26.747,0,27.206,0,30.943999999999999,30.943999999999999,30.943999999999999]
[null,"Magnetita",110,"Magnetita 110 kV - H7 Transformador TR 28MVA 110/4,16kV",3.7069999999999999,0,3.98,0,3.2069999999999999,0,3.9790000000000001,0,3.98,3.98,3.98]
[null,"Maipo",110,"Maipo 110 kV - H1 Línea 110 kV Maipo - Puente Alto (CMPC)/Pirque ",3.629,1.042,3.8610000000000002,1.163,3.194,0.94699999999999995,3.7690000000000001,1.1020000000000001,3.8610000000000002,2.6980000000000004,2.6980000000000004]
[null,"Maipú",110,"Maipú 110 kV - H1 Línea 110 kV Maipu - Cerro Navia (Enel)/Chena 1",47.06,23.53,38.448999999999998,19.225000000000001,40.756999999999998,20.379000000000001,44.085000000000001,22.042999999999999,47.06,23.53,23.53]
[null,null,null,"Maipú 110 kV - H2 Línea 110 kV Maipu - Cerro Navia (Enel)/Chena 2",47.06,23.53,38.448999999999998,19.225000000000001,40.756999999999998,20.379000000000001,44.085000000000001,22.042999999999999,47.06,23.53,23.53]
[null,"Maitencillo",110,"Maitencillo 110 kV - H1 Línea 110 kV Maitencillo - Pan de Azucar",8.9030000000000005,0.63400000000000001,9.9190000000000005,0.53900000000000003,7.6989999999999998,0.54900000000000004,9.7050000000000001,0.61299999999999999,9.9190000000000005,9.3800000000000008,9.3800000000000008]
[null,null,null,"Maitencillo 110 kV - HT2 Transformador ATR2 90 MVA 220/115/13.2 kV",8.9030000000000005,3.05,9.9190000000000005,3.5630000000000002,7.6989999999999998,2.637,9.7050000000000001,3.38,9.9190000000000005,6.3559999999999999,6.3559999999999999]
[null,null,null,"Maitencillo 110 kV - H2 Línea 110 kV Maitencillo - Huasco C2",8.9030000000000005,0.68100000000000005,9.9190000000000005,0.75600000000000001,7.6989999999999998,0.58599999999999997,9.7050000000000001,0.70199999999999996,9.9190000000000005,9.1630000000000003,9.1630000000000003]
[null,null,null,"Maitencillo 110 kV - HT1 Transformador ATR1 90 MVA 220/115/13.2 kV",8.9030000000000005,2.9609999999999999,9.9190000000000005,3.4620000000000002,7.6989999999999998,2.56,9.7050000000000001,3.2730000000000001,9.9190000000000005,6.4570000000000007,6.4570000000000007]
[null,null,null,"Maitencillo 110 kV - H3 Línea 110 kV Maitencillo - Huasco 1",8.9030000000000005,0.67200000000000004,9.9190000000000005,0.74199999999999999,7.6989999999999998,0.57799999999999996,9.7050000000000001,0.69099999999999995,9.9190000000000005,9.1769999999999996,9.1769999999999996]
[null,null,null,"Maitencillo 110 kV - H4 Línea 110 kV Maitencillo - Vallenar",8.9030000000000005,0.123,9.9190000000000005,0.189,7.6989999999999998,0.112,9.7050000000000001,0.16800000000000001,9.9190000000000005,9.73,9.73]
[null,null,null,"Maitencillo 110 kV - H5 Línea 110 kV Maitencillo - Cardones/Tap Off Punta Toro",8.9030000000000005,0.95399999999999996,9.9190000000000005,0.79800000000000004,7.6989999999999998,0.82599999999999996,9.7050000000000001,0.90700000000000003,9.9190000000000005,9.1210000000000004,9.1210000000000004]
[null,"Malloco",110,"Malloco 110 kV - HT1 Transformador TR01 22,4 MVA 110/12.5 kV",7.2649999999999997,0,4.2309999999999999,0,6.2930000000000001,0,6.8380000000000001,0,7.2649999999999997,7.2649999999999997,7.2649999999999997]
[null,null,null,"Malloco 110 kV - HT2 Transformador TR02 22,4 MVA 110/12.5 kV ",7.2649999999999997,0,4.2309999999999999,0,6.2930000000000001,0,6.8380000000000001,0,7.2649999999999997,7.2649999999999997,7.2649999999999997]
[null,null,null,"Malloco 110 kV - HT3 Transformador TR03 37,5 MVA 110/23.5 kV ",7.2649999999999997,0,4.2309999999999999,0,6.2930000000000001,0,6.8380000000000001,0,7.2649999999999997,7.2649999999999997,7.2649999999999997]
[null,null,null,"Malloco 110 kV - H4 Transformador TR04 50 MVA 110/23.5 kV ",7.2649999999999997,0,4.2309999999999999,0,6.2930000000000001,0,6.8380000000000001,0,7.2649999999999997,7.2649999999999997,7.2649999999999997]
[null,"Mantilhue",110,"Mantilhue 110 kV - H1 Línea 110 kV Mantilhue - Chirre",3.3809999999999998,2.6059999999999999,3.55,2.2309999999999999,2.9460000000000002,2.2839999999999998,3.589,2.484,3.589,1.319,2.6059999999999999]
[null,null,null,"Mantilhue 110 kV - H2 Línea 110 kV Mantilhue - Mocho",3.3809999999999998,0.35299999999999998,3.55,0.65900000000000003,2.9460000000000002,0.3,3.589,0.57599999999999996,3.589,3.0279999999999996,3.0279999999999996]
[null,"Mantos de la Luna",110,"Mantos de la Luna 110 kV - H1 Línea 110 kV Mantos de la Luna - Tap Off Barriles ",1.115,1.115,0.71,0.71,0.96499999999999997,0.96499999999999997,1.002,1.002,1.115,0,1.115]
[null,"Manto Verde",110,"Manto Verde 110 kV - HT1 Transformador TR1 110/13.8 kV ",2.6739999999999999,0,1.7070000000000001,0,2.3130000000000002,0,2.4380000000000002,0,2.6739999999999999,2.6739999999999999,2.6739999999999999]
[null,null,null,"Manto Verde 110 kV - HT2 Transformador TR2 110/13.8 kV",2.6739999999999999,0,1.7070000000000001,0,2.3130000000000002,0,2.4380000000000002,0,2.6739999999999999,2.6739999999999999,2.6739999999999999]
[null,null,null,"Manto Verde 110 kV - H1 Línea 110 kV Manto Verde - Diego de Almagro",2.6739999999999999,2.6739999999999999,1.7070000000000001,1.7070000000000001,2.3130000000000002,2.3130000000000002,2.4380000000000002,2.4380000000000002,2.6739999999999999,0,2.6739999999999999]
[null,null,null,"Manto Verde 110 kV - H2 Línea 110 kV Manto Verde - Planta Bombeo 2/Planta Desaladora y Planta Bombeo 1 ",2.6739999999999999,0,1.7070000000000001,0,2.3130000000000002,0,2.4380000000000002,0,2.6739999999999999,2.6739999999999999,2.6739999999999999]
[null,"Mapal",154,"Mapal 154 kV -  AT Transformador TR1 24MVA 154/15kV",12.98,0,12.805,0,11.24,0,13.244,0,13.244,13.244,13.244]
[null,"Marbella",110,"Marbella 110 kV -  H1 Línea 110 kV Marbella - Casas Viejas C1",3.91,1.246,2.581,0.81100000000000005,3.3820000000000001,1.073,3.6920000000000002,1.173,3.91,2.6640000000000001,2.6640000000000001]
[null,null,null,"Marbella 110 kV - HT1 Transformador TR1 13 MVA 110/24 kV ",3.91,0,2.581,0,3.3820000000000001,0,3.6920000000000002,0,3.91,3.91,3.91]
[null,null,null,"Marbella 110 kV - H2 Línea 110 kV Marbella - Quillota C1",3.91,2.6640000000000001,2.581,1.77,3.3820000000000001,2.3079999999999998,3.6920000000000002,2.5190000000000001,3.91,1.246,2.6640000000000001]
[null,"Marga Marga",110,"Marga Marga 110 kV - HT1 Transformador TR1 115/13.6 kV",18.853000000000002,0,13.454000000000001,0,16.404,0,17.349,0,18.853000000000002,18.853000000000002,18.853000000000002]
[null,null,null,"Marga Marga 110 kV - HT2 Transformador TR2 115/14.2 kV",18.853000000000002,0,13.454000000000001,0,16.404,0,17.349,0,18.853000000000002,18.853000000000002,18.853000000000002]
[null,null,null,"Marga Marga 110 kV - HT3 Transformador TR3 115/15.3 kV",18.853000000000002,0,13.454000000000001,0,16.404,0,17.349,0,18.853000000000002,18.853000000000002,18.853000000000002]
[null,"Mariscal",110,"Mariscal 110 kV - H1 Línea 110 kV Mariscal - La Pintana/Santa Rosa Sur 2",22.295999999999999,11.148,11.242000000000001,5.6210000000000004,19.300999999999998,9.65,19.681000000000001,9.84,22.295999999999999,11.148,11.148]
[null,null,null,"Mariscal 110 kV - H2 Línea 110 kV Mariscal - La Pintana/Santa Rosa Sur 1",22.295999999999999,11.148,11.242000000000001,5.6210000000000004,19.300999999999998,9.65,19.681000000000001,9.84,22.295999999999999,11.148,11.148]
[null,null,null,"Mariscal 110 kV - HT1 Transformador TR01 50 MVA 110/12 kV",22.295999999999999,0,11.242000000000001,0,19.300999999999998,0,19.681000000000001,0,22.295999999999999,22.295999999999999,22.295999999999999]
[null,null,null,"Mariscal 110 kV - HT2 Transformador TR02 30 MVA 110/23 kV ",22.295999999999999,0,11.242000000000001,0,19.300999999999998,0,19.681000000000001,0,22.295999999999999,22.295999999999999,22.295999999999999]
[null,null,null,"Mariscal 110 kV - HT3 Transformador TR03 30 MVA 110/23 kV ",22.295999999999999,0,11.242000000000001,0,19.300999999999998,0,19.681000000000001,0,22.295999999999999,22.295999999999999,22.295999999999999]
[null,"Mauco",110,"Mauco 110 kV - HL1 Línea 110 kV Mauco - Torquemada 1",18.501000000000001,8.3759999999999994,16.241,6.5209999999999999,16.212,7.2510000000000003,17.797000000000001,7.6790000000000003,18.501000000000001,10.125000000000002,10.125000000000002]
[null,null,null,"Mauco 110 kV - HL2 Línea 110 kV Mauco - Torquemada 2",18.501000000000001,8.3759999999999994,16.241,6.5209999999999999,16.212,7.2510000000000003,17.797000000000001,7.6790000000000003,18.501000000000001,10.125000000000002,10.125000000000002]
[null,null,null,"Mauco 110 kV - HT1 Transformador TR1 110/12 kV ",18.501000000000001,0,16.241,0,16.212,0,17.797000000000001,0,18.501000000000001,18.501000000000001,18.501000000000001]
[null,null,null,"Mauco 110 kV - HT2 Transformador TR2110/12 kV ",18.501000000000001,0,16.241,0,16.212,0,17.797000000000001,0,18.501000000000001,18.501000000000001,18.501000000000001]
[null,"Maule",154,"Maule 154 kV -  A1 Línea 154kV Maule - Itahue",10.526,3.1549999999999998,13.586,2.931,9.0960000000000001,2.7250000000000001,13.635,3.052,13.635,10.655000000000001,10.655000000000001]
[null,null,null,"Maule 154 kV -  A2 Línea 154kV Maule - Linares/Yerbas Buenas",10.526,1.4750000000000001,13.586,1.4259999999999999,9.0960000000000001,1.27,13.635,1.4710000000000001,13.635,12.164,12.164]
[null,null,null,"Maule 154 kV -  AT Interruptor común Trafo 01 y Trafo 02.",10.526,1.127,13.586,1.3160000000000001,9.0960000000000001,0.97299999999999998,13.635,1.327,13.635,12.308,12.308]
[null,null,null,"Maule 154 kV - HTX Transformador ATR5 300MVA 220/154/24kV",10.526,4.8109999999999999,13.586,7.9489999999999998,9.0960000000000001,4.165,13.635,8.0169999999999995,13.635,5.7149999999999999,8.0169999999999995]
[null,"Mayaca",110,"Mayaca 110 kV - HTX Transformador 30MVA 110/12kV",14.74,0,9.2490000000000006,0,12.73,0,13.347,0,14.74,14.74,14.74]
[null,null,null,"Mayaca 110 kV - HX1 Línea 110kV TO Mayaca - Mayaca C1",14.74,7.37,9.2490000000000006,4.625,12.73,6.3650000000000002,13.347,6.673,14.74,7.37,7.37]
[null,null,null,"Mayaca 110 kV - HX2 Línea 110kV TO Mayaca - Mayaca C2",14.74,7.37,9.2490000000000006,4.6239999999999997,12.73,6.3650000000000002,13.347,6.673,14.74,7.37,7.37]
[null,"MDP Teno (Paneles MDP)",154,"MDP Teno (Paneles MDP) 154 kV - A1 Línea 154 kV MDP Teno - Teno",6.8010000000000002,6.8010000000000002,4.0430000000000001,4.0439999999999996,5.8819999999999997,5.8819999999999997,6.1120000000000001,6.1120000000000001,6.8010000000000002,0,6.8010000000000002]
[null,"Mejillones",110,"Mejillones 110 kV - H4 Línea 110 kV Mejillones - Central Diesel Enaex 1",7.3040000000000003,6.9000000000000006E-2,7.9850000000000003,4.8000000000000001E-2,6.2050000000000001,5.3999999999999999E-2,7.8849999999999998,5.8999999999999997E-2,7.9850000000000003,7.9370000000000003,7.9370000000000003]
[null,null,null,"Mejillones 110 kV - H5 Línea 110 kV Mejillones - Chacaya C1",7.3040000000000003,0.90600000000000003,7.9850000000000003,0.93600000000000005,6.2050000000000001,0.78400000000000003,7.8849999999999998,0.93200000000000005,7.9850000000000003,7.0490000000000004,7.0490000000000004]
[null,null,null,"Mejillones 110 kV - H1 Línea 110 kV Mejillones - Antofagasta/Desalant 1",7.3040000000000003,1.621,7.9850000000000003,1.333,6.2050000000000001,1.387,7.8849999999999998,1.5069999999999999,7.9850000000000003,6.6520000000000001,6.6520000000000001]
[null,null,null,"Mejillones 110 kV - H2 Línea 110 kV Mejillones - El Lince ",7.3040000000000003,0,7.9850000000000003,2E-3,6.2050000000000001,0,7.8849999999999998,2E-3,7.9850000000000003,7.9830000000000005,7.9830000000000005]
[null,null,null,"Mejillones 110 kV - HT Transformador TR01 80/80/20 MVA 220/115/13.8 kV ",7.3040000000000003,3.9529999999999998,7.9850000000000003,4.6959999999999997,6.2050000000000001,3.42,7.8849999999999998,4.4379999999999997,7.9850000000000003,3.4470000000000001,4.6959999999999997]
[null,null,null,"Mejillones 110 kV - H3/HT2 Transformador TR03 30/25 MVA 110/13.8 kV",7.3040000000000003,0.80400000000000005,7.9850000000000003,1.0089999999999999,6.2050000000000001,0.60399999999999998,7.8849999999999998,0.98399999999999999,7.9850000000000003,6.9760000000000009,6.9760000000000009]
[null,"Melipeuco",110,"Melipeuco 110 kV - H1 Línea 110 kV Melipeuco - Río Tolten/Cunco",1.5149999999999999,1.143,1.7609999999999999,0.98099999999999998,1.2949999999999999,0.98899999999999999,1.758,1.073,1.7609999999999999,0.77999999999999992,1.143]
[null,"Melipulli",110,"Melipulli 110 kV - H1 Línea 110 kV Melipulli - Alto Bonito/Central Trapén/Molinos (Enlasa) 1",4.4409999999999998,1.875,5.1710000000000003,1.5780000000000001,3.8050000000000002,1.607,5.0439999999999996,1.722,5.1710000000000003,3.593,3.593]
[null,null,null,"Melipulli 110 kV - HT11 Transformador T11 60 MVA 230/115/69 kV",4.4409999999999998,1.827,5.1710000000000003,2.92,3.8050000000000002,1.573,5.0439999999999996,2.77,5.1710000000000003,2.6139999999999999,2.92]
[null,"Metro",110,"Metro 110 kV - ITRA1 Transformador TRA1 110/20 kV ",45.603000000000002,0,37.311999999999998,0,39.43,0,43.750999999999998,0,45.603000000000002,45.603000000000002,45.603000000000002]
[null,null,null,"Metro 110 kV - ITRB1 Transformador TRB2 110/20 kV ",45.603000000000002,0,37.311999999999998,0,39.43,0,43.750999999999998,0,45.603000000000002,45.603000000000002,45.603000000000002]
[null,null,null,"Metro 110 kV - ITRC1 Transformador TRC1 110/20 kV",45.603000000000002,0,37.311999999999998,0,39.43,0,43.750999999999998,0,45.603000000000002,45.603000000000002,45.603000000000002]
[null,"Minera Franke",110,"Minera Franke 110 kV -  En Barra",1.599,0,1.0449999999999999,0,1.3839999999999999,0,1.524,0,1.599,1.599,1.599]
[null,"Minera Maricunga",110,"Minera Maricunga 110 kV - 00-BK-101 Transformador  ATR1 110/23 kV",1.1339999999999999,0,0.66900000000000004,0,0.98199999999999998,0,1.0149999999999999,0,1.1339999999999999,1.1339999999999999,1.1339999999999999]
[null,null,null,"Minera Maricunga 110 kV - 00-BK-102 Transformador ATR2 110/23 kV N°2",1.1339999999999999,0,0.66900000000000004,0,0.98199999999999998,0,1.0149999999999999,0,1.1339999999999999,1.1339999999999999,1.1339999999999999]
[null,"Minera Teck CDA",110,"Minera Teck CDA 110 kV - H1 Transformador TR 12/15 MVA 220/13.2 kV",3.3620000000000001,3.3620000000000001,2.194,2.1949999999999998,2.899,2.899,3.16,3.16,3.3620000000000001,0,3.3620000000000001]
[null,"Minera Valle Central",154,"Minera Valle Central 154 kV - AT1 Transformador TR1 154/4,16kV",9.5399999999999991,0.20799999999999999,8.1199999999999992,0.12,8.2870000000000008,0.184,9.6649999999999991,0.191,9.6649999999999991,9.4739999999999984,9.4739999999999984]
[null,null,null,"Minera Valle Central 154 kV - AT2 Transformador TR2 154/4,16kV",9.5399999999999991,0.20799999999999999,8.1199999999999992,0.12,8.2870000000000008,0.184,9.6649999999999991,0.191,9.6649999999999991,9.4739999999999984,9.4739999999999984]
[null,null,null,"Minera Valle Central 154 kV - AT3 Transformador 154/23 kV N°3 ",9.5399999999999991,4.2999999999999997E-2,8.1199999999999992,2.4E-2,8.2870000000000008,3.5000000000000003E-2,9.6649999999999991,3.9E-2,9.6649999999999991,9.6259999999999994,9.6259999999999994]
[null,"Minero",110,"Minero 110 kV - H1 Línea 110 kV Minero - Colón 1",19.212,0,21.109000000000002,0,16.722999999999999,0,20.420000000000002,0,21.109000000000002,21.109000000000002,21.109000000000002]
[null,null,null,"Minero 110 kV - H2 Línea 110 kV Minero - Colón 2",19.212,0,21.109000000000002,0,16.722999999999999,0,20.420000000000002,0,21.109000000000002,21.109000000000002,21.109000000000002]
[null,null,null,"Minero 110 kV - H3 Línea 110 kV Minero - Cordillera 1",19.212,0,21.109000000000002,0,16.722999999999999,0,20.420000000000002,0,21.109000000000002,21.109000000000002,21.109000000000002]
[null,null,null,"Minero 110 kV - H4 Línea 110 kV Minero - Cordillera 2",19.212,0,21.109000000000002,0,16.722999999999999,0,20.420000000000002,0,21.109000000000002,21.109000000000002,21.109000000000002]
[null,null,null,"Minero 110 kV - H5 Línea 110 kV Minero - Sauzal 3",19.212,2.3690000000000002,21.109000000000002,2.2519999999999998,16.722999999999999,2.0390000000000001,20.420000000000002,2.2989999999999999,21.109000000000002,18.857000000000003,18.857000000000003]
[null,null,null,"Minero 110 kV - H6 Línea 110 kV Minero - Interconexión Chacayes/Sauzal 1",19.212,2.5739999999999998,21.109000000000002,2.4969999999999999,16.722999999999999,2.2330000000000001,20.420000000000002,2.516,21.109000000000002,18.612000000000002,18.612000000000002]
[null,null,null,"Minero 110 kV - H7 Línea 110 kV Minero - Interconexión Chacayes/Sauzal 2",19.212,2.5739999999999998,21.109000000000002,2.4969999999999999,16.722999999999999,2.2330000000000001,20.420000000000002,2.516,21.109000000000002,18.612000000000002,18.612000000000002]
[null,null,null,"Minero 110 kV - H8 Línea 110 kV Minero -  Sewell 1",19.212,0,21.109000000000002,0,16.722999999999999,0,20.420000000000002,0,21.109000000000002,21.109000000000002,21.109000000000002]
[null,null,null,"Minero 110 kV - H9 Línea 110 kV Minero -  Sewell 2",19.212,0,21.109000000000002,0,16.722999999999999,0,20.420000000000002,0,21.109000000000002,21.109000000000002,21.109000000000002]
[null,null,null,"Minero 110 kV - HR Paño Acoplador ",19.212,0,21.109000000000002,0,16.722999999999999,0,20.420000000000002,0,21.109000000000002,21.109000000000002,21.109000000000002]
[null,null,null,"Minero 110 kV - HT1 Transformador  TR1 230/115/13.8 kV ",19.212,3.9180000000000001,21.109000000000002,4.6420000000000003,16.722999999999999,3.423,20.420000000000002,4.3639999999999999,21.109000000000002,16.467000000000002,16.467000000000002]
[null,null,null,"Minero 110 kV - HT2 Transformador  TR2 230/115/13.8 kV ",19.212,3.9180000000000001,21.109000000000002,4.6420000000000003,16.722999999999999,3.423,20.420000000000002,4.3639999999999999,21.109000000000002,16.467000000000002,16.467000000000002]
[null,null,null,"Minero 110 kV - HT3 Transformador  TR3  230/115/13.8 kV ",19.212,3.9180000000000001,21.109000000000002,4.6420000000000003,16.722999999999999,3.423,20.420000000000002,4.3639999999999999,21.109000000000002,16.467000000000002,16.467000000000002]
[null,null,null,"Minero 110 kV - H10 Línea 110 kV Minero - El Cobre (Codelco) 1",19.212,0,21.109000000000002,0,16.722999999999999,0,20.420000000000002,0,21.109000000000002,21.109000000000002,21.109000000000002]
[null,null,null,"Minero 110 kV - H11 Línea 110 kV Minero - El Cobre (Codelco) 2",19.212,0,21.109000000000002,0,16.722999999999999,0,20.420000000000002,0,21.109000000000002,21.109000000000002,21.109000000000002]
[null,"Minsal",110,"Minsal 110 kV - H1 Transformador TR01 25/20 MVA 110/23 kV ",1.3380000000000001,0,1.143,0,1.1579999999999999,0,1.268,0,1.3380000000000001,1.3380000000000001,1.3380000000000001]
[null,null,null,"Minsal 110 kV - H2 Transformador TR02 30 MVA 110/23 kV",1.3380000000000001,0,1.143,0,1.1579999999999999,0,1.268,0,1.3380000000000001,1.3380000000000001,1.3380000000000001]
[null,"Miraflores",110,"Miraflores 110 kV - H3 Línea 110 kV Miraflores - San Pedro (AES GENER) 1",22.148,4.0720000000000001,16.797000000000001,2.9039999999999999,19.286000000000001,3.5430000000000001,20.468,3.798,22.148,18.076000000000001,18.076000000000001]
[null,null,null,"Miraflores 110 kV - H4 Línea 110 kV Miraflores - San Pedro (AES GENER) 2",22.148,4.0720000000000001,16.797000000000001,2.9039999999999999,19.286000000000001,3.5430000000000001,20.468,3.798,22.148,18.076000000000001,18.076000000000001]
[null,null,null,"Miraflores 110 kV - H5 Línea 110 kV Miraflores - Agua Santa 3",22.148,3.827,16.797000000000001,2.9009999999999998,19.286000000000001,3.3149999999999999,20.468,3.4889999999999999,22.148,18.320999999999998,18.320999999999998]
[null,null,null,"Miraflores 110 kV - H6 Línea 110 kV Miraflores - Agua Santa 4",22.148,3.827,16.797000000000001,2.9009999999999998,19.286000000000001,3.3149999999999999,20.468,3.4889999999999999,22.148,18.320999999999998,18.320999999999998]
[null,null,null,"Miraflores 110 kV - HS Paño Acoplador ",22.148,0,16.797000000000001,1E-3,19.286000000000001,0,20.468,1E-3,22.148,22.148,22.148]
[null,null,null,"Miraflores 110 kV - HT1 Transformador TR1 110/12 kV ",22.148,0,16.797000000000001,0,19.286000000000001,0,20.468,0,22.148,22.148,22.148]
[null,null,null,"Miraflores 110 kV - HT2 Transformador TR2 110/12 kV ",22.148,0,16.797000000000001,0,19.286000000000001,0,20.468,0,22.148,22.148,22.148]
[null,null,null,"Miraflores 110 kV - HT3 Transformador TR3 110/13.6 kV",22.148,0,16.797000000000001,0,19.286000000000001,0,20.468,0,22.148,22.148,22.148]
[null,null,null,"Miraflores 110 kV - H1 Línea 110 kV Miraflores - Ventanas/Torquemada 1",22.148,3.3050000000000002,16.797000000000001,2.6579999999999999,19.286000000000001,2.9,20.468,3.024,22.148,18.843,18.843]
[null,null,null,"Miraflores 110 kV - H2 Línea 110 kV Miraflores - Ventanas/Torquemada 2",22.148,3.3050000000000002,16.797000000000001,2.6579999999999999,19.286000000000001,2.9,20.468,3.024,22.148,18.843,18.843]
[null,null,null,"Miraflores 110 kV - H10 Línea 110 kV Miraflores -  Marga Marga 1",22.148,0,16.797000000000001,1E-3,19.286000000000001,0,20.468,1E-3,22.148,22.148,22.148]
[null,null,null,"Miraflores 110 kV - H11 Línea 110 kV Miraflores -  Marga Marga 2",22.148,0,16.797000000000001,1E-3,19.286000000000001,0,20.468,1E-3,22.148,22.148,22.148]
[null,"Mocho",110,"Mocho 110 kV - H1 Línea 110 kV Mocho - Mantilhue",2.7789999999999999,2.4239999999999999,3.0779999999999998,2.169,2.415,2.1120000000000001,3.1110000000000002,2.3639999999999999,3.1110000000000002,0.90899999999999981,2.4239999999999999]
[null,"Molinos (Enlasa)",110,"Molinos (Enlasa) 110 kV - HT Transformador TR1 100/80 MVA 110/23 kV ",4.4359999999999999,1.55,4.0170000000000003,0.96399999999999997,3.8029999999999999,1.341,4.2779999999999996,1.373,4.4359999999999999,3.0530000000000004,3.0530000000000004]
[null,null,null,"Molinos (Enlasa) 110 kV - H1 Línea 110 kV Molinos (Enlasa) - Alto Bonito 1",4.4359999999999999,1.91,4.0170000000000003,2.1560000000000001,3.8029999999999999,1.6379999999999999,4.2779999999999996,2.0529999999999999,4.4359999999999999,2.5259999999999998,2.5259999999999998]
[null,null,null,"Molinos (Enlasa) 110 kV - H2 Línea 110 kV Molinos (Enlasa) -  El Empalme 1",4.4359999999999999,0.98799999999999999,4.0170000000000003,0.90600000000000003,3.8029999999999999,0.83699999999999997,4.2779999999999996,0.93100000000000005,4.4359999999999999,3.448,3.448]
[null,"Monterrico",154,"Monterrico 154 kV - A1 Línea 154kV Monterrico - Parral",5.758,1.508,5.0860000000000003,1.361,4.9610000000000003,1.3029999999999999,5.5759999999999996,1.4870000000000001,5.758,4.25,4.25]
[null,null,null,"Monterrico 154 kV - AX Línea 154kV Monterrico - Charrúa",5.758,3.1280000000000001,5.0860000000000003,2.2989999999999999,4.9610000000000003,2.6920000000000002,5.5759999999999996,2.81,5.758,2.7870000000000004,3.1280000000000001]
[null,null,null,"Monterrico 154 kV - AT1 Transformador TR1 75MVA 154/66/13,2kV",5.758,1.139,5.0860000000000003,1.4379999999999999,4.9610000000000003,0.98099999999999998,5.5759999999999996,1.3740000000000001,5.758,4.6189999999999998,4.6189999999999998]
[null,"Muelle",110,"Muelle 110 kV - H1 Línea 110 kV Muelle - Chacaya C1",2.2189999999999999,1.714,1.4,1.1890000000000001,1.92,1.484,2.0630000000000002,1.6220000000000001,2.2189999999999999,0.50499999999999989,1.714]
[null,null,null,"Muelle 110 kV - H4 Línea 110 kV Muelle - Tap Off Antucoya/Tap Off Licancabur/Tap Off Sairecabur 1",2.2189999999999999,0.505,1.4,0.21099999999999999,1.92,0.437,2.0630000000000002,0.44500000000000001,2.2189999999999999,1.714,1.714]
[null,null,null,"Muelle 110 kV - H2 Transformador Muelle 110/24 kV N°1",2.2189999999999999,0,1.4,0,1.92,0,2.0630000000000002,0,2.2189999999999999,2.2189999999999999,2.2189999999999999]
[null,"Ochagavia",110,"Ochagavia 110 kV - H1 Línea 110 kV Ochagavia - Metro 1",45.488,19.181000000000001,28.175000000000001,12.382999999999999,39.347999999999999,16.559999999999999,40.75,16.975999999999999,45.488,26.306999999999999,26.306999999999999]
[null,null,null,"Ochagavia 110 kV - H2 Línea 110 kV Ochagavia - Florida 2",45.488,3.91,28.175000000000001,2.2349999999999999,39.347999999999999,3.38,40.75,3.4820000000000002,45.488,41.578000000000003,41.578000000000003]
[null,null,null,"Ochagavia 110 kV - H3 Línea 110 kV Ochagavia - Florida 1",45.488,3.91,28.175000000000001,2.2349999999999999,39.347999999999999,3.38,40.75,3.4820000000000002,45.488,41.578000000000003,41.578000000000003]
[null,null,null,"Ochagavia 110 kV - H4 Línea 110 kV Ochagavia - Chena 1",45.488,9.2929999999999993,28.175000000000001,5.6710000000000003,39.347999999999999,8.0559999999999992,40.75,8.4320000000000004,45.488,36.195,36.195]
[null,null,null,"Ochagavia 110 kV - H5 Línea 110 kV Ochagavia - Chena 2",45.488,9.2929999999999993,28.175000000000001,5.6710000000000003,39.347999999999999,8.0559999999999992,40.75,8.4320000000000004,45.488,36.195,36.195]
[null,null,null,"Ochagavia 110 kV - HT1 Transformador TR01 40 MVA 105/12 kV ",45.488,0,28.175000000000001,0,39.347999999999999,0,40.75,0,45.488,45.488,45.488]
[null,null,null,"Ochagavia 110 kV - AC1 Banco de Condensadores 1 ",45.488,0,28.175000000000001,0,39.347999999999999,0,40.75,0,45.488,45.488,45.488]
[null,null,null,"Ochagavia 110 kV - HT2 Transformador TR02 50 MVA  110/12.5 kV ",45.488,0,28.175000000000001,0,39.347999999999999,0,40.75,0,45.488,45.488,45.488]
[null,"Ovalle",110,"Ovalle 110 kV - H2 Línea 110 kV Ovalle -  El Peñón 2",4.5119999999999996,1.381,3.899,1.0169999999999999,3.8679999999999999,1.19,4.5839999999999996,1.3069999999999999,4.5839999999999996,3.2769999999999997,3.2769999999999997]
[null,null,null,"Ovalle 110 kV - HT3 Transformador TR03 30 MVA 110/66/23 kV",4.5119999999999996,0.38700000000000001,3.899,0.38,3.8679999999999999,0.32600000000000001,4.5839999999999996,0.40799999999999997,4.5839999999999996,4.1759999999999993,4.1759999999999993]
[null,null,null,"Ovalle 110 kV - H1 Línea 110 kV Ovalle - Punitaqui 1",4.5119999999999996,1.1359999999999999,3.899,0.87,3.8679999999999999,0.97099999999999997,4.5839999999999996,1.085,4.5839999999999996,3.4989999999999997,3.4989999999999997]
[null,null,null,"Ovalle 110 kV - HT4 Transformador TR 04 60 MVA 110/69/23 kV ",4.5119999999999996,0.251,3.899,0.63300000000000001,3.8679999999999999,0.21099999999999999,4.5839999999999996,0.54,4.5839999999999996,4.2609999999999992,4.2609999999999992]
[null,null,null,"Ovalle 110 kV - H3 Línea 110 kV Ovalle -  El Peñón 1",4.5119999999999996,1.371,3.899,1.018,3.8679999999999999,1.1819999999999999,4.5839999999999996,1.3049999999999999,4.5839999999999996,3.2789999999999999,3.2789999999999999]
[null,"Oxy",154,"Oxy 154 kV - A Transformador 154/69/13.8 kV N°1 ; Transformador 154/69/13.8 kV N°2",13.347,13.347,14.398,14.372999999999999,11.519,11.519,14.037000000000001,14.025,14.398,2.5000000000000355E-2,14.372999999999999]
[null,"Pacífico",110,"Pacífico 110 kV - HT1 Transformador TRAFO 33/25 MVA 110/13.8 kV ",2.82,0,2.7490000000000001,0,2.423,0,2.8140000000000001,0,2.82,2.82,2.82]
[null,"Padre Hurtado",110,"Padre Hurtado 110 kV - HTX Transformador TR01 30 MVA 110/23 kV",16.734999999999999,0,8.3040000000000003,0,14.494,0,14.82,0,16.734999999999999,16.734999999999999,16.734999999999999]
[null,null,null,"Padre Hurtado 110 kV - HX Línea 110 kV Padre Hurtado - Santa Marta",16.734999999999999,16.734999999999999,8.3040000000000003,8.3040000000000003,14.494,14.494,14.82,14.82,16.734999999999999,0,16.734999999999999]
[null,"Paine",154,"Paine 154 kV - AT Transformador TR1 56MVA 154/66/13,2kV - TR2 75MVA 230-154/69/14,8kV",11.637,10.395,9.6549999999999994,8.0619999999999994,10.11,9.0329999999999995,10.952999999999999,9.5399999999999991,11.637,1.593,10.395]
[null,"Pajaritos",110,"Pajaritos 110 kV - H1 Línea 110 kV Pajaritos - Cerro Navia (Enel)/ Chena 1",33.381,16.690000000000001,16.696999999999999,8.3480000000000008,28.908999999999999,14.454000000000001,29.545999999999999,14.773,33.381,16.690999999999999,16.690999999999999]
[null,null,null,"Pajaritos 110 kV - H2 Línea 110 kV Pajaritos - Cerro Navia (Enel)/Chena 2",33.381,16.690000000000001,16.696999999999999,8.3480000000000008,28.908999999999999,14.454000000000001,29.545999999999999,14.773,33.381,16.690999999999999,16.690999999999999]
[null,null,null,"Pajaritos 110 kV - HT1 Transformador Pajaritos 110/12.5 kV N°1",33.381,0,16.696999999999999,0,28.908999999999999,0,29.545999999999999,0,33.381,33.381,33.381]
[null,null,null,"Pajaritos 110 kV - HT2 Transformador Pajaritos 110/12.5 kV N°2",33.381,0,16.696999999999999,0,28.908999999999999,0,29.545999999999999,0,33.381,33.381,33.381]
[null,null,null,"Pajaritos 110 kV - HT3 Transformador Pajaritos 110/23.5 kV N°3",33.381,0,16.696999999999999,0,28.908999999999999,0,29.545999999999999,0,33.381,33.381,33.381]
[null,null,null,"Pajaritos 110 kV - H4 Transformador Pajaritos 110/23.5 kV N°4",33.381,0,16.696999999999999,0,28.908999999999999,0,29.545999999999999,0,33.381,33.381,33.381]
[null,"Pajonales (Infotécnica interna)",110,"Pajonales (Infotécnica interna) 110 kV -  En Barra",2.59,0,2.0099999999999998,0,2.242,0,2.5529999999999999,0,2.59,2.59,2.59]
[null,"Palafitos",110,"Palafitos 110 kV - HT1 Transformador Trafo1 25/33MVA 110/13,8 kV",2.5880000000000001,0,2.6019999999999999,0,2.2250000000000001,0,2.6070000000000002,0,2.6070000000000002,2.6070000000000002,2.6070000000000002]
[null,"Palmar",110,"Palmar 110 kV - HT1 Transformador 15MVA 110/13.2kV T1",2.7570000000000001,0.192,2.5129999999999999,0.115,2.4249999999999998,0.16500000000000001,2.766,0.17,2.766,2.5960000000000001,2.5960000000000001]
[null,null,null,"Palmar 110 kV - HT2 Transformador 15MVA 110/13.2kVT2",2.7570000000000001,0.192,2.5129999999999999,0.115,2.4249999999999998,0.16500000000000001,2.766,0.17,2.766,2.5960000000000001,2.5960000000000001]
[null,null,null,"Palmar 110 kV - H1 Línea 110kV PALMAR - COPIHUES",2.7570000000000001,2.383,2.5129999999999999,2.2890000000000001,2.4249999999999998,2.105,2.766,2.4700000000000002,2.766,0.37400000000000011,2.4700000000000002]
[null,"Pan de Azúcar",110,"Pan de Azúcar 110 kV - HT4 Transformador 150 MVA 220/110/13,2kV ATR4  ",13.045999999999999,3.2570000000000001,17.274000000000001,3.7759999999999998,11.241,2.8119999999999998,17.492000000000001,3.6880000000000002,17.492000000000001,13.804,13.804]
[null,null,null,"Pan de Azúcar 110 kV - HT1 Transformador TR01 48MVA 110/110kV",13.045999999999999,0.6,17.274000000000001,3.6179999999999999,11.241,0.51800000000000002,17.492000000000001,5.157,17.492000000000001,13.656000000000001,13.656000000000001]
[null,null,null,"Pan de Azúcar 110 kV - HT3 Transformador ATR3 75MVA 220/110/13,2kV y ATR9 90 MVA 220/110/13.2 kV",13.045999999999999,3.4980000000000002,17.274000000000001,3.8260000000000001,11.241,3.0209999999999999,17.492000000000001,3.7850000000000001,17.492000000000001,13.707000000000001,13.707000000000001]
[null,null,null,"Pan de Azúcar 110 kV - H2 Línea 110 kV Pan de Azucar - Maitencillo - Las Compañias C1",13.045999999999999,0.6,17.274000000000001,0.53100000000000003,11.241,0.51800000000000002,17.492000000000001,0.56299999999999994,17.492000000000001,16.929000000000002,16.929000000000002]
[null,null,null,"Pan de Azúcar 110 kV - HT7 Transformador TR7 35MVA 110/110kV",13.045999999999999,0,17.274000000000001,2E-3,11.241,0,17.492000000000001,3.0000000000000001E-3,17.492000000000001,17.489000000000001,17.489000000000001]
[null,null,null,"Pan de Azúcar 110 kV - H1 Línea 110 kV Pan de Azucar - Ovalle (El Peñon)",13.045999999999999,1.177,17.274000000000001,1.0820000000000001,11.241,0.999,17.492000000000001,1.1379999999999999,17.492000000000001,16.353999999999999,16.353999999999999]
[null,null,null,"Pan de Azúcar 110 kV - H6 Línea 110 kV Pan de Azucar - San Joaquin",13.045999999999999,0,17.274000000000001,0,11.241,0,17.492000000000001,0,17.492000000000001,17.492000000000001,17.492000000000001]
[null,null,null,"Pan de Azúcar 110 kV - HT2 Transformador T10 60MVA 110/66/23kV TR2 60 MVA 110/66/23 kV",13.045999999999999,0,17.274000000000001,9.0999999999999998E-2,11.241,0,17.492000000000001,0.13700000000000001,17.492000000000001,17.355,17.355]
[null,null,null,"Pan de Azúcar 110 kV - HT10 Transformador 220/110/13.2 kV N°10",13.045999999999999,3.4609999999999999,17.274000000000001,3.85,11.241,2.988,17.492000000000001,3.802,17.492000000000001,13.690000000000001,13.690000000000001]
[null,null,null,"Pan de Azúcar 110 kV - H8 Línea 110 kV Pan de Azucar - El Peñon C2",13.045999999999999,1.177,17.274000000000001,1.0820000000000001,11.241,0.999,17.492000000000001,1.1379999999999999,17.492000000000001,16.353999999999999,16.353999999999999]
[null,null,null,"Pan de Azúcar 110 kV - HT8/11 TR8 - TR11",13.045999999999999,0,17.274000000000001,0,11.241,0,17.492000000000001,0,17.492000000000001,17.492000000000001,17.492000000000001]
[null,null,null,"Pan de Azúcar 110 kV - HT11 Transformador TR11 24MVA 110/13,8kV",13.045999999999999,0,17.274000000000001,0,11.241,0,17.492000000000001,0,17.492000000000001,17.492000000000001,17.492000000000001]
[null,null,null,"Pan de Azúcar 110 kV - HT8 Transformador TR8 24MVA 110/13,8kV",13.045999999999999,0,17.274000000000001,0,11.241,0,17.492000000000001,0,17.492000000000001,17.492000000000001,17.492000000000001]
[null,"Panamericana",110,"Panamericana 110 kV - HT1 Transformador TR01 25MVA 110/13,2kV",48.642000000000003,0,39.392000000000003,0,42.125999999999998,0,45.502000000000002,0,48.642000000000003,48.642000000000003,48.642000000000003]
[null,null,null,"Panamericana 110 kV - HT2 Transformador TR02 22,4MVA 110/12,5kV",48.642000000000003,0,39.392000000000003,0,42.125999999999998,0,45.502000000000002,0,48.642000000000003,48.642000000000003,48.642000000000003]
[null,null,null,"Panamericana 110 kV - H4 Transformador TR04 22,4MVA 110/12,5kV",48.642000000000003,0,39.392000000000003,0,42.125999999999998,0,45.502000000000002,0,48.642000000000003,48.642000000000003,48.642000000000003]
[null,"Pargua",110,"Pargua 110 kV - HTX Transformador 60 MVA 230/115/13.8 kV",4.0679999999999996,1.536,4.6580000000000004,2.3929999999999998,3.4590000000000001,1.298,4.6120000000000001,2.274,4.6580000000000004,2.5319999999999996,2.5319999999999996]
[null,null,null,"Pargua 110 kV - HX1 Línea 110 kV Colaco-Pargua",4.0679999999999996,1.909,4.6580000000000004,1.716,3.4590000000000001,1.649,4.6120000000000001,1.8160000000000001,4.6580000000000004,2.9420000000000002,2.9420000000000002]
[null,null,null,"Pargua 110 kV - HX2 Línea 110kV Pargua - Ancud 110 kV",4.0679999999999996,0.63800000000000001,4.6580000000000004,0.56100000000000005,3.4590000000000001,0.52200000000000002,4.6120000000000001,0.60899999999999999,4.6580000000000004,4.0970000000000004,4.0970000000000004]
[null,"Parral",154,"Parral 154 kV - A2 Línea 154kV Parral  - Monterrico",4.7519999999999998,1.909,7.1079999999999997,1.903,4.1040000000000001,1.6479999999999999,8.23,1.909,8.23,6.3210000000000006,6.3210000000000006]
[null,null,null,"Parral 154 kV - A1 Línea 154kV Parral  - Itahue/Linares",4.7519999999999998,2.294,7.1079999999999997,2.29,4.1040000000000001,1.9830000000000001,8.23,2.294,8.23,5.9359999999999999,5.9359999999999999]
[null,null,null,"Parral 154 kV - AT1 Transformador TR1 75MVA 154/66/13,2kV",4.7519999999999998,8.6999999999999994E-2,7.1079999999999997,2.4489999999999998,4.1040000000000001,7.3999999999999996E-2,8.23,4.8209999999999997,8.23,4.665,4.8209999999999997]
[null,null,null,"Parral 154 kV - AT2 Transformador TR2 56/56/22,4MVA 154/66/13,2kV",4.7519999999999998,0.48199999999999998,7.1079999999999997,0.47899999999999998,4.1040000000000001,0.41499999999999998,8.23,0.48199999999999998,8.23,7.7480000000000002,7.7480000000000002]
[null,"Pellets",110,"Pellets 110 kV - H1 Línea 110 kV Pellets - Central Huasco C1",5.4660000000000002,2.7330000000000001,6.0609999999999999,3.03,4.7240000000000002,2.3620000000000001,6.1349999999999998,3.0670000000000002,6.1349999999999998,3.0679999999999996,3.0679999999999996]
[null,null,null,"Pellets 110 kV - H2 Línea 110 kV Pellets - Central Huasco C2",5.4660000000000002,2.7330000000000001,6.0609999999999999,3.03,4.7240000000000002,2.3620000000000001,6.1349999999999998,3.0670000000000002,6.1349999999999998,3.0679999999999996,3.0679999999999996]
[null,"Peñablanca",110,"Peñablanca 110 kV - H1 Línea 110 kV Peñablanca - San Pedro C2",11.337999999999999,5.1669999999999998,6.3680000000000003,2.8420000000000001,9.8279999999999994,4.4829999999999997,10.170999999999999,4.6440000000000001,11.337999999999999,6.1709999999999994,6.1709999999999994]
[null,null,null,"Peñablanca 110 kV - H2 Línea 110 kV Peñablanca - Miraflores C1",11.337999999999999,6.1749999999999998,6.3680000000000003,3.5289999999999999,9.8279999999999994,5.3490000000000002,10.170999999999999,5.5289999999999999,11.337999999999999,5.1629999999999994,6.1749999999999998]
[null,null,null,"Peñablanca 110 kV - HT2 Transformador TR2 25MVA110/12,5 kV ",11.337999999999999,0,6.3680000000000003,0,9.8279999999999994,0,10.170999999999999,0,11.337999999999999,11.337999999999999,11.337999999999999]
[null,"Petrodow",154,"Petrodow 154 kV - CT Transformador Petrodow 154/4.16 kV",12.978999999999999,0,13.628,0,11.202999999999999,0,13.473000000000001,0,13.628,13.628,13.628]
[null,"Pid Pid",110,"Pid Pid 110 kV - H1 Línea 110 kV Pid Pid - Gamboa",3.7759999999999998,2.351,3.95,2.706,3.101,1.994,3.9620000000000002,2.581,3.9620000000000002,1.4249999999999998,2.706]
[null,null,null,"Pid Pid 110 kV - HT1 Transformador TR1 16MVA115/69/24/13.8 kV",3.7759999999999998,0,3.95,0,3.101,0,3.9620000000000002,0,3.9620000000000002,3.9620000000000002,3.9620000000000002]
[null,null,null,"Pid Pid 110 kV - H2 Línea 110 kV Pid Pid - Chiloe/ Dalcahue ",3.7759999999999998,1.444,3.95,1.254,3.101,1.1279999999999999,3.9620000000000002,1.3819999999999999,3.9620000000000002,2.6960000000000002,2.6960000000000002]
[null,"Pirque",110,"Pirque 110 kV - HT Transformador TR1 y TR2",3.2370000000000001,0,3.4689999999999999,0,2.863,0,3.3919999999999999,0,3.4689999999999999,3.4689999999999999,3.4689999999999999]
[null,"Placilla",110,"Placilla 110 kV - HT2 Transformador TR2 30MVA 110/12kV ",13.122,0.19400000000000001,10.015000000000001,9.9000000000000005E-2,11.388,0.16600000000000001,12.305,0.16800000000000001,13.122,12.927999999999999,12.927999999999999]
[null,"Planta de Óxidos",110,"Planta de Óxidos 110 kV - HT1 Transformador ATR1 4MVA 110/33 kV N°1",1.4410000000000001,0,1.105,0,1.248,0,1.4019999999999999,0,1.4410000000000001,1.4410000000000001,1.4410000000000001]
[null,null,null,"Planta de Óxidos 110 kV - H2 Línea 110 kV Planta de Oxidos - Las Luces",1.4410000000000001,0,1.105,3.0000000000000001E-3,1.248,0,1.4019999999999999,2E-3,1.4410000000000001,1.4410000000000001,1.4410000000000001]
[null,"Planta Matta ",110,"Planta Matta  110 kV - HT TR - Cardones",4.048,0,3.1309999999999998,0,3.5019999999999998,0,3.86,0,4.048,4.048,4.048]
[null,"Plantas",110,"Plantas 110 kV - HT1 Transformador T1 16-20-24MVA 110-24/13,8kV",3.3420000000000001,0,2.4860000000000002,0,2.891,0,3.149,0,3.3420000000000001,3.3420000000000001,3.3420000000000001]
[null,"Playa Ancha",110,"Playa Ancha 110 kV - HT1 Transformador TR1 22,4MVA 110/12 kV N°1",10.728999999999999,0,7.5019999999999998,0,9.3109999999999999,0,9.9440000000000008,0,10.728999999999999,10.728999999999999,10.728999999999999]
[null,null,null,"Playa Ancha 110 kV - HT2 Transformador TR2 22,4MVA 110/12 kV N°2",10.728999999999999,0,7.5019999999999998,0,9.3109999999999999,0,9.9440000000000008,0,10.728999999999999,10.728999999999999,10.728999999999999]
[null,"Portezuelo",110,"Portezuelo 110 kV - H1 Línea 110 kV Portezuelo - Quelentaro",3.1240000000000001,2.71,2.9020000000000001,2.161,2.706,2.347,3.1930000000000001,2.5379999999999998,3.1930000000000001,0.7410000000000001,2.71]
[null,null,null,"Portezuelo 110 kV - HT2 Transformador TR2 15/18MVA 110/66/13.8 kV N°2",3.1240000000000001,0.16,2.9020000000000001,0.29599999999999999,2.706,0.13900000000000001,3.1930000000000001,0.32,3.1930000000000001,2.964,2.964]
[null,null,null,"Portezuelo 110 kV - HT1 Transformador TR1 75 MVA 110/66/13.8 kV N°1",3.1240000000000001,0.30399999999999999,2.9020000000000001,0.45,2.706,0.26300000000000001,3.1930000000000001,0.48799999999999999,3.1930000000000001,2.8200000000000003,2.8200000000000003]
[null,"Potrerillos",110,"Potrerillos 110 kV -  H3 Línea 110 kV Potrerillos - Llanta 1/ Diego de Almagro 1",3.3090000000000002,1.821,3.1379999999999999,1.7210000000000001,2.8610000000000002,1.575,3.3730000000000002,1.85,3.3730000000000002,1.5230000000000001,1.85]
[null,null,null,"Potrerillos 110 kV - H2 Línea 110 kV Potrerillos - Llanta 2/ Diego de Almagro 2",3.3090000000000002,1.488,3.1379999999999999,1.4159999999999999,2.8610000000000002,1.286,3.3730000000000002,1.5229999999999999,3.3730000000000002,1.8500000000000003,1.8500000000000003]
[null,null,null,"Potrerillos 110 kV - HT1 Transformador TR01 110/12/2.1 kV N°1",3.3090000000000002,0,3.1379999999999999,0,2.8610000000000002,0,3.3730000000000002,0,3.3730000000000002,3.3730000000000002,3.3730000000000002]
[null,null,null,"Potrerillos 110 kV - HT2 Transformador TR02 110/12/2.1 kV N°2",3.3090000000000002,0,3.1379999999999999,0,2.8610000000000002,0,3.3730000000000002,0,3.3730000000000002,3.3730000000000002,3.3730000000000002]
[null,"Pozo Almonte",110,"Pozo Almonte 110 kV - H1 Línea 110 kV Pozo Almonte - Tap Off Cerro Balcón",4.0830000000000002,0.37,4.7270000000000003,0.33400000000000002,3.4249999999999998,0.314,4.7110000000000003,0.36099999999999999,4.7270000000000003,4.3930000000000007,4.3930000000000007]
[null,null,null,"Pozo Almonte 110 kV - H2 Línea 110 kV Pozo Almonte - Cerro Colorado ",4.0830000000000002,0,4.7270000000000003,1E-3,3.4249999999999998,0,4.7110000000000003,2E-3,4.7270000000000003,4.726,4.726]
[null,null,null,"Pozo Almonte 110 kV - H3 Línea 110 kV Pozo Almonte - Cerro Colorado ",4.0830000000000002,0,4.7270000000000003,1E-3,3.4249999999999998,0,4.7110000000000003,2E-3,4.7270000000000003,4.726,4.726]
[null,null,null,"Pozo Almonte 110 kV - HT2 Transformador ATR 2 100/100/25MVA 220/115/13.8 kV",4.0830000000000002,1.734,4.7270000000000003,2.0470000000000002,3.4249999999999998,1.4510000000000001,4.7110000000000003,2.0179999999999998,4.7270000000000003,2.6930000000000005,2.6930000000000005]
[null,null,null,"Pozo Almonte 110 kV - HT1 Transformador ATR1 110/66/13.8  kV ",4.0830000000000002,0.34200000000000003,4.7270000000000003,0.34499999999999997,3.4249999999999998,0.25700000000000001,4.7110000000000003,0.374,4.7270000000000003,4.3820000000000006,4.3820000000000006]
[null,null,null,"Pozo Almonte 110 kV - HT5 Transformador ATR 5 100/100/25MVA 220/115/13.8 kV N°5",4.0830000000000002,1.6539999999999999,4.7270000000000003,2.016,3.4249999999999998,1.4179999999999999,4.7110000000000003,1.9610000000000001,4.7270000000000003,2.75,2.75]
[null,"Pudahuel",110,"Pudahuel 110 kV - HT1 Transformador TR01 22,4MVA 110/12.5 kV N°1",57.36,0,60.313000000000002,0,49.628999999999998,0,59.405000000000001,0,60.313000000000002,60.313000000000002,60.313000000000002]
[null,null,null,"Pudahuel 110 kV - HT2 Transformador TR02 22,4MVA 110/12.5 kV N°2",57.36,0,60.313000000000002,0,49.628999999999998,0,59.405000000000001,0,60.313000000000002,60.313000000000002,60.313000000000002]
[null,null,null,"Pudahuel 110 kV - HT3 Transformador TR03 20MVA 110/12.5 kV N°3",57.36,0,60.313000000000002,0,49.628999999999998,0,59.405000000000001,0,60.313000000000002,60.313000000000002,60.313000000000002]
[null,"Puente Alto (CMPC)",110,"Puente Alto (CMPC) 110 kV - A-1 Línea 110 kV Puente Alto - Pirque C1",3.1190000000000002,1.907,3.5950000000000002,1.7370000000000001,2.7650000000000001,1.6419999999999999,3.492,1.8520000000000001,3.5950000000000002,1.8580000000000001,1.907]
[null,null,null,"Puente Alto (CMPC) 110 kV - H-T3 Transformador TR3 45/60MVA 110/11.5 kV",3.1190000000000002,1.2190000000000001,3.5950000000000002,1.867,2.7650000000000001,1.129,3.492,1.671,3.5950000000000002,1.9000000000000001,1.9000000000000001]
[null,"Puente Alto (EEPA)",110,"Puente Alto (EEPA) 110 kV - H2 Línea 100 kV Puente Alto - Costanera",8.7520000000000007,0,6.49,0,7.5739999999999998,0,8.5380000000000003,0,8.7520000000000007,8.7520000000000007,8.7520000000000007]
[null,null,null,"Puente Alto (EEPA) 110 kV - H3 Línea 110 kV Puente Alto - Central Puntilla",8.7520000000000007,0.34699999999999998,6.49,0.89800000000000002,7.5739999999999998,0.33200000000000002,8.5380000000000003,0.66500000000000004,8.7520000000000007,8.4050000000000011,8.4050000000000011]
[null,null,null,"Puente Alto (EEPA) 110 kV - H1 Línea 110 kV Puente Alto - Las Vizcachas",8.7520000000000007,8.4350000000000005,6.49,5.6189999999999998,7.5739999999999998,7.2670000000000003,8.5380000000000003,7.9169999999999998,8.7520000000000007,0.87100000000000044,8.4350000000000005]
[null,"Punitaqui",110,"Punitaqui 110 kV - HT2 Transformador T2 20MVA 110/13,2kV",3.419,0,2.5670000000000002,0,2.9239999999999999,0,3.2879999999999998,0,3.419,3.419,3.419]
[null,"Punta de Cortés",154,"Punta de Cortés 154 kV - AT Acoplador",12.361000000000001,0.67,11.486000000000001,2.0699999999999998,10.769,0.59,12.138999999999999,1.91,12.361000000000001,11.691000000000001,11.691000000000001]
[null,null,null,"Punta de Cortés 154 kV - AT1 Transformador TR1 56MVA 154/69/13,8kV",12.361000000000001,0.14199999999999999,11.486000000000001,0.443,10.769,0.124,12.138999999999999,0.40400000000000003,12.361000000000001,12.219000000000001,12.219000000000001]
[null,null,null,"Punta de Cortés 154 kV - AT2 Transformador TR2 36/48/60MVA 154/69/13,8kV",12.361000000000001,0.25600000000000001,11.486000000000001,0.79200000000000004,10.769,0.224,12.138999999999999,0.72599999999999998,12.361000000000001,12.105,12.105]
[null,null,null,"Punta de Cortés 154 kV - A1 Transformador TR3 60/75MVA 154/69/14,8kV",12.361000000000001,0.26800000000000002,11.486000000000001,0.84099999999999997,10.769,0.23400000000000001,12.138999999999999,0.77300000000000002,12.361000000000001,12.093,12.093]
[null,"Punta Padrones",110,"Punta Padrones 110 kV - H1 Línea 110 kV Punta Pradones - Travesia/EB2",1.5489999999999999,1.5489999999999999,0.88300000000000001,0.88300000000000001,1.341,1.341,1.3979999999999999,1.3979999999999999,1.5489999999999999,0,1.5489999999999999]
[null,"Punta Peuco (Cemento Polpaico)",110,"Punta Peuco (Cemento Polpaico) 110 kV - HT1 Transformador TR1 15/22MVA110/44kV",13.461,0,10.763,0,11.631,0,12.545999999999999,0,13.461,13.461,13.461]
[null,null,null,"Punta Peuco (Cemento Polpaico) 110 kV - HT2 Transformador TR2 20MVA110/44kV",13.461,0,10.763,0,11.631,0,12.545999999999999,0,13.461,13.461,13.461]
[null,"Quelentaro",110,"Quelentaro 110 kV - H1 Línea 110 kV Quelentaro - Las Arañas",6.1310000000000002,0,10.048999999999999,9.4E-2,5.3079999999999998,0,15.196999999999999,0.26100000000000001,15.196999999999999,14.936,14.936]
[null,null,null,"Quelentaro 110 kV - H2 Línea 110 kV Quelentaro - Portezuelo",6.1310000000000002,0.42099999999999999,10.048999999999999,0.41,5.3079999999999998,0.36499999999999999,15.196999999999999,0.48299999999999998,15.196999999999999,14.713999999999999,14.713999999999999]
[null,null,null,"Quelentaro 110 kV - HT1 Transformador AT1 195MVA 220/110kV",6.1310000000000002,5.798,10.048999999999999,9.8320000000000007,5.3079999999999998,5.0199999999999996,15.196999999999999,15.391999999999999,15.196999999999999,0.33300000000000018,15.391999999999999]
[null,null,null,"Quelentaro 110 kV - HT5 Transformador TR5 13MVA 110/23 kV",6.1310000000000002,0,10.048999999999999,0,5.3079999999999998,0,15.196999999999999,0,15.196999999999999,15.196999999999999,15.196999999999999]
[null,"Quellon",110,"Quellon 110 kV -  H1 Línea 110 kV Quellón - Chonchi",1.617,1.222,0.96899999999999997,0.80900000000000005,1.38,1.0349999999999999,1.454,1.149,1.617,0.39500000000000002,1.222]
[null,null,null,"Quellon 110 kV - HT1 Transformador TR1 16MVA 115/13,8 kV N°1",1.617,0.222,0.96899999999999997,0.09,1.38,0.19500000000000001,1.454,0.193,1.617,1.395,1.395]
[null,null,null,"Quellon 110 kV - HT2 Transformador TR2 16MVA  115/24 kV N°2",1.617,0.20599999999999999,0.96899999999999997,8.4000000000000005E-2,1.38,0.18099999999999999,1.454,0.17899999999999999,1.617,1.411,1.411]
[null,"Quereo",110,"Quereo 110 kV -  En Barra",8.1479999999999997,0,9.0120000000000005,0,6.89,0,9.0419999999999998,0,9.0419999999999998,9.0419999999999998,9.0419999999999998]
[null,"Quilicura",110,"Quilicura 110 kV -  H1 Línea 110 kV Qulicura - San Cristobal /Cerro Navia C1",38.606000000000002,19.303000000000001,20.276,10.138,33.42,16.71,34.451999999999998,17.225999999999999,38.606000000000002,19.303000000000001,19.303000000000001]
[null,null,null,"Quilicura 110 kV -  H2 Línea 110 kV Qulicura - San Cristobal /Cerro Navia C2",38.606000000000002,19.303000000000001,20.276,10.138,33.42,16.71,34.451999999999998,17.225999999999999,38.606000000000002,19.303000000000001,19.303000000000001]
[null,null,null,"Quilicura 110 kV - HT1 Transformador TR01 50MVA 110/23kV",38.606000000000002,0,20.276,0,33.42,0,34.451999999999998,0,38.606000000000002,38.606000000000002,38.606000000000002]
[null,null,null,"Quilicura 110 kV - HT2 Transformador TR02 25MVA 110/12kV",38.606000000000002,0,20.276,0,33.42,0,34.451999999999998,0,38.606000000000002,38.606000000000002,38.606000000000002]
[null,null,null,"Quilicura 110 kV - HT3 Transformador TR03 50MVA 110/12kV",38.606000000000002,0,20.276,0,33.42,0,34.451999999999998,0,38.606000000000002,38.606000000000002,38.606000000000002]
[null,null,null,"Quilicura 110 kV - AT4 Transformador TR04 22,4MVA 110/12kV",38.606000000000002,0,20.276,0,33.42,0,34.451999999999998,0,38.606000000000002,38.606000000000002,38.606000000000002]
[null,"Quillota",110,"Quillota 110 kV - H3 Línea 110 kV Quillota - Marbella/ Illapel",12.956,0.879,15.797000000000001,0.77300000000000002,11.218999999999999,0.76,15.523,0.84699999999999998,15.797000000000001,15.024000000000001,15.024000000000001]
[null,null,null,"Quillota 110 kV - HT3 Transformador TR03 48MVA 110/110 kV N°3",26.81,0.81499999999999995,38.353999999999999,12.282999999999999,23.216000000000001,0.70099999999999996,41.247999999999998,20.956,41.247999999999998,26.070999999999998,26.070999999999998]
[null,null,null,"Quillota 110 kV - H2 Línea 110 kV Quillota - San Pedro",26.81,14.819000000000001,38.353999999999999,14.444000000000001,23.216000000000001,12.840999999999999,41.247999999999998,14.542,41.247999999999998,26.705999999999996,26.705999999999996]
[null,null,null,"Quillota 110 kV - HT1/2 Transformador ATR1 75 MVA 220/115/13.8 kV ATR2 75 MVA 220/115/13.8 kV",26.81,2.2029999999999998,38.353999999999999,2.3170000000000002,23.216000000000001,1.907,41.247999999999998,2.29,41.247999999999998,38.957999999999998,38.957999999999998]
[null,null,null,"Quillota 110 kV - HT4 Transformador ATR4 150MVA 220/115/13.8 kV N°4",26.81,4.4859999999999998,38.353999999999999,4.6689999999999996,23.216000000000001,3.883,41.247999999999998,4.6139999999999999,41.247999999999998,36.634,36.634]
[null,null,null,"Quillota 110 kV - HT5 Tranformador ATR5 150MVA  ",26.81,4.6459999999999999,38.353999999999999,4.7229999999999999,23.216000000000001,4.0220000000000002,41.247999999999998,4.6980000000000004,41.247999999999998,36.549999999999997,36.549999999999997]
[null,"Quilpue",110,"Quilpue 110 kV - HT1 Transformador TR1 25MVA 110/12 kV ",13.686,0,7.734,0,11.881,0,12.324999999999999,0,13.686,13.686,13.686]
[null,null,null,"Quilpue 110 kV - HT2 Transformador TR2 110/12 kV ",13.686,0,7.734,0,11.881,0,12.324999999999999,0,13.686,13.686,13.686]
[null,null,null,"Quilpue 110 kV - HT3 Transformador TR3 25MVA 110/12 kV",13.686,0,7.734,0,11.881,0,12.324999999999999,0,13.686,13.686,13.686]
[null,"Quinquimo",110,"Quinquimo 110 kV - HT1 Transformador 20MVA 110/23 kV",3.4,0,2.2229999999999999,0,2.9359999999999999,0,3.2080000000000002,0,3.4,3.4,3.4]
[null,null,null,"Quinquimo 110 kV -  H1 Línea 110 kV Quinquimo - Choapa",3.4,1.73,2.2229999999999999,1.1439999999999999,2.9359999999999999,1.4890000000000001,3.2080000000000002,1.6279999999999999,3.4,1.67,1.73]
[null,null,null,"Quinquimo 110 kV -  H2 Línea 110 kV Quinquimo - Casas Viejas",3.4,1.67,2.2229999999999999,1.079,2.9359999999999999,1.448,3.2080000000000002,1.58,3.4,1.73,1.73]
[null,null,null,"Quinquimo 110 kV -  H3 Línea 110 kV Quinquimo - Cabildo",3.4,0,2.2229999999999999,0,2.9359999999999999,0,3.2080000000000002,0,3.4,3.4,3.4]
[null,"Quintero (Chilquinta)",110,"Quintero (Chilquinta) 110 kV - H1 Transformador TR1 22,5MVA 110/12 kV ",32.749000000000002,0,36.445,0,28.643999999999998,0,34.932000000000002,0,36.445,36.445,36.445]
[null,null,null,"Quintero (Chilquinta) 110 kV - H2 Transformador TR2 20MVA 110/12 kV ",32.749000000000002,0,36.445,0,28.643999999999998,0,34.932000000000002,0,36.445,36.445,36.445]
[null,"Rancagua",154,"Rancagua 154 kV - A1 Línea 154kV Rancagua - Tinguiririca 2/Alto Jahuel 2",11.824999999999999,3.8069999999999999,10.904,3.117,10.29,3.3159999999999998,11.651,3.5310000000000001,11.824999999999999,8.1199999999999992,8.1199999999999992]
[null,null,null,"Rancagua 154 kV - A2 Línea 154kV Rancagua - Tinguiririca 1/Alto Jahuel 1",11.824999999999999,3.7919999999999998,10.904,3.1040000000000001,10.29,3.302,11.651,3.5169999999999999,11.824999999999999,8.1340000000000003,8.1340000000000003]
[null,null,null,"Rancagua 154 kV - A3 Línea 154kV Rancagua - Sauzal/Minera del Valle Central",11.824999999999999,3.3650000000000002,10.904,2.7610000000000001,10.29,2.9180000000000001,11.651,3.54,11.824999999999999,8.4599999999999991,8.4599999999999991]
[null,null,null,"Rancagua 154 kV - AT2/3 Transformador TR02 25MVA 154/66kV",11.824999999999999,0,10.904,0.38700000000000001,10.29,0,11.651,0.35599999999999998,11.824999999999999,11.824999999999999,11.824999999999999]
[null,null,null,"Rancagua 154 kV - AT4 Transformador TR04 45/60/75MVA 154/69/14,8kV",11.824999999999999,0.46700000000000003,10.904,0.82299999999999995,10.29,0.40899999999999997,11.651,0.63800000000000001,11.824999999999999,11.357999999999999,11.357999999999999]
[null,null,null,"Rancagua 154 kV - AT2 Transformador TR01 35/45/56MVA 154/69/13,8kV",11.824999999999999,0.39800000000000002,10.904,0.754,10.29,0.34799999999999998,11.651,0.57699999999999996,11.824999999999999,11.427,11.427]
[null,"Recoleta",110,"Recoleta 110 kV - H1 Línea 110 kV Recoleta - San Cristobal/Cerro Navia C1",31.035,15.518000000000001,15.231,7.6150000000000002,26.875,13.436999999999999,27.48,13.74,31.035,15.516999999999999,15.518000000000001]
[null,null,null,"Recoleta 110 kV - H2 Línea 110 kV Recoleta - San Cristobal/Cerro Navia C2",31.035,15.518000000000001,15.231,7.6150000000000002,26.875,13.436999999999999,27.48,13.74,31.035,15.516999999999999,15.518000000000001]
[null,null,null,"Recoleta 110 kV - HT3 Transformador TR03 110/12,5kV",31.035,0,15.231,0,26.875,0,27.48,0,31.035,31.035,31.035]
[null,null,null,"Recoleta 110 kV - HT1 Transformador TR01 25MVA 110/13.2 kV",31.035,0,15.231,0,26.875,0,27.48,0,31.035,31.035,31.035]
[null,"Renca",110,"Renca 110 kV - H4 Línea 110 kV Renca - Brasil C2",51.707000000000001,0,48.497999999999998,0,44.664000000000001,0,50.991999999999997,0,51.707000000000001,51.707000000000001,51.707000000000001]
[null,null,null,"Renca 110 kV - H3 Línea 110 kV Renca - Brasil C1",51.707000000000001,0,48.497999999999998,0,44.664000000000001,0,50.991999999999997,0,51.707000000000001,51.707000000000001,51.707000000000001]
[null,null,null,"Renca 110 kV - H1 Línea 110 kV Renca - Cerro Navia C1",51.707000000000001,14.099,48.497999999999998,10.351000000000001,44.664000000000001,12.237,50.991999999999997,12.61,51.707000000000001,38.381999999999998,38.381999999999998]
[null,null,null,"Renca 110 kV - H2 Línea 110 kV Renca - Cerro Navia C2",51.707000000000001,14.099,48.497999999999998,10.351000000000001,44.664000000000001,12.237,50.991999999999997,12.61,51.707000000000001,38.381999999999998,38.381999999999998]
[null,null,null,"Renca 110 kV - H5 Línea 110 kV Renca - Metro C1",51.707000000000001,12.763,48.497999999999998,9.6449999999999996,44.664000000000001,11.074999999999999,50.991999999999997,11.746,51.707000000000001,39.245999999999995,39.245999999999995]
[null,null,null,"Renca 110 kV - H7 Enlace unidad a Gas central nueva renca - Renca",51.707000000000001,4.117,48.497999999999998,5.673,44.664000000000001,3.4510000000000001,50.991999999999997,5.1029999999999998,51.707000000000001,47.59,47.59]
[null,null,null,"Renca 110 kV - H8 Enlace unidad a Vapor central nueva renca - Renca",51.707000000000001,3.8090000000000002,48.497999999999998,5.718,44.664000000000001,3.1920000000000002,50.991999999999997,5.0519999999999996,51.707000000000001,47.898000000000003,47.898000000000003]
[null,"Reñaca",110,"Reñaca 110 kV - HT1 Transformador TR1 22,4MVA 110/12 kV N°1",12.247,0,8.3960000000000008,0,10.651,0,11.472,0,12.247,12.247,12.247]
[null,null,null,"Reñaca 110 kV - HT2 Transformador TR2 30MVA 110/12 kV N°2",12.247,0,8.3960000000000008,0,10.651,0,11.472,0,12.247,12.247,12.247]
[null,"Río Bonito",110,"Río Bonito 110 kV - HT1 Transformador T1 40MVA 110/66/23 kV",1.9870000000000001,5.5E-2,2.036,0.51,1.7909999999999999,0.125,2.1259999999999999,0.39200000000000002,2.1259999999999999,1.9320000000000002,1.9320000000000002]
[null,"Río Toltén",110,"Río Toltén 110 kV - H1 Línea 110 kV Rio Toltén - Cunco/Melipeuco",3.06,0.313,2.9689999999999999,0.32700000000000001,2.6360000000000001,0.25900000000000001,3.0369999999999999,0.32700000000000001,3.06,2.7469999999999999,2.7469999999999999]
[null,"S/E ACONCAGUA TG [En_Revision]",110,"S/E ACONCAGUA TG [En_Revision] 110 kV -  En Barra",18.501000000000001,0,16.241,0,16.212,0,17.797000000000001,0,18.501000000000001,18.501000000000001,18.501000000000001]
[null,"S/E CENTRAL CUEL",154,"S/E CENTRAL CUEL 154 kV - AL Línea 154 kV Negrete Cuel - Tap Santa Luisa",4.242,4.242,4.0449999999999999,3.641,3.641,3.641,4.359,4.12,4.359,0.40399999999999991,4.242]
[null,"S/E CENTRAL SAUZALITO",154,"S/E CENTRAL SAUZALITO 154 kV - A1 Línea 154 kV Sauzal - Minera Valle Central / Rancagua",9.7989999999999995,5.9020000000000001,8.7959999999999994,4.3220000000000001,8.5090000000000003,5.1379999999999999,9.6660000000000004,5.8460000000000001,9.7989999999999995,4.4739999999999993,5.9020000000000001]
[null,"S/E INTERCONEXION CHACAYES",110,"S/E INTERCONEXION CHACAYES 110 kV - J1 Línea 110 kV Interconexión Chacayes - Arranque a: Sauzal 1 / Central Chacayes 1",17.018999999999998,4.9530000000000003,17.106000000000002,5.1589999999999998,14.8,4.3029999999999999,17.239999999999998,5.0880000000000001,17.239999999999998,12.151999999999997,12.151999999999997]
[null,null,null,"S/E INTERCONEXION CHACAYES 110 kV - J2 Línea 110 kV Interconexión Chacayes - Arranque a: Sauzal 2 / Central Chacayes 2",17.018999999999998,4.9530000000000003,17.106000000000002,5.1589999999999998,14.8,4.3029999999999999,17.239999999999998,5.0880000000000001,17.239999999999998,12.151999999999997,12.151999999999997]
[null,null,null,"S/E INTERCONEXION CHACAYES 110 kV - JT  Transformador Interconexión Chacayes 110/110 kV",17.018999999999998,9.9060000000000006,17.106000000000002,10.318,14.8,8.6059999999999999,17.239999999999998,10.176,17.239999999999998,7.1129999999999978,10.318]
[null,null,null,"S/E INTERCONEXION CHACAYES 110 kV - HT Transformador Interconexión Chacayes 110/110 kV",17.018999999999998,7.1139999999999999,17.106000000000002,6.7880000000000003,14.8,6.194,17.239999999999998,7.0720000000000001,17.239999999999998,10.318000000000001,10.318000000000001]
[null,null,null,"S/E INTERCONEXION CHACAYES 110 kV - H1 Línea 110 kV Interconexión Chacayes - Minero 1",17.018999999999998,3.5569999999999999,17.106000000000002,3.3940000000000001,14.8,3.097,17.239999999999998,3.536,17.239999999999998,13.712000000000002,13.712000000000002]
[null,null,null,"S/E INTERCONEXION CHACAYES 110 kV - H2 Línea 110 kV Interconexión Chacayes - Minero 2",17.018999999999998,3.5569999999999999,17.106000000000002,3.3940000000000001,14.8,3.097,17.239999999999998,3.536,17.239999999999998,13.712000000000002,13.712000000000002]
[null,"S/E MALLOA NUEVA",154,"S/E MALLOA NUEVA 154 kV - AT1 Transformador TR01 60/75MVA 220-154/66/15kV",13.006,0.35,13.696999999999999,0.245,11.362,0.30499999999999999,13.525,0.313,13.696999999999999,13.452,13.452]
[null,null,null,"S/E MALLOA NUEVA 154 kV - A1 Línea 154 kV Nueva Malloa - Tap Malloa 2",13.006,6.1639999999999997,13.696999999999999,6.6109999999999998,11.362,5.3860000000000001,13.525,6.4509999999999996,13.696999999999999,7.0859999999999994,7.0859999999999994]
[null,null,null,"S/E MALLOA NUEVA 154 kV - A2 Línea 154 kV Nueva Malloa - Tap Malloa 1",13.006,6.1639999999999997,13.696999999999999,6.6109999999999998,11.362,5.3860000000000001,13.525,6.4509999999999996,13.696999999999999,7.0859999999999994,7.0859999999999994]
[null,null,null,"S/E MALLOA NUEVA 154 kV - AT2 Transformador TR02 ",13.006,0.35,13.696999999999999,0.245,11.362,0.30499999999999999,13.525,0.313,13.696999999999999,13.452,13.452]
[null,"S/E POLPAICO (ENEL DISTRIBUCIÓN)",110,"S/E POLPAICO (ENEL DISTRIBUCIÓN) 110 kV -  En Barra",13.423,0,10.715,0,11.598000000000001,0,12.51,0,13.423,13.423,13.423]
[null,"Salamanca",110,"Salamanca 110 kV - HT1 Transformador TR1 ",2.2229999999999999,0,1.516,0,1.9119999999999999,0,2.1179999999999999,0,2.2229999999999999,2.2229999999999999,2.2229999999999999]
[null,"Salamanca ",110,"Salamanca  110 kV - HT2 Transformador TR2",2.2229999999999999,0,1.516,0,1.9119999999999999,0,2.1179999999999999,0,2.2229999999999999,2.2229999999999999,2.2229999999999999]
[null,"Salar",110,"Salar 110 kV - H25 Línea 100 kV Salar - KM6 ",9.6859999999999999,3.0089999999999999,10.555,3.081,8.2669999999999995,2.5720000000000001,10.324999999999999,3.06,10.555,7.4740000000000002,7.4740000000000002]
[null,null,null,"Salar 110 kV - HT3 Transformador  ATR1 120/120/30 MVA 220/110/13,8 kV ",9.6859999999999999,2.8929999999999998,10.555,3.7650000000000001,8.2669999999999995,2.4609999999999999,10.324999999999999,3.516,10.555,6.8089999999999993,6.8089999999999993]
[null,null,null,"Salar 110 kV - H26 Línea 100 kV Salar - KM6 ",9.6859999999999999,3.0089999999999999,10.555,3.081,8.2669999999999995,2.5720000000000001,10.324999999999999,3.06,10.555,7.4740000000000002,7.4740000000000002]
[null,null,null,"Salar 110 kV - H4 Línea 100 kV Salar - Central Tamaya ",9.6859999999999999,0.78800000000000003,10.555,0.64300000000000002,8.2669999999999995,0.67400000000000004,10.324999999999999,0.72399999999999998,10.555,9.911999999999999,9.911999999999999]
[null,null,null,"Salar 110 kV - HPT1 Transformador TR1 40/32/40 MVA 100/13,8/13,8 kV ",9.6859999999999999,0,10.555,0,8.2669999999999995,0,10.324999999999999,0,10.555,10.555,10.555]
[null,null,null,"Salar 110 kV - HPT2 Transformador TR2 40/32/40 MVA 100/13,8/13,8 kV ",9.6859999999999999,0,10.555,0,8.2669999999999995,0,10.324999999999999,0,10.555,10.555,10.555]
[null,null,null,"Salar 110 kV - HAB Acoplador ",9.6859999999999999,0,10.555,0,8.2669999999999995,0,10.324999999999999,0,10.555,10.555,10.555]
[null,"San Antonio ",110,"San Antonio  110 kV -  H1 Línea 110 kV San Antonio - Alto Melipilla ",3.9980000000000002,1.6279999999999999,3.2759999999999998,1.347,3.4620000000000002,1.41,3.7320000000000002,1.5109999999999999,3.9980000000000002,2.37,2.37]
[null,null,null,"San Antonio  110 kV - HT2 Transformador TR2 25 MVA 110/12 kV  ",3.9980000000000002,0,3.2759999999999998,0,3.4620000000000002,0,3.7320000000000002,0,3.9980000000000002,3.9980000000000002,3.9980000000000002]
[null,null,null,"San Antonio  110 kV - HT3 Transformador ATR 110/66 kV",3.9980000000000002,0.75900000000000001,3.2759999999999998,0.59,3.4620000000000002,0.65700000000000003,3.7320000000000002,0.71799999999999997,3.9980000000000002,3.2390000000000003,3.2390000000000003]
[null,null,null,"San Antonio  110 kV -  H2 Línea 110 kV San Antonio - Leyda ",3.9980000000000002,1.627,3.2759999999999998,1.347,3.4620000000000002,1.409,3.7320000000000002,1.5109999999999999,3.9980000000000002,2.3710000000000004,2.3710000000000004]
[null,null,null,"San Antonio  110 kV - HT4 Transformador TR4 25 MVA 110/23 kV ",3.9980000000000002,0,3.2759999999999998,0,3.4620000000000002,0,3.7320000000000002,0,3.9980000000000002,3.9980000000000002,3.9980000000000002]
[null,null,null,"San Antonio  110 kV - HT1 Transformador TR1 30 MVA 110/12 kV  ",3.9980000000000002,0,3.2759999999999998,0,3.4620000000000002,0,3.7320000000000002,0,3.9980000000000002,3.9980000000000002,3.9980000000000002]
[null,null,null,"San Antonio  110 kV - HT5 Transformador TR5 50 MVA 110/23 kV",3.9980000000000002,0,3.2759999999999998,0,3.4620000000000002,0,3.7320000000000002,0,3.9980000000000002,3.9980000000000002,3.9980000000000002]
[null,"San Bernardo ",110,"San Bernardo  110 kV -  H1 Línea 110 kV San Bernardo - Buin/Lo Espejo 1 ",35.259,17.629000000000001,15.598000000000001,7.7990000000000004,30.553999999999998,15.276999999999999,31.068999999999999,15.535,35.259,17.63,17.63]
[null,null,null,"San Bernardo  110 kV -  H2 Línea 110 kV San Bernardo - Buin/Lo Espejo 2",35.259,17.629000000000001,15.598000000000001,7.7990000000000004,30.553999999999998,15.276999999999999,31.068999999999999,15.535,35.259,17.63,17.63]
[null,null,null,"San Bernardo  110 kV -  H3 Línea 110 kV San Bernardo - Malloco ",35.259,0,15.598000000000001,1E-3,30.553999999999998,0,31.068999999999999,1E-3,35.259,35.259,35.259]
[null,"San Cristóbal ",110,"San Cristóbal  110 kV -  H1 Línea 110 kV San Cristóbal - El Salto/Cerro Navia 1 ",26.786999999999999,13.393000000000001,12.935,6.468,23.198,11.599,23.594000000000001,11.797000000000001,26.786999999999999,13.393999999999998,13.393999999999998]
[null,null,null,"San Cristóbal  110 kV -  H2 Línea 110 kV San Cristóbal - El Salto/Cerro Navia 2",26.786999999999999,13.393000000000001,12.935,6.468,23.198,11.599,23.594000000000001,11.797000000000001,26.786999999999999,13.393999999999998,13.393999999999998]
[null,null,null,"San Cristóbal  110 kV - HT1 Transformador TR01 40 MVA 110/12 kV ",26.786999999999999,0,12.935,0,23.198,0,23.594000000000001,0,26.786999999999999,26.786999999999999,26.786999999999999]
[null,null,null,"San Cristóbal  110 kV - HT2 Transformador TR02 40 MVA 110/12 kV ",26.786999999999999,0,12.935,0,23.198,0,23.594000000000001,0,26.786999999999999,26.786999999999999,26.786999999999999]
[null,null,null,"San Cristóbal  110 kV - HT3 TR03-TR04",26.786999999999999,0,12.935,0,23.198,0,23.594000000000001,0,26.786999999999999,26.786999999999999,26.786999999999999]
[null,null,null,"San Cristóbal  110 kV - HT4 Transformador TR04 50 MVA 110/12,5 kV ",26.786999999999999,0,12.935,0,23.198,0,23.594000000000001,0,26.786999999999999,26.786999999999999,26.786999999999999]
[null,null,null,"San Cristóbal  110 kV - HT5 Transformador TR05 50 MVA 110/12 kV ",26.786999999999999,0,12.935,0,23.198,0,23.594000000000001,0,26.786999999999999,26.786999999999999,26.786999999999999]
[null,"San Felipe",110,"San Felipe 110 kV - H1 Línea 110 kV San Felipe - Tap San Felipe C1",8.6319999999999997,4.3780000000000001,4.78,2.4220000000000002,7.5540000000000003,3.8260000000000001,7.8419999999999996,3.9750000000000001,8.6319999999999997,4.2539999999999996,4.3780000000000001]
[null,null,null,"San Felipe 110 kV - H2 Línea 110 kV San Felipe - Tap San Felipe C2",8.6319999999999997,4.2539999999999996,4.78,2.359,7.5540000000000003,3.7280000000000002,7.8419999999999996,3.867,8.6319999999999997,4.3780000000000001,4.3780000000000001]
[null,"San Fernando",154,"San Fernando 154 kV - AT1 Transformador 220-154/69/14.8 kV N°1",13.481999999999999,0.33600000000000002,14.584,0.56899999999999995,11.802,0.29099999999999998,14.282,0.56000000000000005,14.584,14.015000000000001,14.015000000000001]
[null,null,null,"San Fernando 154 kV - AT2 Transformador 154/69/13.8 kV N°2",13.481999999999999,0.48799999999999999,14.584,0.86499999999999999,11.802,0.42299999999999999,14.282,0.85,14.584,13.718999999999999,13.718999999999999]
[null,null,null,"San Fernando 154 kV - AT3 Transformador 154/69/13.2 kV N°3",13.481999999999999,0.249,14.584,0.17799999999999999,11.802,0.215,14.282,0.191,14.584,14.405999999999999,14.405999999999999]
[null,"San Joaquín (Enel Distribución) ",110,"San Joaquín (Enel Distribución)  110 kV - H1 Línea 110 kV San Joaquín (Chilectra) - Ochagavía/Florida 1 ",35.47,17.734999999999999,17.143999999999998,8.5719999999999992,30.678000000000001,15.339,31.242000000000001,15.621,35.47,17.734999999999999,17.734999999999999]
[null,null,null,"San Joaquín (Enel Distribución)  110 kV - H2 Línea 110 kV San Joaquín (Chilectra) - Ochagavía/Florida 2",35.47,17.734999999999999,17.143999999999998,8.5719999999999992,30.678000000000001,15.339,31.242000000000001,15.621,35.47,17.734999999999999,17.734999999999999]
[null,"San Joaquín (Transnet)",110,"San Joaquín (Transnet) 110 kV - HT2 Transformador TR2 30/24/18 MVA 110/13,8 kV ",7.4390000000000001,0,6.2130000000000001,0,6.4260000000000002,0,7.1210000000000004,0,7.4390000000000001,7.4390000000000001,7.4390000000000001]
[null,null,null,"San Joaquín (Transnet) 110 kV - HT1 Transformador TR1 30/24/18 MVA 110/13,8 kV ",7.4390000000000001,0,6.2130000000000001,0,6.4260000000000002,0,7.1210000000000004,0,7.4390000000000001,7.4390000000000001,7.4390000000000001]
[null,"San José ",110,"San José  110 kV - H1 Línea 110 kV San José - Cerro Navia/Chena 1",35.29,17.645,18.13,9.0649999999999995,30.555,15.278,31.390999999999998,15.696,35.29,17.645,17.645]
[null,null,null,"San José  110 kV - H2 Línea 110 kV San José - Cerro Navia/Chena 2",35.29,17.645,18.13,9.0649999999999995,30.555,15.278,31.390999999999998,15.696,35.29,17.645,17.645]
[null,null,null,"San José  110 kV - HT3 Transformador TR03 22,4 MVA 110/12,5 kV ",35.29,0,18.13,0,30.555,0,31.390999999999998,0,35.29,35.29,35.29]
[null,null,null,"San José  110 kV - H4 Transformador TR04 50 MVA 110/12,5 kV ",35.29,0,18.13,0,30.555,0,31.390999999999998,0,35.29,35.29,35.29]
[null,"San Pablo ",110,"San Pablo  110 kV -  H1 Línea 110 kV San Pablo - Cerro Navia/Lo Aguirre 1",32.731999999999999,16.550999999999998,25.821999999999999,13.14,28.34,14.33,30.895,15.653,32.731999999999999,16.181000000000001,16.550999999999998]
[null,null,null,"San Pablo  110 kV -  H2 Línea 110 kV San Pablo - Cerro Navia/Lo Aguirre 2",32.731999999999999,16.181000000000001,25.821999999999999,12.682,28.34,14.01,30.895,15.242000000000001,32.731999999999999,16.550999999999998,16.550999999999998]
[null,null,null,"San Pablo  110 kV - HT1 Transformador TR01 37,5MVA 110/23,5kV",32.731999999999999,0,25.821999999999999,0,28.34,0,30.895,0,32.731999999999999,32.731999999999999,32.731999999999999]
[null,null,null,"San Pablo  110 kV - HT2 Transformador TR02 37,5MVA 110/23,5kV",32.731999999999999,0,25.821999999999999,0,28.34,0,30.895,0,32.731999999999999,32.731999999999999,32.731999999999999]
[null,"San Pedro (AES GENER)",110,"San Pedro (AES GENER) 110 kV - H6 Línea 110 kV San Pedro - TO Mayaca C1",27.536999999999999,2.718,32.048000000000002,2.4460000000000002,23.844999999999999,2.3330000000000002,30.88,2.5750000000000002,32.048000000000002,29.602,29.602]
[null,null,null,"San Pedro (AES GENER) 110 kV - H7 Línea 110 kV San Pedro - TO Mayaca C2",27.536999999999999,2.718,32.048000000000002,2.4460000000000002,23.844999999999999,2.3330000000000002,30.88,2.5750000000000002,32.048000000000002,29.602,29.602]
[null,null,null,"San Pedro (AES GENER) 110 kV - HT Transformador TR1 110/12 kV / TR2 110/12 kV",27.536999999999999,0,32.048000000000002,0,23.844999999999999,0,30.88,0,32.048000000000002,32.048000000000002,32.048000000000002]
[null,null,null,"San Pedro (AES GENER) 110 kV - H3 Línea 110 kV San Pedro - Quillota",27.536999999999999,11.004,32.048000000000002,17.439,23.844999999999999,9.5229999999999997,30.88,16.885000000000002,32.048000000000002,16.533000000000001,17.439]
[null,null,null,"San Pedro (AES GENER) 110 kV - H1 Línea 110 kV San Pedro - Ventanas /Codelco Div. Ventanas 1 ",27.536999999999999,3.2229999999999999,32.048000000000002,2.8660000000000001,23.844999999999999,2.8039999999999998,30.88,3.0979999999999999,32.048000000000002,29.182000000000002,29.182000000000002]
[null,null,null,"San Pedro (AES GENER) 110 kV - H2 Línea 110 kV San Pedro - Ventanas /Codelco Div. Ventanas 2",27.536999999999999,3.2229999999999999,32.048000000000002,2.8660000000000001,23.844999999999999,2.8039999999999998,30.88,3.0979999999999999,32.048000000000002,29.182000000000002,29.182000000000002]
[null,null,null,"San Pedro (AES GENER) 110 kV - H4 Línea 110 kV San Pedro - Miraflores 1 ",27.536999999999999,3.0329999999999999,32.048000000000002,2.5619999999999998,23.844999999999999,2.64,30.88,2.77,32.048000000000002,29.486000000000001,29.486000000000001]
[null,null,null,"San Pedro (AES GENER) 110 kV - H5 Línea 110 kV San Pedro - Miraflores 2",27.536999999999999,1.794,32.048000000000002,1.544,23.844999999999999,1.5620000000000001,30.88,1.667,32.048000000000002,30.504000000000001,30.504000000000001]
[null,null,null,"San Pedro (AES GENER) 110 kV - HR Acoplador ",27.536999999999999,0,32.048000000000002,0,23.844999999999999,0,30.88,0,32.048000000000002,32.048000000000002,32.048000000000002]
[null,"San Rafael (Chilquinta)",110,"San Rafael (Chilquinta) 110 kV - HT1 Transformador TR1 25MVA 110/12kV",8.6989999999999998,0,5.5229999999999997,0,7.7060000000000004,0,8.0719999999999992,0,8.6989999999999998,8.6989999999999998,8.6989999999999998]
[null,null,null,"San Rafael (Chilquinta) 110 kV - HT2 Transformador TR2 22,5MVA 110/12kV",8.6989999999999998,0,5.5229999999999997,0,7.7060000000000004,0,8.0719999999999992,0,8.6989999999999998,8.6989999999999998,8.6989999999999998]
[null,null,null,"San Rafael (Chilquinta) 110 kV - HT3 Transformador TR3 30MVA 110/23kV",8.6989999999999998,0,5.5229999999999997,0,7.7060000000000004,0,8.0719999999999992,0,8.6989999999999998,8.6989999999999998,8.6989999999999998]
[null,"San Vicente",154,"San Vicente 154 kV - A1 Línea 154kV San Vicente - Hualpén 2",14.94,4.2450000000000001,17.841999999999999,4.8979999999999997,12.885999999999999,3.6709999999999998,17.108000000000001,4.7930000000000001,17.841999999999999,12.943999999999999,12.943999999999999]
[null,null,null,"San Vicente 154 kV - A2 Línea 154kV San Vicente - EKA Chile /Hualpén 1",14.94,4.2450000000000001,17.841999999999999,4.9050000000000002,12.885999999999999,3.6709999999999998,17.108000000000001,4.798,17.841999999999999,12.936999999999998,12.936999999999998]
[null,null,null,"San Vicente 154 kV - A3 Línea 154kV San Vicente - Concepción 1",14.94,2.9689999999999999,17.841999999999999,3.45,12.885999999999999,2.5569999999999999,17.108000000000001,3.3050000000000002,17.841999999999999,14.391999999999999,14.391999999999999]
[null,null,null,"San Vicente 154 kV - A10 Línea 154kV San Vicente - Concepción 2",14.94,2.9689999999999999,17.841999999999999,3.45,12.885999999999999,2.5569999999999999,17.108000000000001,3.3050000000000002,17.841999999999999,14.391999999999999,14.391999999999999]
[null,null,null,"San Vicente 154 kV - A9 Línea 154kV San Vicente - Huachipato 2",14.94,0,17.841999999999999,0,12.885999999999999,0,17.108000000000001,0,17.841999999999999,17.841999999999999,17.841999999999999]
[null,null,null,"San Vicente 154 kV - ACE1 Condensador CCEE1",14.94,0,17.841999999999999,0,12.885999999999999,0,17.108000000000001,0,17.841999999999999,17.841999999999999,17.841999999999999]
[null,null,null,"San Vicente 154 kV - A6 Línea 154kV San Vicente - Huachipato 1",14.94,0,17.841999999999999,0,12.885999999999999,0,17.108000000000001,0,17.841999999999999,17.841999999999999,17.841999999999999]
[null,null,null,"San Vicente 154 kV - AT4 Transformador TR4",14.94,0,17.841999999999999,0,12.885999999999999,0,17.108000000000001,0,17.841999999999999,17.841999999999999,17.841999999999999]
[null,null,null,"San Vicente 154 kV - AT3 Transformador TR3 40/20/30MVA 154/69/13,8kV",14.94,0.223,17.841999999999999,0.16900000000000001,12.885999999999999,0.18099999999999999,17.108000000000001,0.19800000000000001,17.841999999999999,17.672999999999998,17.672999999999998]
[null,null,null,"San Vicente 154 kV - AT2 Transformador TR2 26MVA 154/13,8kV",14.94,0,17.841999999999999,0,12.885999999999999,0,17.108000000000001,0,17.841999999999999,17.841999999999999,17.841999999999999]
[null,null,null,"San Vicente 154 kV - A5 Línea 154kV San Vicente - Talcahuano",14.94,0.32400000000000001,17.841999999999999,0.997,12.885999999999999,0.28000000000000003,17.108000000000001,0.97399999999999998,17.841999999999999,16.844999999999999,16.844999999999999]
[null,"Santa Elena",110,"Santa Elena 110 kV - HT2 Transformador TR02 50MVA 110/12,5kV",29.518999999999998,0,12.602,0,25.533000000000001,0,25.881,0,29.518999999999998,29.518999999999998,29.518999999999998]
[null,null,null,"Santa Elena 110 kV - H3 Transformador TR03 50MVA 110/13,2kV",29.518999999999998,0,12.602,0,25.533000000000001,0,25.881,0,29.518999999999998,29.518999999999998,29.518999999999998]
[null,null,null,"Santa Elena 110 kV - H4 Transformador TR04 50MVA 110/12,5kV",29.518999999999998,0,12.602,0,25.533000000000001,0,25.881,0,29.518999999999998,29.518999999999998,29.518999999999998]
[null,null,null,"Santa Elena 110 kV - AT5 Transformador TR05 22,4MVA 110/12,5kV",29.518999999999998,0,12.602,0,25.533000000000001,0,25.881,0,29.518999999999998,29.518999999999998,29.518999999999998]
[null,null,null,"Santa Elena 110 kV - H1 Línea 110kV Santa Elena - Ochagavía/Florida1",29.518999999999998,14.76,12.602,6.3019999999999996,25.533000000000001,12.766999999999999,25.881,12.938000000000001,29.518999999999998,14.758999999999999,14.76]
[null,null,null,"Santa Elena 110 kV - H2 Línea 110kV Santa Elena - Ochagavía/Florida2",29.518999999999998,14.76,12.602,6.3,25.533000000000001,12.766999999999999,25.881,12.943,29.518999999999998,14.758999999999999,14.76]
[null,"Santa Fe",154,"Santa Fe 154 kV -  En Barra",4.5179999999999998,0,4.3129999999999997,0,3.8759999999999999,0,4.6379999999999999,0,4.6379999999999999,4.6379999999999999,4.6379999999999999]
[null,"Santa Marta",110,"Santa Marta 110 kV - HT2 Transformador TR02 50MVA 110/12,5kV",32.768999999999998,0,16.542000000000002,0,28.381,0,29.106999999999999,0,32.768999999999998,32.768999999999998,32.768999999999998]
[null,null,null,"Santa Marta 110 kV - HT4 Transformador TR04 37,5MVA 110/23,5kV",32.768999999999998,0,16.542000000000002,0,28.381,0,29.106999999999999,0,32.768999999999998,32.768999999999998,32.768999999999998]
[null,null,null,"Santa Marta 110 kV - H1 Línea 110kV Santa Marta - Cerro Navia/Chena1",32.768999999999998,16.384,16.542000000000002,8.2710000000000008,28.381,14.19,29.106999999999999,14.553000000000001,32.768999999999998,16.384999999999998,16.384999999999998]
[null,null,null,"Santa Marta 110 kV - H2 Línea 110kV Santa Marta - Cerro Navia/Chena2",32.768999999999998,16.384,16.542000000000002,8.2710000000000008,28.381,14.19,29.106999999999999,14.553000000000001,32.768999999999998,16.384999999999998,16.384999999999998]
[null,null,null,"Santa Marta 110 kV - HX Línea 110kV Santa Marta  - Padre Hurtado",32.768999999999998,0,16.542000000000002,0,28.381,0,29.106999999999999,0,32.768999999999998,32.768999999999998,32.768999999999998]
[null,"Santa Raquel",110,"Santa Raquel 110 kV - HT1 Transformador TR01 50MVA 110/12,5kV",22.899000000000001,0,10.894,0,19.817,0,20.338999999999999,0,22.899000000000001,22.899000000000001,22.899000000000001]
[null,null,null,"Santa Raquel 110 kV - HT2 Transformador TR02 25MVA 110/12,5kV",22.899000000000001,0,10.894,0,19.817,0,20.338999999999999,0,22.899000000000001,22.899000000000001,22.899000000000001]
[null,null,null,"Santa Raquel 110 kV - H4 Transformador TR04 22,4MVA 110/12,5kV",22.899000000000001,0,10.894,0,19.817,0,20.338999999999999,0,22.899000000000001,22.899000000000001,22.899000000000001]
[null,null,null,"Santa Raquel 110 kV - H1 Línea 110kV Santa Raquel - Buin/Florida1",22.899000000000001,11.45,10.894,5.4470000000000001,19.817,9.9079999999999995,20.338999999999999,10.169,22.899000000000001,11.449000000000002,11.45]
[null,null,null,"Santa Raquel 110 kV - H2 Línea 110kV Santa Raquel - Buin/Florida2",22.899000000000001,11.45,10.894,5.4470000000000001,19.817,9.9079999999999995,20.338999999999999,10.169,22.899000000000001,11.449000000000002,11.45]
[null,null,null,"Santa Raquel 110 kV - H5 Transformador TR05 50MVA 110/20,4kV",22.899000000000001,0,10.894,0,19.817,0,20.338999999999999,0,22.899000000000001,22.899000000000001,22.899000000000001]
[null,null,null,"Santa Raquel 110 kV - HT6 Transformador N°6 12/16/20/22,4MVA 110/12,5kV",22.899000000000001,0,10.894,0,19.817,0,20.338999999999999,0,22.899000000000001,22.899000000000001,22.899000000000001]
[null,"Santa Rosa Sur",110,"Santa Rosa Sur 110 kV - H1 Línea 110kV Santa Rosa Sur - Buin/Florida1",29.504000000000001,14.752000000000001,15.766,7.883,25.526,12.763,26.181999999999999,13.090999999999999,29.504000000000001,14.752000000000001,14.752000000000001]
[null,null,null,"Santa Rosa Sur 110 kV - H2 Línea 110kV Santa Rosa Sur - Buin/Florida2",29.504000000000001,14.752000000000001,15.766,7.883,25.526,12.763,26.181999999999999,13.090999999999999,29.504000000000001,14.752000000000001,14.752000000000001]
[null,null,null,"Santa Rosa Sur 110 kV - HT3 Transformador TR03 25MVA 110/12,5kV",29.504000000000001,0,15.766,0,25.526,0,26.181999999999999,0,29.504000000000001,29.504000000000001,29.504000000000001]
[null,null,null,"Santa Rosa Sur 110 kV - H4 Transformador TR04 22,4MVA 110/12,5kV",29.504000000000001,0,15.766,0,25.526,0,26.181999999999999,0,29.504000000000001,29.504000000000001,29.504000000000001]
[null,"Sauzal (C.Sauzal)",110,"Sauzal (C.Sauzal) 110 kV - HT4 Transformador TR4 50 MVA 154/110/13.8 kV y TR7 70 MVA 154/110/13.8 kV",18.736000000000001,4.0590000000000002,20.143999999999998,5.3019999999999996,16.161000000000001,3.5379999999999998,19.706,4.7690000000000001,20.143999999999998,14.936999999999999,14.936999999999999]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - H4 Línea 110kV Sauzal - Minero 2/Interconexión Chacayes 2",18.736000000000001,2.8759999999999999,20.143999999999998,2.84,16.161000000000001,2.54,19.706,2.8050000000000002,20.143999999999998,17.303999999999998,17.303999999999998]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - H3 Línea 110kV Sauzal - Minero 1/Interconexión Chacayes 1",18.736000000000001,2.8759999999999999,20.143999999999998,2.84,16.161000000000001,2.54,19.706,2.8050000000000002,20.143999999999998,17.303999999999998,17.303999999999998]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - H1 Línea 110kV Sauzal - Alto Jahuel 1",18.736000000000001,2.0590000000000002,20.143999999999998,1.6819999999999999,16.161000000000001,1.7889999999999999,19.706,1.915,20.143999999999998,18.462,18.462]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - H2 Línea 110kV Sauzal - Alto Jahuel 2",18.736000000000001,2.0590000000000002,20.143999999999998,1.6819999999999999,16.161000000000001,1.7889999999999999,19.706,1.915,20.143999999999998,18.462,18.462]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - H5 Línea 110kV Sauzal - Minero 3 ",18.736000000000001,2.5089999999999999,20.143999999999998,2.3940000000000001,16.161000000000001,2.1970000000000001,19.706,2.411,20.143999999999998,17.75,17.75]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - HT6 Transformador TR6 30 MVA 110/66/6 kV",18.736000000000001,0.25700000000000001,20.143999999999998,0.43,16.161000000000001,0.20300000000000001,19.706,0.40200000000000002,20.143999999999998,19.713999999999999,19.713999999999999]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - HT1 Transformador T1 29 MVA 110/13.2 kV",18.736000000000001,0.59299999999999997,20.143999999999998,0.93200000000000005,16.161000000000001,0.46700000000000003,19.706,0.874,20.143999999999998,19.212,19.212]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - HT2 Transformador T2 29 MVA 110/13.2 kV",18.736000000000001,0.59299999999999997,20.143999999999998,0.93200000000000005,16.161000000000001,0.46700000000000003,19.706,0.874,20.143999999999998,19.212,19.212]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - HT3 Transformador T3 29 MVA 110/13.2 kV",18.736000000000001,0.65600000000000003,20.143999999999998,1.036,16.161000000000001,0.51700000000000002,19.706,0.97199999999999998,20.143999999999998,19.107999999999997,19.107999999999997]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - T5 Transformador T5 10 MVA 110/13.8 kV",18.736000000000001,0.25700000000000001,20.143999999999998,0.13500000000000001,16.161000000000001,0.16300000000000001,19.706,0.19800000000000001,20.143999999999998,20.008999999999997,20.008999999999997]
[null,"Seat El Sol (El Sol)",110,"Seat El Sol (El Sol) 110 kV - 3 Transformador TR1 ",13.686,0,7.734,0,11.881,0,12.324999999999999,0,13.686,13.686,13.686]
[null,null,null,"Seat El Sol (El Sol) 110 kV - 5 Transformador TR2",13.686,0,7.734,0,11.881,0,12.324999999999999,0,13.686,13.686,13.686]
[null,null,null,"Seat El Sol (El Sol) 110 kV - 1 Línea",13.686,0,7.734,0,11.881,0,12.324999999999999,0,13.686,13.686,13.686]
[null,null,null,"Seat El Sol (El Sol) 110 kV - 2 Línea",13.686,0,7.734,0,11.881,0,12.324999999999999,0,13.686,13.686,13.686]
[null,"Sewell",110,"Sewell 110 kV - H1 Línea 100kV Sewell - Minero C1",12.436,6.218,10.518000000000001,5.2590000000000003,10.805999999999999,5.4029999999999996,11.778,5.8890000000000002,12.436,6.218,6.218]
[null,null,null,"Sewell 110 kV - H2 Línea 100kV Sewell - Minero C2",12.436,6.218,10.518000000000001,5.2590000000000003,10.805999999999999,5.4029999999999996,11.778,5.8890000000000002,12.436,6.218,6.218]
[null,null,null,"Sewell 110 kV - HR Acoplador",12.436,0,10.518000000000001,0,10.805999999999999,0,11.778,0,12.436,12.436,12.436]
[null,null,null,"Sewell 110 kV - HT1 Transformador TR1 110/34,5kV",12.436,0,10.518000000000001,0,10.805999999999999,0,11.778,0,12.436,12.436,12.436]
[null,null,null,"Sewell 110 kV - HT2 Transformador TR2 110/34,5kV",12.436,0,10.518000000000001,0,10.805999999999999,0,11.778,0,12.436,12.436,12.436]
[null,null,null,"Sewell 110 kV - HT3 Transformador TR3 110/34,5kV",12.436,0,10.518000000000001,0,10.805999999999999,0,11.778,0,12.436,12.436,12.436]
[null,"Sierra Miranda",110,"Sierra Miranda 110 kV -  En Barra",6.1029999999999998,0,6.36,0,5.2069999999999999,0,6.335,0,6.36,6.36,6.36]
[null,"Sopladores",110,"Sopladores 110 kV - HT1 Transformador TR01 25/33MVA 100/13,8kV",8.3870000000000005,0,7.7549999999999999,0,7.173,0,8.1199999999999992,0,8.3870000000000005,8.3870000000000005,8.3870000000000005]
[null,null,null,"Sopladores 110 kV - HT2 Transformador TR02 25/33MVA 100/13,8kV",8.3870000000000005,0,7.7549999999999999,0,7.173,0,8.1199999999999992,0,8.3870000000000005,8.3870000000000005,8.3870000000000005]
[null,null,null,"Sopladores 110 kV - HACOP Acoplador",8.3870000000000005,0,7.7549999999999999,0,7.173,0,8.1199999999999992,0,8.3870000000000005,8.3870000000000005,8.3870000000000005]
[null,null,null,"Sopladores 110 kV - H24 Línea 100kV Sopladores - KM6",8.3870000000000005,8.3870000000000005,7.7549999999999999,7.7549999999999999,7.173,7.173,8.1199999999999992,8.1199999999999992,8.3870000000000005,0,8.3870000000000005]
[null,"Sur",110,"Sur 110 kV - HT1 Transformador TR1 110/13,8kV",5.327,0,4.8819999999999997,0,4.5439999999999996,0,5.125,0,5.327,5.327,5.327]
[null,"Tal Tal (ELECDA)",110,"Tal Tal (ELECDA) 110 kV -  En Barra",0.98899999999999999,0,0.68100000000000005,0,0.85599999999999998,0,0.94599999999999995,0,0.98899999999999999,0.98899999999999999,0.98899999999999999]
[null,"Talcahuano ",154,"Talcahuano  154 kV - AT3 Transformador TR03 18,7MVA 154/15kV",13.984999999999999,3.4000000000000002E-2,16.806000000000001,2.7E-2,12.066000000000001,0.03,16.138999999999999,3.1E-2,16.806000000000001,16.779,16.779]
[null,null,null,"Talcahuano  154 kV - AT1 Transformador TR01 75MVA 154/69/14,8kV",13.984999999999999,0.21,16.806000000000001,0.501,12.066000000000001,0.182,16.138999999999999,0.53500000000000003,16.806000000000001,16.305,16.305]
[null,null,null,"Talcahuano  154 kV - ATX Transformador TR04 56MVA 154/69/14,8kV",13.984999999999999,0.16400000000000001,16.806000000000001,0.53,12.066000000000001,0.14199999999999999,16.138999999999999,0.58899999999999997,16.806000000000001,16.276,16.276]
[null,null,null,"Talcahuano  154 kV - A Línea 154kV Talcahuano - San Vicente",13.984999999999999,13.577,16.806000000000001,15.755000000000001,12.066000000000001,11.714,16.138999999999999,15.089,16.806000000000001,1.0510000000000002,15.755000000000001]
[null,"Tap Off Achupallas",110,"Tap Off Achupallas 110 kV -  En Barra",21.876999999999999,0,16.216000000000001,0,19.047999999999998,0,20.146000000000001,0,21.876999999999999,21.876999999999999,21.876999999999999]
[null,"Tap Off Alto Melipilla",110,"Tap Off Alto Melipilla 110 kV - H1 Línea 110kV Tap Alto Melipilla - Melipilla",5.976,8.6999999999999994E-2,6.4089999999999998,6.0999999999999999E-2,5.1749999999999998,7.4999999999999997E-2,6.2549999999999999,7.5999999999999998E-2,6.4089999999999998,6.3479999999999999,6.3479999999999999]
[null,null,null,"Tap Off Alto Melipilla 110 kV - H2 Línea 110kV Tap Alto Melipilla - Bollenar",5.976,0,6.4089999999999998,1E-3,5.1749999999999998,0,6.2549999999999999,1E-3,6.4089999999999998,6.4079999999999995,6.4079999999999995]
[null,"Tap Off Antucoya",110,"Tap Off Antucoya 110 kV - HT Línea 110kV Tap Antucoya - Antucoya",1.748,0.58899999999999997,0.88400000000000001,0.19700000000000001,1.5129999999999999,0.50900000000000001,1.591,0.51600000000000001,1.748,1.159,1.159]
[null,"Tap Off Barriles ",110,"Tap Off Barriles  110 kV - HT1 Transformador TR1 220/110/13,2kV",1.363,1.363,0.57599999999999996,0.57599999999999996,1.179,1.179,1.1919999999999999,1.1919999999999999,1.363,0,1.363]
[null,"Tap Off Cerro Balcón ",110,"Tap Off Cerro Balcón  110 kV -  En Barra",1.722,0,1.296,0,1.472,0,1.64,0,1.722,1.722,1.722]
[null,"Tap Off Chañares",110,"Tap Off Chañares 110 kV - H1 Línea 110kV Tap Chañares - Central Chañares",7.649,0,8.19,0.53900000000000003,6.593,0,8.0530000000000008,0.58599999999999997,8.19,7.6509999999999998,7.6509999999999998]
[null,"Tap Off Chiza",110,"Tap Off Chiza 110 kV -  En Barra",1.722,0,1.296,0,1.472,0,1.64,0,1.722,1.722,1.722]
[null,"Tap Off Codelco Ventanas",110,"Tap Off Codelco Ventanas 110 kV - E Línea 110 kV Ventanas 1 - Tap Codelco Ventanas",29.385999999999999,0,30.58,1.234,25.658000000000001,0,30.571999999999999,1.2629999999999999,30.58,29.385999999999999,29.385999999999999]
[null,"Tap Off Coyanco",154,"Tap Off Coyanco 154 kV -  En Barra",4.5179999999999998,0,4.3129999999999997,0,3.8759999999999999,0,4.6379999999999999,0,4.6379999999999999,4.6379999999999999,4.6379999999999999]
[null,"Tap Off Cuya",110,"Tap Off Cuya 110 kV -  En Barra",1.4530000000000001,0,1.732,0,1.2390000000000001,0,1.7769999999999999,0,1.7769999999999999,1.7769999999999999,1.7769999999999999]
[null,"Tap Off Desalant",110,"Tap Off Desalant 110 kV -  En Barra",5.641,0,4.0819999999999999,0,4.8010000000000002,0,5.1310000000000002,0,5.641,5.641,5.641]
[null,"Tap Off Dolores",110,"Tap Off Dolores 110 kV -  En Barra",1.722,0,1.296,0,1.472,0,1.64,0,1.722,1.722,1.722]
[null,"Tap Off Eden",110,"Tap Off Eden 110 kV - H1 Línea 110 kV Tap Off Eden - Central Río Huasco/Alto del Carmen",3.968,0.125,3.5779999999999998,0.246,3.4390000000000001,0.113,4.1459999999999999,0.19600000000000001,4.1459999999999999,3.9499999999999997,3.9499999999999997]
[null,"Tap Off El Negro ",110,"Tap Off El Negro  110 kV - HT1 Transformador TR1 110/23kV",4.3470000000000004,0,3.0640000000000001,0,3.7090000000000001,0,3.9550000000000001,0,4.3470000000000004,4.3470000000000004,4.3470000000000004]
[null,"Tap Off El Romeral",110,"Tap Off El Romeral 110 kV -  En Barra",3.8730000000000002,0,2.8380000000000001,0,3.351,0,3.6789999999999998,0,3.8730000000000002,3.8730000000000002,3.8730000000000002]
[null,"Tap Off Impulsión",110,"Tap Off Impulsión 110 kV - H Línea 110kV TO Impulsión - Impulsión ",3.6720000000000002,0,2.8610000000000002,0,3.1760000000000002,0,3.4180000000000001,0,3.6720000000000002,3.6720000000000002,3.6720000000000002]
[null,"Tap Off La Laja",110,"Tap Off La Laja 110 kV - H2 Línea 110 kV Tap La Laja - Central Queltehues 1",13.976000000000001,0.47699999999999998,11.095000000000001,0.46600000000000003,11.904999999999999,0.377,13.413,0.44700000000000001,13.976000000000001,13.499000000000001,13.499000000000001]
[null,null,null,"Tap Off La Laja 110 kV - H3 Línea 110 kV Tap La Laja - Central Queltehues 2",13.976000000000001,0.47099999999999997,11.095000000000001,0.45600000000000002,11.904999999999999,0.373,13.413,0.441,13.976000000000001,13.505000000000001,13.505000000000001]
[null,"La Laja (Energía coyanco)",110,"La Laja (Energía coyanco) 110 kV - BTP Transformador 110/23 kV 15 MVA ",13.976000000000001,0.23599999999999999,11.1,0.8,11.904999999999999,0.13600000000000001,13.414999999999999,0.69499999999999995,13.976000000000001,13.74,13.74]
[null,"Tap Off La Negra",110,"Tap Off La Negra 110 kV - HT1 Transformador TR1 110/23kV",4.726,0.109,3.347,4.4999999999999998E-2,4.0190000000000001,0.08,4.2889999999999997,8.4000000000000005E-2,4.726,4.617,4.617]
[null,"Tap Off Licancabur (Licancabur)",110,"Tap Off Licancabur (Licancabur) 110 kV - HT1 Transformador TR01 37,5MVA 110/3,45kV",2.0840000000000001,0,1.248,0,1.804,0,1.9259999999999999,0,2.0840000000000001,2.0840000000000001,2.0840000000000001]
[null,null,null,"Tap Off Licancabur (Licancabur) 110 kV - HT2 Transformador TR02 37,5MVA 110/3,45kV",2.0840000000000001,0,1.248,0,1.804,0,1.9259999999999999,0,2.0840000000000001,2.0840000000000001,2.0840000000000001]
[null,"Tap Off Mal Paso",110,"Tap Off Mal Paso 110 kV -  En Barra",1.56,0,2.302,0,1.337,0,2.7010000000000001,0,2.7010000000000001,2.7010000000000001,2.7010000000000001]
[null,"Tap Off Malloa",154,"Tap Off Malloa 154 kV -  En Barra",13.006,0,13.696999999999999,0,11.362,0,13.525,0,13.696999999999999,13.696999999999999,13.696999999999999]
[null,"Tap Off Mayaca",110,"Tap Off Mayaca 110 kV - HX1 Línea 110kV TO Mayaca - TO Pachacama C1",20.137,3.3010000000000002,20.068999999999999,2.7879999999999998,17.376999999999999,2.827,20.449000000000002,3.0640000000000001,20.449000000000002,17.385000000000002,17.385000000000002]
[null,null,null,"Tap Off Mayaca 110 kV - HX2 Línea 110kV TO Mayaca - TO Pachacama C2",20.137,3.3010000000000002,20.068999999999999,2.7890000000000001,17.376999999999999,2.827,20.449000000000002,3.0640000000000001,20.449000000000002,17.385000000000002,17.385000000000002]
[null,null,null,"Tap Off Mayaca 110 kV - HX3 Línea 110kV TO Mayaca - San Pedro C1",20.137,6.7679999999999998,20.068999999999999,7.2469999999999999,17.376999999999999,5.8630000000000004,20.449000000000002,7.2050000000000001,20.449000000000002,13.369,13.369]
[null,null,null,"Tap Off Mayaca 110 kV - HX4 Línea 110kV TO Mayaca - San Pedro C2",20.137,6.7679999999999998,20.068999999999999,7.2469999999999999,17.376999999999999,5.8630000000000004,20.449000000000002,7.2050000000000001,20.449000000000002,13.369,13.369]
[null,null,null,"Tap Off Mayaca 110 kV - HX5 Línea 110kV TO Mayaca - Mayaca C1",20.137,0,20.068999999999999,1E-3,17.376999999999999,0,20.449000000000002,1E-3,20.449000000000002,20.448,20.448]
[null,null,null,"Tap Off Mayaca 110 kV - HX6 Línea 110kV TO Mayaca - Mayaca C2",20.137,0,20.068999999999999,0,17.376999999999999,0,20.449000000000002,0,20.449000000000002,20.449000000000002,20.449000000000002]
[null,"Tap Off Oeste ",110,"Tap Off Oeste  110 kV - H1 Línea 110 kV Tap Off Oeste (Oeste) - Minsal ",1.861,0,1.966,1E-3,1.61,0,1.9450000000000001,1E-3,1.966,1.9650000000000001,1.9650000000000001]
[null,"Petroquímicas",154,"Petroquímicas 154 kV -  En Barra",14.507,0,16.8,0,12.516,0,16.154,0,16.8,16.8,16.8]
[null,"Tap Off Playa Ancha",110,"Tap Off Playa Ancha 110 kV -  En Barra",12.686999999999999,0,9.2420000000000009,0,11.013999999999999,0,11.784000000000001,0,12.686999999999999,12.686999999999999,12.686999999999999]
[null,"Tap Off Punta de Cortés",154,"Tap Off Punta de Cortés 154 kV - A2 Línea 154 kV Tap Punta de Cortés - Tinguiririca 1/Tap Tilcoco C1",12.353999999999999,2.6760000000000002,11.391999999999999,2.1850000000000001,10.762,2.3380000000000001,12.086,2.4969999999999999,12.353999999999999,9.677999999999999,9.677999999999999]
[null,null,null,"Tap Off Punta de Cortés 154 kV - A3 Línea 154 kV Tap Punta de Cortés - Tinguiririca 2/Tap Tilcoco C2",12.353999999999999,2.3959999999999999,11.391999999999999,1.8,10.762,2.0950000000000002,12.086,2.1829999999999998,12.353999999999999,9.9579999999999984,9.9579999999999984]
[null,"Tap Off Punta Peuco",110,"Tap Off Punta Peuco 110 kV - HT3 Línea 110kV Tap Punta Peuco - Polpaico (Enel distribución)",13.505000000000001,0,10.811,0,11.669,0,12.586,0,13.505000000000001,13.505000000000001,13.505000000000001]
[null,null,null,"Tap Off Punta Peuco 110 kV - HL Línea 110kV Tap Punta Peuco - Central Loma los Colorados",13.505000000000001,0.44800000000000001,10.811,0.69199999999999995,11.669,0.38700000000000001,12.586,0.56100000000000005,13.505000000000001,13.057,13.057]
[null,null,null,"Tap Off Punta Peuco 110 kV - HT Línea 110kV Tap Punta Peuco - Punta Peuco (Cementos Polpaico)",13.505000000000001,0,10.811,0,11.669,0,12.586,0,13.505000000000001,13.505000000000001,13.505000000000001]
[null,"Tap Off Punta Toro",110,"Tap Off Punta Toro 110 kV - L-1 Línea 110 kV Tap Punta Toro - Los Colorados ",4.4930000000000003,0,3.137,0,3.8889999999999998,0,4.218,0,4.4930000000000003,4.4930000000000003,4.4930000000000003]
[null,"Tap Off Quiñenco",154,"Tap Off Quiñenco 154 kV -  En Barra",13.542999999999999,0,16.247,0,11.866,0,15.381,0,16.247,16.247,16.247]
[null,"Central Río Melado",154,"Central Río Melado 154 kV - AT Línea 154 kV Tap Río Melado - Itahue2/Cipreses2",4.9630000000000001,0,3.55,0,4.1890000000000001,0,4.492,0,4.9630000000000001,4.9630000000000001,4.9630000000000001]
[null,"Tap Off Sairecabur (Sairecabur)",110,"Tap Off Sairecabur (Sairecabur) 110 kV - HT1 Transformador TR01 37,5MVA 110/3,45kV",2.1760000000000002,0,1.35,0,1.883,0,2.0190000000000001,0,2.1760000000000002,2.1760000000000002,2.1760000000000002]
[null,null,null,"Tap Off Sairecabur (Sairecabur) 110 kV - HT2 Transformador TR02 37,5MVA 110/3,45kV",2.1760000000000002,0,1.35,0,1.883,0,2.0190000000000001,0,2.1760000000000002,2.1760000000000002,2.1760000000000002]
[null,"Tap Off Santa Luisa",154,"Tap Off Santa Luisa 154 kV -  En Barra",4.5179999999999998,0,4.3129999999999997,0,3.8759999999999999,0,4.6379999999999999,0,4.6379999999999999,4.6379999999999999,4.6379999999999999]
[null,"Tap Off Tilcoco",154,"Tap Off Tilcoco 154 kV -  En Barra",12.231,0,10.032999999999999,0,10.667999999999999,0,11.493,0,12.231,12.231,12.231]
[null,"Tuniche",154,"Tuniche 154 kV -  En Barra",11.693,0,10.295999999999999,0,10.176,0,11.205,0,11.693,11.693,11.693]
[null,"Tap Off Uribe",110,"Tap Off Uribe 110 kV - H1 Acoplador  (Une los arranques (Uribe - Esmeralda con Antofagasta - Capricornio) ",7.0640000000000001,3.835,7.0919999999999996,3.3039999999999998,5.9550000000000001,3.286,7.2110000000000003,3.5790000000000002,7.2110000000000003,3.7879999999999998,3.835]
[null,"Tap Off Vítor",110,"Tap Off Vítor 110 kV -  En Barra",1.4530000000000001,0,1.732,0,1.2390000000000001,0,1.7769999999999999,0,1.7769999999999999,1.7769999999999999,1.7769999999999999]
[null,"Tap Off Vítor N°2 Móvil (Movil Vítor)",110,"Tap Off Vítor N°2 Móvil (Movil Vítor) 110 kV - HTT Transformador  20/25/30MVA 110/23kV",1.4530000000000001,3.1E-2,1.732,0.39800000000000002,1.2390000000000001,1.4999999999999999E-2,1.7769999999999999,0.504,1.7769999999999999,1.4220000000000002,1.4220000000000002]
[null,"Teno",154,"Teno 154 kV - AT1 Transformador TR1 154/13,2kV - 33,3 MVA",11.611000000000001,0.17399999999999999,6.9880000000000004,0.06,10.031000000000001,0.127,10.379,0.13200000000000001,11.611000000000001,11.437000000000001,11.437000000000001]
[null,null,null,"Teno 154 kV - AT2 Transformador TR2 154/13,2kV - 33,3 MVA",11.611000000000001,0.17399999999999999,6.9880000000000004,0.06,10.031000000000001,0.127,10.379,0.13200000000000001,11.611000000000001,11.437000000000001,11.437000000000001]
[null,null,null,"Teno 154 kV - AT Interruptor transformadores N°3 y N°5",11.611000000000001,0,6.9880000000000004,1E-3,10.031000000000001,0,10.379,0,11.611000000000001,11.611000000000001,11.611000000000001]
[null,null,null,"Teno 154 kV - A9 Línea 154kV Teno - Paneles MDP Teno",11.611000000000001,0,6.9880000000000004,1E-3,10.031000000000001,0,10.379,0,11.611000000000001,11.611000000000001,11.611000000000001]
[null,"Teno Empalme",154,"Teno Empalme 154 kV - A Línea 154 kV Teno Empalme - Teno",12.98,1.7090000000000001,8.2050000000000001,0.69599999999999995,11.226000000000001,1.431,11.634,1.448,12.98,11.271000000000001,11.271000000000001]
[null,"Tierra Amarilla",110,"Tierra Amarilla 110 kV - HT1 Transformador T1 10-12MVA 110/23kV",4.2119999999999997,0,3.327,0,3.6429999999999998,0,3.98,0,4.2119999999999997,4.2119999999999997,4.2119999999999997]
[null,null,null,"Tierra Amarilla 110 kV - HT2 Transformador T2 25-30MVA 110/23kV",4.2119999999999997,0,3.327,0,3.6429999999999998,0,3.98,0,4.2119999999999997,4.2119999999999997,4.2119999999999997]
[null,null,null,"Tierra Amarilla 110 kV - H3  Línea 110kV Tierra Amarilla - Atacama Kozán",4.2119999999999997,0,3.327,0,3.6429999999999998,0,3.98,0,4.2119999999999997,4.2119999999999997,4.2119999999999997]
[null,null,null,"Tierra Amarilla 110 kV - H4 Línea 110kV Tierra Amarilla - Plantas",4.2119999999999997,0,3.327,0,3.6429999999999998,0,3.98,0,4.2119999999999997,4.2119999999999997,4.2119999999999997]
[null,"Tinguiririca",154,"Tinguiririca 154 kV - A3 Línea 154kV Tinguiririca - Convento Viejo/Itahue 2",15.384,2.2109999999999999,18.934000000000001,1.9350000000000001,13.49,1.8979999999999999,18.337,2.0779999999999998,18.934000000000001,16.999000000000002,16.999000000000002]
[null,null,null,"Tinguiririca 154 kV - A4 Línea 154kV Tinguiririca - Itahue 1",15.384,2.1629999999999998,18.934000000000001,1.8620000000000001,13.49,1.8580000000000001,18.337,2.0169999999999999,18.934000000000001,17.072000000000003,17.072000000000003]
[null,null,null,"Tinguiririca 154 kV - A8 Línea 154kV Tinguiririca - San Fernando 1",15.384,0.876,18.934000000000001,1.1599999999999999,13.49,0.75700000000000001,18.337,1.224,18.934000000000001,17.774000000000001,17.774000000000001]
[null,null,null,"Tinguiririca 154 kV - A9 Línea 154kV Tinguiririca - Rancagua 1/Alto Jahuel 1",15.384,1.9730000000000001,18.934000000000001,1.7809999999999999,13.49,1.7170000000000001,18.337,1.8819999999999999,18.934000000000001,17.153000000000002,17.153000000000002]
[null,null,null,"Tinguiririca 154 kV - A10 Línea 154kV Tinguiririca - Rancagua 2/Alto Jahuel 2",15.384,1.9730000000000001,18.934000000000001,1.7809999999999999,13.49,1.7170000000000001,18.337,1.8819999999999999,18.934000000000001,17.153000000000002,17.153000000000002]
[null,null,null,"Tinguiririca 154 kV - AT1 Transformador AT1 300MVA 220/154/69kV",15.384,6.2450000000000001,18.934000000000001,10.451000000000001,13.49,5.6029999999999998,18.337,9.8049999999999997,18.934000000000001,9.1389999999999993,10.451000000000001]
[null,"Torquemada",110,"Torquemada 110 kV - H1 Línea 110kV Torquemada - Ventanas/Tap Achupallas 1",22.132999999999999,4.84,20.084,3.7589999999999999,19.355,4.2110000000000003,21.547999999999998,4.4009999999999998,22.132999999999999,17.292999999999999,17.292999999999999]
[null,null,null,"Torquemada 110 kV - H2 Línea 110kV Torquemada - Ventanas/Tap Achupallas 2",22.132999999999999,4.84,20.084,3.7589999999999999,19.355,4.2110000000000003,21.547999999999998,4.4009999999999998,22.132999999999999,17.292999999999999,17.292999999999999]
[null,null,null,"Torquemada 110 kV - H11 Línea 110kV Torquemada - Miraflores 1",22.132999999999999,3.2759999999999998,20.084,2.456,19.355,2.8380000000000001,21.547999999999998,2.964,22.132999999999999,18.856999999999999,18.856999999999999]
[null,null,null,"Torquemada 110 kV - H12 Línea 110kV Torquemada - Miraflores 2",22.132999999999999,3.2759999999999998,20.084,2.456,19.355,2.8380000000000001,21.547999999999998,2.964,22.132999999999999,18.856999999999999,18.856999999999999]
[null,null,null,"Torquemada 110 kV - HR Acoplador",22.132999999999999,0,20.084,0,19.355,0,21.547999999999998,0,22.132999999999999,22.132999999999999,22.132999999999999]
[null,null,null,"Torquemada 110 kV - H3 Línea 110kV Torquemada - Con Con 1",22.132999999999999,1.446,20.084,1.1040000000000001,19.355,1.254,21.547999999999998,1.371,22.132999999999999,20.686999999999998,20.686999999999998]
[null,null,null,"Torquemada 110 kV - H4 Línea 110kV Torquemada - Con Con 2",22.132999999999999,1.446,20.084,1.1040000000000001,19.355,1.254,21.547999999999998,1.371,22.132999999999999,20.686999999999998,20.686999999999998]
[null,null,null,"Torquemada 110 kV - H5 Línea 110kV Torquemada - Central Colmito",22.132999999999999,1.448,20.084,2.782,19.355,1.244,21.547999999999998,2.3170000000000002,22.132999999999999,20.684999999999999,20.684999999999999]
[null,null,null,"Torquemada 110 kV - H7 Línea 110kV Torquemada - Mauco 1",22.132999999999999,0.86799999999999999,20.084,1.3839999999999999,19.355,0.82499999999999996,21.547999999999998,1.135,22.132999999999999,21.265000000000001,21.265000000000001]
[null,null,null,"Torquemada 110 kV - H8 Línea 110kV Torquemada - Mauco 2",22.132999999999999,0.86799999999999999,20.084,1.3839999999999999,19.355,0.82499999999999996,21.547999999999998,1.135,22.132999999999999,21.265000000000001,21.265000000000001]
[null,"Totoralillo",110,"Totoralillo 110 kV - HT Transformador TR 33MVA 115/66kV",8.0960000000000001,0.182,5.5780000000000003,0.24099999999999999,7.3289999999999997,0.50700000000000001,7.585,0.443,8.0960000000000001,7.9139999999999997,7.9139999999999997]
[null,null,null,"Totoralillo 110 kV - H2 Línea 110kV Totoralillo - Aconcagua/Los Maquis 2",8.0960000000000001,4.7130000000000001,5.5780000000000003,3.367,7.3289999999999997,4.1260000000000003,7.585,4.3339999999999996,8.0960000000000001,3.383,4.7130000000000001]
[null,null,null,"Totoralillo 110 kV - H2A Línea 110kV Totoralillo - San Rafael/Esperanza 2",8.0960000000000001,3.2290000000000001,5.5780000000000003,1.986,7.3289999999999997,2.8130000000000002,7.585,2.9580000000000002,8.0960000000000001,4.867,4.867]
[null,"Travesía",110,"Travesía 110 kV - H3 Línea 110kV Travesía - Punta Padrones/ EB2",4.2729999999999997,0,3.0720000000000001,0,3.6949999999999998,0,3.9,0,4.2729999999999997,4.2729999999999997,4.2729999999999997]
[null,null,null,"Travesía 110 kV - H2 Transformador TR1 110/23kV",4.2729999999999997,0,3.0720000000000001,0,3.6949999999999998,0,3.9,0,4.2729999999999997,4.2729999999999997,4.2729999999999997]
[null,"Uribe",110,"Uribe 110 kV - H2 Línea 110kV Uribe - Esmeralda/Tap Uribe",5.6470000000000002,5.3840000000000003,5.8819999999999997,4.6870000000000003,4.7439999999999998,4.6399999999999997,5.9340000000000002,5.069,5.9340000000000002,1.1949999999999994,5.3840000000000003]
[null,null,null,"Uribe 110 kV - H3 Línea 110kV Uribe - Uribe Solar",5.6470000000000002,0.26400000000000001,5.8819999999999997,1.1970000000000001,4.7439999999999998,0.128,5.9340000000000002,1.353,5.9340000000000002,5.383,5.383]
[null,null,null,"Uribe 110 kV - HT1 Transformador TR1 110/23kV",5.6470000000000002,0,5.8819999999999997,0,4.7439999999999998,0,5.9340000000000002,0,5.9340000000000002,5.9340000000000002,5.9340000000000002]
[null,"Uribe Solar",110,"Uribe Solar 110 kV - H1 Línea 110kV Uribe Solar - Uribe",4.4880000000000004,4.226,5.5039999999999996,3.8740000000000001,3.7519999999999998,3.63,5.7460000000000004,4.0599999999999996,5.7460000000000004,1.6860000000000008,4.226]
[null,"Valle de los vientos",110,"Valle de los vientos 110 kV - HT1 Transformador TR01 50/65MVA 110/23kV",3.6720000000000002,0.21099999999999999,4.2439999999999998,0.53600000000000003,2.968,9.9000000000000005E-2,4.29,0.73799999999999999,4.29,3.7079999999999997,3.7079999999999997]
[null,null,null,"Valle de los vientos 110 kV - HT2 Transformador TR02 50/65MVA 110/23kV",3.6720000000000002,0.21099999999999999,4.2439999999999998,0.53600000000000003,2.968,9.9000000000000005E-2,4.29,0.73799999999999999,4.29,3.7079999999999997,3.7079999999999997]
[null,null,null,"Valle de los vientos 110 kV - HL1 Línea 110kV Valle de los vientos - Calama",3.6720000000000002,3.25,4.2439999999999998,3.1739999999999999,2.968,2.7989999999999999,4.29,3.1429999999999998,4.29,1.1470000000000002,3.25]
[null,"Vallenar",110,"Vallenar 110 kV - HT1 Transformador TR01 y TR02",3.968,0,3.5779999999999998,0,3.4390000000000001,0,4.1459999999999999,0,4.1459999999999999,4.1459999999999999,4.1459999999999999]
[null,"Valparaíso",110,"Valparaíso 110 kV - HT1 Transformador TR1 25MVA 110/12kV",12.225,0,8.7680000000000007,0,10.612,0,11.327999999999999,0,12.225,12.225,12.225]
[null,null,null,"Valparaíso 110 kV - HT2 Transformador TR2 25MVA 110/12kV",12.225,0,8.7680000000000007,0,10.612,0,11.327999999999999,0,12.225,12.225,12.225]
[null,null,null,"Valparaíso 110 kV - HT3 Transformador TR3 25MVA 110/12kV",12.225,0,8.7680000000000007,0,10.612,0,11.327999999999999,0,12.225,12.225,12.225]
[null,"Ventanas",110,"Ventanas 110 kV - HS1 Acoplador",33.371000000000002,0,39.392000000000003,0,29.193000000000001,0,37.393000000000001,0,39.392000000000003,39.392000000000003,39.392000000000003]
[null,null,null,"Ventanas 110 kV - HS2 Acoplador",33.371000000000002,0,39.392000000000003,0,29.193000000000001,0,37.393000000000001,0,39.392000000000003,39.392000000000003,39.392000000000003]
[null,null,null,"Ventanas 110 kV - HR Acoplador",33.371000000000002,0,39.392000000000003,0,29.193000000000001,0,37.393000000000001,0,39.392000000000003,39.392000000000003,39.392000000000003]
[null,null,null,"Ventanas 110 kV - H1 Línea 110kV Ventanas - San Pedro/Codelco Div. Ventanas C2",33.371000000000002,2.7829999999999999,39.392000000000003,2.855,29.193000000000001,2.415,37.393000000000001,2.8039999999999998,39.392000000000003,36.537000000000006,36.537000000000006]
[null,null,null,"Ventanas 110 kV - H2 Línea 110kV Ventanas - San Pedro/Codelco Div. Ventanas C1",33.371000000000002,2.7829999999999999,39.392000000000003,2.855,29.193000000000001,2.415,37.393000000000001,2.8039999999999998,39.392000000000003,36.537000000000006,36.537000000000006]
[null,null,null,"Ventanas 110 kV - H3 Línea 110kV Ventanas - Torquemada C1",33.371000000000002,2.9830000000000001,39.392000000000003,2.7149999999999999,29.193000000000001,2.6120000000000001,37.393000000000001,2.835,39.392000000000003,36.677000000000007,36.677000000000007]
[null,null,null,"Ventanas 110 kV - H4 Línea 110kV Ventanas - Torquemada C2",33.371000000000002,2.9830000000000001,39.392000000000003,2.7149999999999999,29.193000000000001,2.6120000000000001,37.393000000000001,2.835,39.392000000000003,36.677000000000007,36.677000000000007]
[null,null,null,"Ventanas 110 kV - H5 Línea 110kV Ventanas - Quintero (Chilquinta)",33.371000000000002,0,39.392000000000003,0,29.193000000000001,0,37.393000000000001,0,39.392000000000003,39.392000000000003,39.392000000000003]
[null,null,null,"Ventanas 110 kV - HX Línea 110kV Ventanas - El Bato",33.371000000000002,0,39.392000000000003,0,29.193000000000001,0,37.393000000000001,0,39.392000000000003,39.392000000000003,39.392000000000003]
[null,null,null,"Ventanas 110 kV - H6 Línea 110kV Ventanas - GNL Quintero",33.371000000000002,4.8739999999999997,39.392000000000003,2.9860000000000002,29.193000000000001,4.2140000000000004,37.393000000000001,3.8069999999999999,39.392000000000003,36.406000000000006,36.406000000000006]
[null,null,null,"Ventanas 110 kV - HT1 Transformador 3 devanado",33.371000000000002,8.5649999999999995,39.392000000000003,10.817,29.193000000000001,7.4329999999999998,37.393000000000001,10.183,39.392000000000003,28.575000000000003,28.575000000000003]
[null,null,null,"Ventanas 110 kV - HTP Transformador TRP 20MVA 110/4,16kV",33.371000000000002,0,39.392000000000003,0.23200000000000001,29.193000000000001,0,37.393000000000001,0.27600000000000002,39.392000000000003,39.160000000000004,39.160000000000004]
[null,null,null,"Ventanas 110 kV - HT4 Transformador T4 20MVA 110/4,16kV",33.371000000000002,0,39.392000000000003,0.23200000000000001,29.193000000000001,0,37.393000000000001,0.27600000000000002,39.392000000000003,39.160000000000004,39.160000000000004]
[null,null,null,"Ventanas 110 kV - HT Aguas abajo paño HTP y HT4",33.371000000000002,0,39.392000000000003,0.46400000000000002,29.193000000000001,0,37.393000000000001,0.55300000000000005,39.392000000000003,38.928000000000004,38.928000000000004]
[null,null,null,"Ventanas 110 kV - HT1A Transformador TR1A 22,5MVA 110/13kV",33.371000000000002,1.365,39.392000000000003,2.1179999999999999,29.193000000000001,1.155,37.393000000000001,2.0049999999999999,39.392000000000003,37.274000000000001,37.274000000000001]
[null,null,null,"Ventanas 110 kV - HT1B Transformador TR1B 22,5MVA 110/13kV",33.371000000000002,1.35,39.392000000000003,2.1059999999999999,29.193000000000001,1.143,37.393000000000001,1.9950000000000001,39.392000000000003,37.286000000000001,37.286000000000001]
[null,null,null,"Ventanas 110 kV - HT2A Transformador TR2A 22,5MVA 110/18kV",33.371000000000002,2.867,39.392000000000003,4.92,29.193000000000001,2.6230000000000002,37.393000000000001,4.5039999999999996,39.392000000000003,34.472000000000001,34.472000000000001]
[null,null,null,"Ventanas 110 kV - HT2B Transformador TR2B 22,5MVA 110/18kV",33.371000000000002,2.867,39.392000000000003,4.92,29.193000000000001,2.6230000000000002,37.393000000000001,4.5039999999999996,39.392000000000003,34.472000000000001,34.472000000000001]
[null,"Vicuña",110,"Vicuña 110 kV - HT Transformador TR1 10/13MVA",1.7569999999999999,0,1.0940000000000001,0,1.5209999999999999,0,1.6559999999999999,0,1.7569999999999999,1.7569999999999999,1.7569999999999999]
[null,null,null,"Vicuña 110 kV - H2 Línea 110kV Vicuña - El Indio",1.7569999999999999,0,1.0940000000000001,7.0000000000000001E-3,1.5209999999999999,0,1.6559999999999999,5.0000000000000001E-3,1.7569999999999999,1.7569999999999999,1.7569999999999999]
[null,"Vitacura",110,"Vitacura 110 kV - HT1 Transformador TR1 50MVA 110/12,5kV",27.123000000000001,0,15.342000000000001,0,23.489000000000001,0,24.21,0,27.123000000000001,27.123000000000001,27.123000000000001]
[null,null,null,"Vitacura 110 kV - HT2 Transformador TR2 50MVA 110/12,5kV",27.123000000000001,0,15.342000000000001,0,23.489000000000001,0,24.21,0,27.123000000000001,27.123000000000001,27.123000000000001]
[null,null,null,"Vitacura 110 kV - HT3 Transformador TR3 50MVA 110/12,5kV",27.123000000000001,0,15.342000000000001,0,23.489000000000001,0,24.21,0,27.123000000000001,27.123000000000001,27.123000000000001]
[null,null,null,"Vitacura 110 kV - H4 Transformador TR4 50MVA 110/12,5kV",27.123000000000001,0,15.342000000000001,0,23.489000000000001,0,24.21,0,27.123000000000001,27.123000000000001,27.123000000000001]
[null,null,null,"Vitacura 110 kV - HS1 Acoplador",27.123000000000001,0,15.342000000000001,0,23.489000000000001,0,24.21,0,27.123000000000001,27.123000000000001,27.123000000000001]
[null,null,null,"Vitacura 110 kV - H1 Línea 110kV Vitacura - Los Almendros/El Salto1",27.123000000000001,13.561,15.342000000000001,7.6710000000000003,23.489000000000001,11.744,24.21,12.105,27.123000000000001,13.562000000000001,13.562000000000001]
[null,null,null,"Vitacura 110 kV - H2 Línea 110kV Vitacura - Los Almendros/El Salto2",27.123000000000001,13.561,15.342000000000001,7.6710000000000003,23.489000000000001,11.744,24.21,12.105,27.123000000000001,13.562000000000001,13.562000000000001]
[null,"Yerbas Buenas",154,"Yerbas Buenas 154 kV - A1 Transformador T1 20MVA 154/13,2kV",6.5069999999999997,0,5.7409999999999997,0,5.6230000000000002,0,6.3070000000000004,0,6.5069999999999997,6.5069999999999997,6.5069999999999997]
[null,"Yungay",110,"Yungay 110 kV -  En Barra",5.2649999999999997,0,6.2270000000000003,0,4.5359999999999996,0,6.0229999999999997,0,6.2270000000000003,6.2270000000000003,6.2270000000000003]
[null,"CD Combarbalá",110,"CD Combarbalá 110 kV - HTX Transformador Combarbalá 110/13,8 kV",4.2460000000000004,2.0539999999999998,4.609,2.7130000000000001,3.58,1.679,4.84,2.5779999999999998,4.84,2.262,2.7130000000000001]

{"sheet":"Icc 2024","index":1,"n_rows":1281,"n_cols":15,"rows_kept":1281,"cut":false,"hidden":false,"merged":[[1276,1,1278,1],[1276,2,1278,2],[1279,1,1280,1],[1279,2,1280,2],[1266,1,1268,1],[1266,2,1268,2],[1269,1,1270,1],[1269,2,1270,2],[1271,1,1275,1],[1271,2,1275,2],[1254,1,1258,1],[1254,2,1258,2],[1259,1,1263,1],[1259,2,1263,2],[1264,1,1265,1],[1264,2,1265,2],[1233,1,1238,1],[1233,2,1238,2],[1239,1,1244,1],[1239,2,1244,2],[1245,1,1253,1],[1245,2,1253,2],[1219,1,1222,1],[1219,2,1222,2],[1223,1,1227,1],[1223,2,1227,2],[1228,1,1232,1],[1228,2,1232,2],[1201,1,1207,1],[1201,2,1207,2],[1211,1,1215,1],[1211,2,1215,2],[1216,1,1218,1],[1216,2,1218,2],[1178,1,1180,1],[1178,2,1180,2],[1181,2,1198,2],[1184,1,1198,1],[1199,1,1200,1],[1199,2,1200,2],[1168,1,1169,1],[1168,2,1169,2],[1170,1,1172,1],[1170,2,1172,2],[1174,1,1176,1],[1174,2,1176,2],[1148,1,1154,1],[1148,2,1154,2],[1155,1,1164,1],[1155,2,1164,2],[1165,1,1167,1],[1165,2,1167,2],[1131,1,1132,1],[1131,2,1132,2],[1139,1,1142,1],[1139,2,1142,2],[1144,1,1147,1],[1144,2,1147,2],[1113,1,1114,1],[1113,2,1114,2],[1117,1,1122,1],[1117,2,1122,2],[1125,1,1127,1],[1125,2,1127,2],[1090,1,1091,1],[1090,2,1091,2],[1101,1,1103,1],[1101,2,1103,2],[1108,1,1111,1],[1108,2,1111,2],[1072,1,1077,1],[1072,2,1077,2],[1079,1,1082,1],[1079,2,1082,2],[1085,1,1088,1],[1085,2,1088,2],[1053,1,1056,1],[1053,2,1056,2],[1057,1,1067,1],[1057,2,1067,2],[1068,1,1071,1],[1068,2,1071,2],[1034,1,1039,1],[1034,2,1039,2],[1041,1,1045,1],[1041,2,1045,2],[1046,1,1052,1],[1046,2,1052,2],[1011,1,1019,1],[1011,2,1019,2],[1020,1,1022,1],[1020,2,1022,2],[1023,1,1033,1],[1023,2,1033,2],[1001,1,1002,1],[1001,2,1002,2],[1003,1,1006,1],[1003,2,1006,2],[1007,1,1010,1],[1007,2,1010,2],[994,1,995,1],[994,2,995,2],[996,1,998,1],[996,2,998,2],[999,1,1000,1],[999,2,1000,2],[977,1,983,1],[977,2,983,2],[984,1,986,1],[984,2,986,2],[987,1,993,1],[987,2,993,2],[963,1,966,1],[963,2,966,2],[968,1,969,1],[968,2,969,2],[970,1,976,1],[970,2,976,2],[942,1,948,1],[942,2,948,2],[949,1,951,1],[949,2,951,2],[957,1,962,1],[957,2,962,2],[930,1,931,1],[930,2,931,2],[932,1,937,1],[932,2,937,2],[938,1,941,1],[938,2,941,2],[917,1,922,1],[917,2,922,2],[923,1,925,1],[923,2,925,2],[926,1,929,1],[926,2,929,2],[903,1,906,1],[903,2,906,2],[907,1,909,1],[907,2,909,2],[911,1,916,1],[911,2,916,2],[887,1,889,1],[887,2,889,2],[891,1,899,1],[891,2,899,2],[901,1,902,1],[901,2,902,2],[875,1,881,1],[875,2,881,2],[882,1,884,1],[882,2,884,2],[885,1,886,1],[885,2,886,2],[866,1,867,1],[866,2,867,2],[868,1,870,1],[868,2,870,2],[871,1,874,1],[871,2,874,2],[857,1,859,1],[857,2,859,2],[860,1,861,1],[860,2,861,2],[863,1,865,1],[863,2,865,2],[846,1,848,1],[846,2,848,2],[850,1,852,1],[850,2,852,2],[853,1,856,1],[853,2,856,2],[837,1,839,1],[837,2,839,2],[840,1,843,1],[840,2,843,2],[844,1,845,1],[844,2,845,2],[818,1,820,1],[818,2,820,2],[821,1,833,1],[821,2,833,2],[834,1,836,1],[834,2,836,2],[800,1,804,1],[800,2,804,2],[807,1,808,1],[807,2,808,2],[810,1,815,1],[810,2,815,2],[785,1,788,1],[785,2,788,2],[789,1,791,1],[789,2,791,2],[792,1,799,1],[792,2,799,2],[767,1,768,1],[767,2,768,2],[769,1,780,1],[769,2,780,2],[782,1,784,1],[782,2,784,2],[746,1,747,1],[746,2,747,2],[749,1,751,1],[749,2,751,2],[752,1,766,1],[752,2,766,2],[733,1,738,1],[733,2,738,2],[740,1,741,1],[740,2,741,2],[742,1,744,1],[742,2,744,2],[721,1,724,1],[721,2,724,2],[725,1,728,1],[725,2,728,2],[729,1,731,1],[729,2,731,2],[710,1,712,1],[710,2,712,2],[713,1,715,1],[713,2,715,2],[716,1,720,1],[716,2,720,2],[698,1,701,1],[698,2,701,2],[702,1,703,1],[702,2,703,2],[705,1,708,1],[705,2,708,2],[682,1,685,1],[682,2,685,2],[688,1,689,1],[688,2,689,2],[690,1,697,1],[690,2,697,2],[674,1,675,1],[674,2,675,2],[676,1,679,1],[676,2,679,2],[680,1,681,1],[680,2,681,2],[665,1,668,1],[665,2,668,2],[670,1,671,1],[670,2,671,2],[672,1,673,1],[672,2,673,2],[652,1,657,1],[652,2,657,2],[658,1,659,1],[658,2,659,2],[660,1,664,1],[660,2,664,2],[626,1,637,1],[626,2,637,2],[639,1,641,1],[639,2,641,2],[646,1,648,1],[646,2,648,2],[618,1,620,1],[618,2,620,2],[621,1,623,1],[621,2,623,2],[624,1,625,1],[624,2,625,2],[608,1,609,1],[608,2,609,2],[610,1,615,1],[610,2,615,2],[616,1,617,1],[616,2,617,2],[598,1,601,1],[598,2,601,2],[602,1,604,1],[602,2,604,2],[605,1,607,1],[605,2,607,2],[582,1,590,1],[582,2,590,2],[591,1,594,1],[591,2,594,2],[595,1,597,1],[595,2,597,2],[560,1,564,1],[560,2,564,2],[567,1,575,1],[567,2,575,2],[576,1,581,1],[576,2,581,2],[544,1,547,1],[544,2,547,2],[548,1,552,1],[548,2,552,2],[553,1,559,1],[553,2,559,2],[533,1,538,1],[533,2,538,2],[539,1,540,1],[539,2,540,2],[541,1,543,1],[541,2,543,2],[521,1,523,1],[521,2,523,2],[524,1,526,1],[524,2,526,2],[527,1,531,1],[527,2,531,2],[499,1,504,1],[499,2,504,2],[505,1,513,1],[505,2,513,2],[515,1,520,1],[515,2,520,2],[487,1,491,1],[487,2,491,2],[492,1,494,1],[492,2,494,2],[495,1,497,1],[495,2,497,2],[463,1,470,1],[463,2,470,2],[473,1,479,1],[473,2,479,2],[480,1,486,1],[480,2,486,2],[447,1,455,1],[447,2,455,2],[456,1,459,1],[456,2,459,2],[460,1,461,1],[460,2,461,2],[423,1,425,1],[423,2,425,2],[428,1,440,1],[428,2,440,2],[444,1,445,1],[444,2,445,2],[403,1,413,1],[403,2,413,2],[414,1,417,1],[414,2,417,2],[420,1,422,1],[420,2,422,2],[390,1,395,1],[390,2,395,2],[396,1,399,1],[396,2,399,2],[400,1,402,1],[400,2,402,2],[379,1,382,1],[379,2,382,2],[383,1,386,1],[383,2,386,2],[387,1,389,1],[387,2,389,2],[363,1,364,1],[363,2,364,2],[365,1,370,1],[365,2,370,2],[371,1,378,1],[371,2,378,2],[355,1,357,1],[355,2,357,2],[358,1,359,1],[358,2,359,2],[360,1,362,1],[360,2,362,2],[334,1,336,1],[334,2,336,2],[337,1,346,1],[337,2,346,2],[348,1,354,1],[348,2,354,2],[313,1,319,1],[313,2,319,2],[321,1,326,1],[321,2,326,2],[328,1,333,1],[328,2,333,2],[297,1,300,1],[297,2,300,2],[301,1,303,1],[301,2,303,2],[304,1,312,1],[304,2,312,2],[277,1,279,1],[277,2,279,2],[280,1,289,1],[280,2,289,2],[290,1,296,1],[290,2,296,2],[266,1,268,1],[266,2,268,2],[269,1,271,1],[269,2,271,2],[273,1,275,1],[273,2,275,2],[246,1,248,1],[246,2,248,2],[249,2,261,2],[250,1,261,1],[262,1,265,1],[262,2,265,2],[229,1,231,1],[229,2,231,2],[234,1,239,1],[234,2,239,2],[243,1,245,1],[243,2,245,2],[207,1,209,1],[207,2,209,2],[210,1,214,1],[210,2,214,2],[221,1,225,1],[221,2,225,2],[185,1,187,1],[185,2,187,2],[195,1,202,1],[195,2,202,2],[203,1,204,1],[203,2,204,2],[166,1,169,1],[166,2,169,2],[170,1,180,1],[170,2,180,2],[181,1,182,1],[181,2,182,2],[152,1,153,1],[152,2,153,2],[154,1,159,1],[154,2,159,2],[161,1,162,1],[161,2,162,2],[142,1,143,1],[142,2,143,2],[144,1,145,1],[144,2,145,2],[146,1,151,1],[146,2,151,2],[127,1,131,1],[127,2,131,2],[132,1,135,1],[132,2,135,2],[136,1,138,1],[136,2,138,2],[115,1,116,1],[115,2,116,2],[118,1,119,1],[118,2,119,2],[120,1,125,1],[120,2,125,2],[102,1,105,1],[102,2,105,2],[106,1,109,1],[106,2,109,2],[110,1,113,1],[110,2,113,2],[88,1,93,1],[88,2,93,2],[94,1,99,1],[94,2,99,2],[100,1,101,1],[100,2,101,2],[74,1,76,1],[74,2,76,2],[79,1,81,1],[79,2,81,2],[82,1,87,1],[82,2,87,2],[64,1,69,1],[64,2,69,2],[70,1,71,1],[70,2,71,2],[72,1,73,1],[72,2,73,2],[49,1,53,1],[49,2,53,2],[54,1,61,1],[54,2,61,2],[18,1,26,1],[18,2,26,2],[27,1,42,1],[27,2,42,2],[43,1,46,1],[43,2,46,2],[5,4,5,5],[5,6,5,7],[5,8,5,9],[5,10,5,11],[5,12,5,14],[7,1,17,1],[7,2,17,2],[1,1,1,12],[47,1,48,1],[47,2,48,2]]}
[]
[null,"CORRIENTES DE CORTOCIRCUITO  - AÑO 2024"]
[]
[]
[]
[null,null,null,null,"I''kss 3F[kA] - 2019",null,"I''kss 1F[kA] - 2019",null,"I''kss 2F[kA] - 2019",null,"I''kss 2FT[kA] - 2019",null,"Máximas Corrientes - [kA]"]
[null,"Identificación de la S/E","Nivel de Tensión [kV]","Identificación del paño","En barra","Contribución por paño","En barra","Contribución por paño","En barra","Contribución por paño","En barra","Contribución por paño","I''kss Concentrada",52,"I''kss \nCirculante"]
[null,10,100,"10 100 kV - H21 Línea 100kV 10 - 10A",10.173999999999999,5.2839999999999998,11.273,6.032,8.69,4.5110000000000001,10.955,5.7430000000000003,11.273,5.2409999999999997,6.032]
[null,null,null,"10 100 kV - H23 Línea 100kV 10 - K1",10.173999999999999,2.19,11.273,2.2429999999999999,8.69,1.871,10.955,2.262,11.273,9.0299999999999994,9.0299999999999994]
[null,null,null,"10 100 kV - HT1 Transformador TR01 8/10MVA 100/13,8kV",10.173999999999999,0,11.273,0,8.69,0,10.955,0,11.273,11.273,11.273]
[null,null,null,"10 100 kV - HT2 Transformador TR02 8/10MVA 100/13,8kV",10.173999999999999,0,11.273,0,8.69,0,10.955,0,11.273,11.273,11.273]
[null,null,null,"10 100 kV - HT3 Transformador TR03 8/10MVA 100/13,8kV",10.173999999999999,0,11.273,0,8.69,0,10.955,0,11.273,11.273,11.273]
[null,null,null,"10 100 kV - HT4 Transformador TR04 8/10MVA 100/13,8kV",10.173999999999999,0,11.273,0,8.69,0,10.955,0,11.273,11.273,11.273]
[null,null,null,"10 100 kV - HT5 Transformador TR05 8/10MVA 100/13,8kV",10.173999999999999,0,11.273,0,8.69,0,10.955,0,11.273,11.273,11.273]
[null,null,null,"10 100 kV - HT6 Transformador TR06 8/10MVA 100/13,8kV",10.173999999999999,0,11.273,0,8.69,0,10.955,0,11.273,11.273,11.273]
[null,null,null,"10 100 kV - HT7 Transformador TR07 8/10MVA 100/13,8kV",10.173999999999999,0,11.273,0,8.69,0,10.955,0,11.273,11.273,11.273]
[null,null,null,"10 100 kV - H10 Línea 100kV 10 - Chuquicamata",10.173999999999999,2.7090000000000001,11.273,3.0019999999999998,8.69,2.3149999999999999,10.955,2.9540000000000002,11.273,8.2710000000000008,8.2710000000000008]
[null,null,null,"10 100 kV - HAB Acoplador",10.173999999999999,0,11.273,0,8.69,0,10.955,0,11.273,11.273,11.273]
[null,"10A",100,"10A 100 kV - H11 Línea 100kV 10A - Chuquicamata",10.173999999999999,2.3260000000000001,11.273,2.8109999999999999,8.69,1.9870000000000001,10.955,2.6139999999999999,11.273,8.4619999999999997,8.4619999999999997]
[null,null,null,"10A 100 kV - HT8 Transformador TR08 15/22,4MVA 100/13,8kV",10.173999999999999,0,11.273,0,8.69,0,10.955,0,11.273,11.273,11.273]
[null,null,null,"10A 100 kV - HT9 Transformador TR09 15/22,4MVA 100/13,8kV",10.173999999999999,0,11.273,0,8.69,0,10.955,0,11.273,11.273,11.273]
[null,null,null,"10A 100 kV - HT10 Transformador TR10 15/22,4MVA 100/13,8kV",10.173999999999999,0,11.273,0,8.69,0,10.955,0,11.273,11.273,11.273]
[null,null,null,"10A 100 kV - HT11 Transformador TR11 44,8/59,73MVA 100/13,8kV",10.173999999999999,0,11.273,0,8.69,0,10.955,0,11.273,11.273,11.273]
[null,null,null,"10A 100 kV - HT12 Transformador TR12 44,8/59,73MVA 100/13,8kV",10.173999999999999,0,11.273,0,8.69,0,10.955,0,11.273,11.273,11.273]
[null,null,null,"10A 100 kV - HT13 Transformador TR13 45/56MVA 100/13,8kV",10.173999999999999,0,11.273,0,8.69,0,10.955,0,11.273,11.273,11.273]
[null,null,null,"10A 100 kV - H22 Línea 100kV 10A - KM6",10.173999999999999,2.9670000000000001,11.273,3.2290000000000001,8.69,2.5310000000000001,10.955,3.14,11.273,8.0440000000000005,8.0440000000000005]
[null,null,null,"10A 100 kV - HAB Acoplador",10.173999999999999,0,11.273,0,8.69,0,10.955,0,11.273,11.273,11.273]
[null,"A",100,"A 100 kV -  H1 Línea 100 kV A - Central Tocopilla 1",10.551,0.68200000000000005,12.407999999999999,0.59599999999999997,9.0079999999999991,0.58499999999999996,12.074,0.63100000000000001,12.407999999999999,11.811999999999999,11.811999999999999]
[null,null,null,"A 100 kV -  H2 Línea 100 kV A - Central Tocopilla 2",10.551,0.66500000000000004,12.407999999999999,0.54300000000000004,9.0079999999999991,0.57099999999999995,12.074,0.60699999999999998,12.407999999999999,11.865,11.865]
[null,null,null,"A 100 kV -  H3 Línea 100 kV A - Central Diesel Tamaya 1",10.551,0.79500000000000004,12.407999999999999,0.67,9.0079999999999991,0.67900000000000005,12.074,0.73299999999999998,12.407999999999999,11.738,11.738]
[null,null,null,"A 100 kV - H14 Línea 100 kV A - Chuquicamata 1",10.551,4.2110000000000003,12.407999999999999,4.6509999999999998,9.0079999999999991,3.5920000000000001,12.074,4.74,12.407999999999999,7.7569999999999997,7.7569999999999997]
[null,null,null,"A 100 kV - H15 Línea 100 kV A - Chuquicamata 2",10.551,4.2110000000000003,12.407999999999999,5.97,9.0079999999999991,3.5920000000000001,12.074,5.556,12.407999999999999,6.5179999999999998,6.5179999999999998]
[null,null,null,"A 100 kV - HT3 Transformador TR03 10 MVA 100/5 kV ",10.551,0,12.407999999999999,0,9.0079999999999991,0,12.074,0,12.407999999999999,12.407999999999999,12.407999999999999]
[null,null,null,"A 100 kV - HT4 Transformador TR04 10 MVA 100/5 kV ",10.551,0,12.407999999999999,0,9.0079999999999991,0,12.074,0,12.407999999999999,12.407999999999999,12.407999999999999]
[null,null,null,"A 100 kV - HT13 Transformador TR13 20 MVA 100/13,8 kV ",10.551,0,12.407999999999999,0,9.0079999999999991,0,12.074,0,12.407999999999999,12.407999999999999,12.407999999999999]
[null,null,null,"A 100 kV - HT14 Transformador TR14 20/25 MVA 100/13,8 kV ",10.551,0,12.407999999999999,0,9.0079999999999991,0,12.074,0,12.407999999999999,12.407999999999999,12.407999999999999]
[null,null,null,"A 100 kV - HT15 Transformador TR15 25/33,3 MVA 100/13,8 kV",10.551,0,12.407999999999999,0,9.0079999999999991,0,12.074,0,12.407999999999999,12.407999999999999,12.407999999999999]
[null,null,null,"A 100 kV - HT16 Transformador TR16 25/33,3 MVA 100/13,8 kV",10.551,0,12.407999999999999,0,9.0079999999999991,0,12.074,0,12.407999999999999,12.407999999999999,12.407999999999999]
[null,null,null,"A 100 kV - HT17 Transformador TR17 40/56 MVA 100/13,8 kV",10.551,0,12.407999999999999,0,9.0079999999999991,0,12.074,0,12.407999999999999,12.407999999999999,12.407999999999999]
[null,null,null,"A 100 kV - HT18 Transformador TR18 25/33,3 MVA 100/13,8 kV",10.551,0,12.407999999999999,0,9.0079999999999991,0,12.074,0,12.407999999999999,12.407999999999999,12.407999999999999]
[null,null,null,"A 100 kV - HT19 Transformador TR19 40/56 MVA 100/13,8 kV",10.551,0,12.407999999999999,0,9.0079999999999991,0,12.074,0,12.407999999999999,12.407999999999999,12.407999999999999]
[null,null,null,"A 100 kV - HC Banco de Condensadores 1",10.551,0,12.407999999999999,0,9.0079999999999991,0,12.074,0,12.407999999999999,12.407999999999999,12.407999999999999]
[null,null,null,"A 100 kV - HACOP Acoplador",10.551,0,12.407999999999999,0,9.0079999999999991,0,12.074,0,12.407999999999999,12.407999999999999,12.407999999999999]
[null,"Abanico",154,"Abanico 154 kV -  A2 Línea 154kV Trupán - Abanico",5.2809999999999997,2.6669999999999998,4.8239999999999998,2.383,3.4889999999999999,2.3340000000000001,5.766,2.5499999999999998,5.766,3.2160000000000002,3.2160000000000002]
[null,null,null,"Abanico 154 kV - AT1 Transformador Abanico N°1 y N°2",5.2809999999999997,0.81599999999999995,4.8239999999999998,0.70599999999999996,3.4889999999999999,0.40200000000000002,5.766,0.95399999999999996,5.766,4.8120000000000003,4.8120000000000003]
[null,null,null,"Abanico 154 kV - AT3 Transformador Abanico N°3",5.2809999999999997,0.79,4.8239999999999998,0.67500000000000004,3.4889999999999999,0.39400000000000002,5.766,0.91700000000000004,5.766,4.8490000000000002,4.8490000000000002]
[null,null,null,"Abanico 154 kV - AT4 Transformador Abanico N°4",5.2809999999999997,1.038,4.8239999999999998,1.075,3.4889999999999999,0.49299999999999999,5.766,1.494,5.766,4.2720000000000002,4.2720000000000002]
[null,"ACL",100,"ACL 100 kV - H1 Línea 100 kV ACL - KM6 1",5.24,5.24,4.9169999999999998,4.9169999999999998,4.5049999999999999,4.5049999999999999,5.1749999999999998,5.1749999999999998,5.24,0,5.24]
[null,null,null,"ACL 100 kV - HT1 Transformador ACL 100/13.8 kV",5.24,0,4.9169999999999998,0,4.5049999999999999,0,5.1749999999999998,0,5.24,5.24,5.24]
[null,"Aconcagua ",110,"Aconcagua  110 kV - H1 Transformador TR1 110/12 kV (Unidad 1 - Blanco)",8.6020000000000003,1.0640000000000001,10.558,3.1640000000000001,7.6289999999999996,1.018,10.295,3.0870000000000002,10.558,7.5380000000000003,7.5380000000000003]
[null,null,null,"Aconcagua  110 kV - H2 Transformador TR2 110/12 kV (Unidad 2 - Juncal)",8.6020000000000003,0.55400000000000005,10.558,0.879,7.6289999999999996,0.45,10.295,0.84699999999999998,10.558,9.6790000000000003,9.6790000000000003]
[null,null,null,"Aconcagua  110 kV - H3 Línea 110 kV Aconcagua - Los Maquis/San Rafael 1",8.6020000000000003,3.2360000000000002,10.558,2.9609999999999999,7.6289999999999996,2.8559999999999999,10.295,3.1389999999999998,10.558,7.5969999999999995,7.5969999999999995]
[null,null,null,"Aconcagua  110 kV - H4 Línea 110 kV Aconcagua - Los Maquis/Totoralillo 2",8.6020000000000003,3.2370000000000001,10.558,2.9649999999999999,7.6289999999999996,2.86,10.295,3.141,10.558,7.593,7.593]
[null,null,null,"Aconcagua  110 kV - HT Transformador TR03 110/66/12 kV ",8.6020000000000003,0.53600000000000003,10.558,0.61099999999999999,7.6289999999999996,0.47299999999999998,10.295,0.59399999999999997,10.558,9.9469999999999992,9.9469999999999992]
[null,"Agua Santa ",110,"Agua Santa  110 kV -  H7 Línea 110 kV Agua Santa - Miraflores 2",27.542999999999999,4.4459999999999997,26.768999999999998,3.4340000000000002,23.888999999999999,3.87,27.475000000000001,4.0890000000000004,27.542999999999999,23.386000000000003,23.386000000000003]
[null,null,null,"Agua Santa  110 kV -  H8 Línea 110 kV Agua Santa - Miraflores 1",27.542999999999999,4.4459999999999997,26.768999999999998,3.4340000000000002,23.888999999999999,3.87,27.475000000000001,4.0890000000000004,27.542999999999999,23.386000000000003,23.386000000000003]
[null,null,null,"Agua Santa  110 kV -  H9 Línea 110 kV Agua Santa - Tap Los Placeres 2",27.542999999999999,2.3170000000000002,26.768999999999998,2.032,23.888999999999999,2.0059999999999998,27.475000000000001,2.2010000000000001,27.542999999999999,25.274000000000001,25.274000000000001]
[null,null,null,"Agua Santa  110 kV - H10 Línea 110 kV Agua Santa - Tap Los Placeres 1",27.542999999999999,2.3170000000000002,26.768999999999998,2.032,23.888999999999999,2.0059999999999998,27.475000000000001,2.2010000000000001,27.542999999999999,25.274000000000001,25.274000000000001]
[null,null,null,"Agua Santa  110 kV - HX Línea 110 kV Agua Santa - Placilla C2 ",27.542999999999999,0.106,26.768999999999998,6.9000000000000006E-2,23.888999999999999,9.0999999999999998E-2,27.475000000000001,9.2999999999999999E-2,27.542999999999999,27.436999999999998,27.436999999999998]
[null,null,null,"Agua Santa  110 kV - H11 Línea 110 kV Agua Santa - Placilla ",27.542999999999999,8.7999999999999995E-2,26.768999999999998,5.7000000000000002E-2,23.888999999999999,7.4999999999999997E-2,27.475000000000001,7.6999999999999999E-2,27.542999999999999,27.454999999999998,27.454999999999998]
[null,null,null,"Agua Santa  110 kV - HTX Transformador TR2 300 MVA 220/110/66 kV ",27.542999999999999,6.9470000000000001,26.768999999999998,6.274,23.888999999999999,6.0149999999999997,27.475000000000001,6.59,27.542999999999999,20.885000000000002,20.885000000000002]
[null,null,null,"Agua Santa  110 kV - HT1 Transformador TR1 300 MVA 220/110/66 kV ",27.542999999999999,6.944,26.768999999999998,9.4849999999999994,23.888999999999999,6.0129999999999999,27.475000000000001,8.4440000000000008,27.542999999999999,20.599,20.599]
[null,"Aihuapi ",110,"Aihuapi  110 kV - HT3 Transformador TR3 27/40 MVA 110/66 kV ",4.2460000000000004,0,3.9780000000000002,7.0000000000000001E-3,3.73,0,4.1639999999999997,6.0000000000000001E-3,4.2460000000000004,4.2460000000000004,4.2460000000000004]
[null,"Algarrobo ",110,"Algarrobo  110 kV - H1 TR 1 110/4,6 kV 6 MVA ",3.9790000000000001,0,2.73,0,3.427,0,3.7450000000000001,0,3.9790000000000001,3.9790000000000001,3.9790000000000001]
[null,"Alonso de Córdova ",110,"Alonso de Córdova  110 kV - H1 Línea 110 kV Alonso de Córdova - Los Almendros (Apoquindo)/El Salto (Vitacura) 1",31.097999999999999,15.56,18.170999999999999,9.09,26.937000000000001,13.478,27.858000000000001,13.939,31.097999999999999,15.537999999999998,15.56]
[null,null,null,"Alonso de Córdova  110 kV - H2 Línea 110 kV Alonso de Córdova - Los Almendros (Apoquindo) /El Salto (Vitacura 2",31.097999999999999,15.538,18.170999999999999,9.0809999999999995,26.937000000000001,13.459,27.858000000000001,13.919,31.097999999999999,15.559999999999999,15.559999999999999]
[null,null,null,"Alonso de Córdova  110 kV - HT1 Transformador TR01 50 MVA 110/12,5 kV ",31.097999999999999,0,18.170999999999999,0,26.937000000000001,0,27.858000000000001,0,31.097999999999999,31.097999999999999,31.097999999999999]
[null,null,null,"Alonso de Córdova  110 kV - HT2 Transformador TR02 50 MVA 110/12,5 kV ",31.097999999999999,0,18.170999999999999,0,26.937000000000001,0,27.858000000000001,0,31.097999999999999,31.097999999999999,31.097999999999999]
[null,null,null,"Alonso de Córdova  110 kV - HT3 Transformador TR03 50 MVA 110/12,5 kV ",31.097999999999999,0,18.170999999999999,0,26.937000000000001,0,27.858000000000001,0,31.097999999999999,31.097999999999999,31.097999999999999]
[null,null,null,"Alonso de Córdova  110 kV - H4 Transformador TR04 50 MVA 110/12,5 kV ",31.097999999999999,0,18.170999999999999,0,26.937000000000001,0,27.858000000000001,0,31.097999999999999,31.097999999999999,31.097999999999999]
[null,"Alonso de Ribera",154,"Alonso de Ribera 154 kV - AT1 Transformador Alonso de Ribera TR1 75MVA 154/66/14,8kV",15.353,0.71599999999999997,20.274999999999999,0.63100000000000001,13.177,0.61499999999999999,20.562999999999999,0.66900000000000004,20.562999999999999,19.893999999999998,19.893999999999998]
[null,null,null,"Alonso de Ribera 154 kV - AT2 Transformador Alonso de Ribera TR2 75MVA 154/66/14,8kV",15.353,0.68799999999999994,20.274999999999999,0.60599999999999998,13.177,0.59099999999999997,20.562999999999999,0.64300000000000002,20.562999999999999,19.919999999999998,19.919999999999998]
[null,"Altamirano ",110,"Altamirano  110 kV -  H1 Línea 110 kV Altamirano - Cerro Navia/Renca 1 ",48.55,24.274999999999999,36.33,18.164999999999999,41.957999999999998,20.978999999999999,44.737000000000002,22.367999999999999,48.55,24.274999999999999,24.274999999999999]
[null,null,null,"Altamirano  110 kV -  H2 Línea 110 kV Altamirano - Cerro Navia/Renca 2",48.55,24.274999999999999,36.33,18.164999999999999,41.957999999999998,20.978999999999999,44.737000000000002,22.367999999999999,48.55,24.274999999999999,24.274999999999999]
[null,"Alto Bonito ",110,"Alto Bonito  110 kV - H1 Línea 110 kV Alto Bonito - Melipulli ",4.6959999999999997,2.129,4.2450000000000001,2.367,4.0469999999999997,1.8360000000000001,4.5289999999999999,2.27,4.6959999999999997,2.5669999999999997,2.5669999999999997]
[null,null,null,"Alto Bonito  110 kV -  H2 Línea 110 kV Alto Bonito - Molinos ",4.6959999999999997,2.569,4.2450000000000001,1.879,4.0469999999999997,2.2109999999999999,4.5289999999999999,2.3380000000000001,4.6959999999999997,2.3660000000000001,2.569]
[null,null,null,"Alto Bonito  110 kV - HT1 Transformador TR1 30 MVA 115/24,5 kV ",4.6959999999999997,0,4.2450000000000001,0,4.0469999999999997,0,4.5289999999999999,0,4.6959999999999997,4.6959999999999997,4.6959999999999997]
[null,"Alto del Carmen ",110,"Alto del Carmen  110 kV -  En Barra",1.8069999999999999,0,1.37,0,1.5620000000000001,0,1.786,0,1.8069999999999999,1.8069999999999999,1.8069999999999999]
[null,"Alto Hospicio ",110,"Alto Hospicio  110 kV - HT1 Transformador T1 15/12,5/10 MVA 110/13,8 kV ",3.7610000000000001,0,4.0869999999999997,0,3.21,0,3.9940000000000002,0,4.0869999999999997,4.0869999999999997,4.0869999999999997]
[null,"Alto Jahuel",154,"Alto Jahuel 154 kV - A1 Línea 154 kV Alto Jahuel - Fátima/ Rancagua 1/ Tingiuririca 1",14.958,2.8879999999999999,17.785,2.5750000000000002,12.988,2.512,17.178999999999998,2.7490000000000001,17.785,15.21,15.21]
[null,null,null,"Alto Jahuel 154 kV - A2 Línea 154 kV Alto Jahuel - Fátima/ Rancagua 2/ Tingiuririca 2",14.958,2.8879999999999999,17.785,2.5750000000000002,12.988,2.512,17.178999999999998,2.7490000000000001,17.785,15.21,15.21]
[null,null,null,"Alto Jahuel 154 kV - AT6 Transformador Alto Jahuel ATR6 220/154 kV ",14.958,9.2309999999999999,17.785,12.67,12.988,8.0069999999999997,17.178999999999998,11.833,17.785,5.7270000000000003,12.67]
[null,"Alto Jahuel ",110,"Alto Jahuel  110 kV - HT1 Transformador ATR1 30 MVA 110/66/13,8 kV ",43.825000000000003,1.046,49.956000000000003,0.94699999999999995,38.017000000000003,0.91100000000000003,48.609000000000002,1.0189999999999999,49.956000000000003,49.009,49.009]
[null,null,null,"Alto Jahuel  110 kV -  H2 Línea 110kV Codegua - Alto Jahuel C1",43.825000000000003,1.5209999999999999,49.956000000000003,1.337,38.017000000000003,1.323,48.609000000000002,1.4490000000000001,49.956000000000003,48.619,48.619]
[null,null,null,"Alto Jahuel  110 kV - HT2 Transformador ATR2 390 MVA 220/110/13,2 kV ",43.825000000000003,10.055,49.956000000000003,18.504000000000001,38.017000000000003,8.7279999999999998,48.609000000000002,17.021000000000001,49.956000000000003,33.770000000000003,33.770000000000003]
[null,null,null,"Alto Jahuel  110 kV -  H1 Línea 110kV Codegua - Alto Jahuel C2",43.825000000000003,1.5209999999999999,49.956000000000003,1.3380000000000001,38.017000000000003,1.323,48.609000000000002,1.45,49.956000000000003,48.618000000000002,48.618000000000002]
[null,null,null,"Alto Jahuel  110 kV -  H5 Línea 110 kV Alto Jahuel - Florida (Buin) 1",43.825000000000003,14.89,49.956000000000003,13.954000000000001,38.017000000000003,12.907999999999999,48.609000000000002,14.465,49.956000000000003,36.002000000000002,36.002000000000002]
[null,null,null,"Alto Jahuel  110 kV -  H6 Línea 110 kV Alto Jahuel - Florida (Buin) 2",43.825000000000003,14.89,49.956000000000003,13.954000000000001,38.017000000000003,12.907999999999999,48.609000000000002,14.465,49.956000000000003,36.002000000000002,36.002000000000002]
[null,"Alto Melipilla ",110,"Alto Melipilla  110 kV - HT1 Transformador TR1 150 MVA 220/110/13,2 kV ",10.55,4.8860000000000001,11.51,5.3579999999999997,9.1349999999999998,4.2309999999999999,11.147,5.15,11.51,6.1520000000000001,6.1520000000000001]
[null,null,null,"Alto Melipilla  110 kV - HTX Transformador TR2 150 MVA 220/110/13,2 kV ",10.55,4.8860000000000001,11.51,5.3579999999999997,9.1349999999999998,4.2309999999999999,11.147,5.15,11.51,6.1520000000000001,6.1520000000000001]
[null,null,null,"Alto Melipilla  110 kV -  H2 Línea 110 kV Alto Melipilla - San Antonio ",10.55,0.36099999999999999,11.51,0.375,9.1349999999999998,0.313,11.147,0.39600000000000002,11.51,11.135,11.135]
[null,null,null,"Alto Melipilla  110 kV -  H4 Línea 110 kV Alto Melipilla - Tap Off Alto Melipilla",10.55,4.2000000000000003E-2,11.51,0.03,9.1349999999999998,3.5999999999999997E-2,11.147,3.6999999999999998E-2,11.51,11.48,11.48]
[null,null,null,"Alto Melipilla  110 kV - HX Línea 110kV Alto Melipilla - Bajo Melipilla",10.55,4.4999999999999998E-2,11.51,3.2000000000000001E-2,9.1349999999999998,3.7999999999999999E-2,11.147,3.9E-2,11.51,11.478,11.478]
[null,null,null,"Alto Melipilla  110 kV -  H3 Línea 110 kV Alto Melipilla - Leyda",10.55,0.36099999999999999,11.51,0.374,9.1349999999999998,0.313,11.147,0.39600000000000002,11.51,11.135999999999999,11.135999999999999]
[null,"Alto Norte ",110,"Alto Norte  110 kV -  H3 Línea 110 kV Alto Norte - Nueva La Negra",7.81,6.1429999999999998,6.5279999999999996,5.2359999999999998,6.6970000000000001,5.2670000000000003,7.3479999999999999,5.8209999999999997,7.81,1.6669999999999998,6.1429999999999998]
[null,null,null,"Alto Norte  110 kV -  H4 Línea 110 kV Alto Norte - Capricornio/Tap Off El Negro ",7.81,1.667,6.5279999999999996,1.292,6.6970000000000001,1.43,7.3479999999999999,1.53,7.81,6.1429999999999998,6.1429999999999998]
[null,null,null,"Alto Norte  110 kV - HT1 Transformador TR1 110/13,8 kV ",7.81,0,6.5279999999999996,0,6.6970000000000001,0,7.3479999999999999,0,7.81,7.81,7.81]
[null,null,null,"Alto Norte  110 kV - HT2 Transformador TR2 110/13,8 kV ",7.81,0,6.5279999999999996,0,6.6970000000000001,0,7.3479999999999999,0,7.81,7.81,7.81]
[null,null,null,"Alto Norte  110 kV - HT3 Transformador TR3 110/13,8 kV ",7.81,0,6.5279999999999996,0,6.6970000000000001,0,7.3479999999999999,0,7.81,7.81,7.81]
[null,null,null,"Alto Norte  110 kV - HT4 Transformador TR4 110/13,8 kV ",7.81,0,6.5279999999999996,0,6.6970000000000001,0,7.3479999999999999,0,7.81,7.81,7.81]
[null,"Ancud ",110,"Ancud  110 kV - HT1 Transformador TR1 110/23 kV ",3.052,9.0999999999999998E-2,2.5110000000000001,4.7E-2,2.609,6.8000000000000005E-2,2.8889999999999998,7.0999999999999994E-2,3.052,2.9609999999999999,2.9609999999999999]
[null,null,null,"Ancud  110 kV - HT2 Transformador TR2 110/110 kV (Línea 110 kV Ancud - Chiloé)",3.052,0.878,2.5110000000000001,0.749,2.609,0.74099999999999999,2.8889999999999998,0.82499999999999996,3.052,2.1739999999999999,2.1739999999999999]
[null,"Andes ",110,"Andes  110 kV - H1 Línea 110 kV Andes - Los Almendros/Florida 1",30.489000000000001,15.244999999999999,21.28,10.64,26.413,13.207000000000001,27.661000000000001,13.831,30.489000000000001,15.244000000000002,15.244999999999999]
[null,null,null,"Andes  110 kV - H2 Línea 110 kV Andes - Los Almendros/Florida 2",30.489000000000001,15.244999999999999,21.28,10.64,26.413,13.207000000000001,27.661000000000001,13.831,30.489000000000001,15.244000000000002,15.244999999999999]
[null,null,null,"Andes  110 kV - HT1 Transformador TR01 50 MVA 110/12,5 kV ",30.489000000000001,0,21.28,0,26.413,0,27.661000000000001,0,30.489000000000001,30.489000000000001,30.489000000000001]
[null,null,null,"Andes  110 kV - HT4 Transformador TR04 22,4 MVA 110/12,5 kV ",30.489000000000001,0,21.28,0,26.413,0,27.661000000000001,0,30.489000000000001,30.489000000000001,30.489000000000001]
[null,"Antillanca ",110,"Antillanca  110 kV - HT1 Transformador T1 220/110/23 kV ",5.4690000000000003,3.8889999999999998,6.2160000000000002,4.399,4.806,3.36,5.9459999999999997,4.2549999999999999,6.2160000000000002,1.8170000000000002,4.399]
[null,null,null,"Antillanca  110 kV - H1 Línea 110 kV Antillanca - Central Licán/Mantilhue ",5.4690000000000003,0.83199999999999996,6.2160000000000002,0.85599999999999998,4.806,0.70499999999999996,5.9459999999999997,0.83899999999999997,6.2160000000000002,5.36,5.36]
[null,null,null,"Antillanca  110 kV - H2 Línea 110 kV Antillanca - Aihuapi ",5.4690000000000003,0.69499999999999995,6.2160000000000002,0.74099999999999999,4.806,0.627,5.9459999999999997,0.71399999999999997,6.2160000000000002,5.4750000000000005,5.4750000000000005]
[null,null,null,"Antillanca  110 kV - H3 Línea 110 kV Antillanca - Río Bonito ",5.4690000000000003,5.5E-2,6.2160000000000002,0.221,4.806,0.121,5.9459999999999997,0.151,6.2160000000000002,5.9950000000000001,5.9950000000000001]
[null,"Antofagasta ",110,"Antofagasta  110 kV - HT1 Transformador TR1 110/13,8 kV ",9.1829999999999998,0,7.9870000000000001,0,7.8159999999999998,0,8.6829999999999998,0,9.1829999999999998,9.1829999999999998,9.1829999999999998]
[null,null,null,"Antofagasta  110 kV -  H1 Línea 110 kV Antofagasta -Tap Off Uribe/Capricornio",9.1829999999999998,3.7789999999999999,7.9870000000000001,3.5920000000000001,7.8159999999999998,3.1779999999999999,8.6829999999999998,3.7480000000000002,9.1829999999999998,5.4039999999999999,5.4039999999999999]
[null,null,null,"Antofagasta  110 kV -  H3 Línea 110kV Guardiamarina - Antofagasta",9.1829999999999998,2.31,7.9870000000000001,1.883,7.8159999999999998,1.978,8.6829999999999998,2.1150000000000002,9.1829999999999998,6.8729999999999993,6.8729999999999993]
[null,null,null,"Antofagasta  110 kV -  H2 Línea 110 kV Antofagasta - Nueva La Negra",9.1829999999999998,3.0990000000000002,7.9870000000000001,2.5150000000000001,7.8159999999999998,2.6659999999999999,8.6829999999999998,2.8580000000000001,9.1829999999999998,6.0839999999999996,6.0839999999999996]
[null,"Antucoya ",110,"Antucoya  110 kV -  HT Transformador TR01 10/12,5 MVA 110/23 kV ",1.677,0.62,0.79600000000000004,0.19600000000000001,1.4510000000000001,0.53700000000000003,1.5189999999999999,0.54300000000000004,1.677,1.0569999999999999,1.0569999999999999]
[null,"Apoquindo ",110,"Apoquindo  110 kV -  H1 Línea 110 kV Apoquindo - Los Almendros (Los Dominicos) / El Salto  (Alonso de Córdova) 1 ",31.193000000000001,16.143000000000001,18.341999999999999,9.3849999999999998,27.018999999999998,13.983000000000001,27.960999999999999,14.44,31.193000000000001,15.05,16.143000000000001]
[null,null,null,"Apoquindo  110 kV -  H2 Línea 110 kV Apoquindo - Los Almendros  (Los Dominicos) /El Salto (Alonso de Córdova) 2",31.193000000000001,15.05,18.341999999999999,8.9570000000000007,27.018999999999998,13.037000000000001,27.960999999999999,13.522,31.193000000000001,16.143000000000001,16.143000000000001]
[null,"Arica ",110,"Arica  110 kV - HT3 Autotransformador 110/66/13,8 kV ",1.69,1.19,2.5049999999999999,2.0139999999999998,1.446,1.0249999999999999,2.9910000000000001,2.649,2.9910000000000001,0.5,2.649]
[null,"Atacama Kozán ",110,"Atacama Kozán  110 kV -  En Barra",7.1550000000000002,0,6.3460000000000001,0,6.1760000000000002,0,6.8860000000000001,0,7.1550000000000002,7.1550000000000002,7.1550000000000002]
[null,null,null,"Atacama Kozán  110 kV - HX Línea 110 kV Cerrillos - Atacama Kozán",7.1550000000000002,2.2090000000000001,6.3460000000000001,2.0099999999999998,6.1760000000000002,1.907,6.8860000000000001,2.145,7.1550000000000002,4.9459999999999997,4.9459999999999997]
[null,"Bajo Melipilla ",110,"Bajo Melipilla  110 kV - HT1 Transformador TR01 25/20/15 MVA 110/13,2 kV ",9.2590000000000003,0,8.9209999999999994,0,8.0180000000000007,0,9.1440000000000001,0,9.2590000000000003,9.2590000000000003,9.2590000000000003]
[null,null,null,"Bajo Melipilla  110 kV - HT2 Transformador TR02 40/50 MVA 110/66 kV ",9.2590000000000003,8.6999999999999994E-2,8.9209999999999994,5.5E-2,8.0180000000000007,7.2999999999999995E-2,9.1440000000000001,7.6999999999999999E-2,9.2590000000000003,9.1720000000000006,9.1720000000000006]
[null,null,null,"Bajo Melipilla  110 kV - H3 Línea 110 kV Bajo Melipilla - Tap Alto Melipilla ",9.2590000000000003,4.4630000000000001,8.9209999999999994,4.55,8.0180000000000007,3.8650000000000002,9.1440000000000001,4.4589999999999996,9.2590000000000003,4.7960000000000003,4.7960000000000003]
[null,null,null,"Bajo Melipilla  110 kV - H4 Línea 110 kV Bajo Melipilla - Carga Móvil ",9.2590000000000003,0,8.9209999999999994,0,8.0180000000000007,0,9.1440000000000001,0,9.2590000000000003,9.2590000000000003,9.2590000000000003]
[null,null,null,"Bajo Melipilla  110 kV - HX Línea 110kV Alto Melipilla - Bajo Melipilla",9.2590000000000003,4.7480000000000002,8.9209999999999994,4.343,8.0180000000000007,4.1130000000000004,9.1440000000000001,4.6189999999999998,9.2590000000000003,4.5779999999999994,4.7480000000000002]
[null,null,null,"Bajo Melipilla  110 kV - HT3 Transformador TR03 25/20/15 MVA 110/13,2 kV ",9.2590000000000003,0,8.9209999999999994,0,8.0180000000000007,0,9.1440000000000001,0,9.2590000000000003,9.2590000000000003,9.2590000000000003]
[null,"Baños del Toro ",110,"Baños del Toro  110 kV - H1 Transformador Baños del Toro (El Indio) 110/13.2 kV",0.86099999999999999,0,0.5,0,0.746,0,0.80600000000000005,0,0.86099999999999999,0.86099999999999999,0.86099999999999999]
[null,"Batuco ",110,"Batuco  110 kV -  H1 Línea 110 kV Batuco - Tap Off Punta Peuco/Cerro Navia 1",17.959,8.9789999999999992,11.91,5.9550000000000001,15.541,7.7709999999999999,16.315000000000001,8.157,17.959,8.98,8.98]
[null,null,null,"Batuco  110 kV -  H2 Línea 110 kV Batuco - Tap Off Punta Peuco/Cerro Navia 2",17.959,8.9789999999999992,11.91,5.9550000000000001,15.541,7.7709999999999999,16.315000000000001,8.157,17.959,8.98,8.98]
[null,null,null,"Batuco  110 kV - HT1 Transformador TR01 37,5 MVA 110/23,5 kV ",17.959,0,11.91,0,15.541,0,16.315000000000001,0,17.959,17.959,17.959]
[null,null,null,"Batuco  110 kV - HT2 Transformador TR02 37,5 MVA 110/23,5 kV ",17.959,0,11.91,0,15.541,0,16.315000000000001,0,17.959,17.959,17.959]
[null,null,null,"Batuco  110 kV - HT3 Transformador TR03 50 MVA 110/23,5 kV ",17.959,0,11.91,0,15.541,0,16.315000000000001,0,17.959,17.959,17.959]
[null,"Bicentenario ",110,"Bicentenario  110 kV -  H1 Línea 110 kV Bicentenario - Cerro Navia (Santa Marta) /Chena 1",41.33,20.664999999999999,26.364999999999998,13.182,35.798000000000002,17.899000000000001,37.305999999999997,18.652999999999999,41.33,20.664999999999999,20.664999999999999]
[null,null,null,"Bicentenario  110 kV -  H2 Línea 110 kV Bicentenario - Cerro Navia (Santa Marta) /Chena 2",41.33,20.664999999999999,26.364999999999998,13.182,35.798000000000002,17.899000000000001,37.305999999999997,18.652999999999999,41.33,20.664999999999999,20.664999999999999]
[null,null,null,"Bicentenario  110 kV - HT1 Transformador TR01 25 MVA 110/12,5 kV ",41.33,0,26.364999999999998,0,35.798000000000002,0,37.305999999999997,0,41.33,41.33,41.33]
[null,null,null,"Bicentenario  110 kV - HT2 Transformador TR02 25 MVA 110/13,2 kV ",41.33,0,26.364999999999998,0,35.798000000000002,0,37.305999999999997,0,41.33,41.33,41.33]
[null,"Bocamina",154,"Bocamina 154 kV - A1 Línea 154 kV Bocamina - Lagunillas",10.715999999999999,10.715999999999999,12.18,10.901,9.2089999999999996,9.2089999999999996,11.778,10.738,12.18,1.2789999999999999,10.901]
[null,null,null,"Bocamina 154 kV - AT1 Transformador Bocamina TR01 147MVA 161/13.8 kV N°1",10.715999999999999,0,12.18,1.292,9.2089999999999996,0,11.778,1.524,12.18,10.888,10.888]
[null,null,null,"Bocamina 154 kV - AT2 Transformador Bocamina 161/13.8 kV SSAA",10.715999999999999,0,12.18,0,9.2089999999999996,0,11.778,0,12.18,12.18,12.18]
[null,"Bollenar ",110,"Bollenar  110 kV - HT Transformador TR1 20/16 MVA 110/23-13,8 kV ",4.7110000000000003,0,3.226,0,4.0810000000000004,0,4.4029999999999996,0,4.7110000000000003,4.7110000000000003,4.7110000000000003]
[null,"Bombeo 2 ",110,"Bombeo 2  110 kV - H1 Transformador TR1 110/4.16 kV 10 MVA ",2.069,0,1.321,0,1.79,0,1.883,0,2.069,2.069,2.069]
[null,"Bombeo 1 y Desaladora",110,"Bombeo 1 y Desaladora 110 kV - H2 Transformador N°1 110/4.16 kV Planta Desaladora y Bombeo 1",1.625,0,1.0389999999999999,0,1.4059999999999999,0,1.4770000000000001,0,1.625,1.625,1.625]
[null,"Bosquemar ",110,"Bosquemar  110 kV - HX Línea 110kV Reñaca - Bosquemar",15.253,4.04,9.8160000000000007,2.7589999999999999,13.265000000000001,3.5089999999999999,13.987,3.7519999999999998,15.253,11.213000000000001,11.213000000000001]
[null,null,null,"Bosquemar  110 kV - H1 Línea 110 kV Bosquemar - Concon",15.253,11.215,9.8160000000000007,7.0590000000000002,13.265000000000001,9.7590000000000003,13.987,10.243,15.253,4.0380000000000003,11.215]
[null,"Brasil ",110,"Brasil  110 kV -  H1 Línea 110 kV Brasil - Renca (Carrascal) 1 ",41.625999999999998,20.812999999999999,24.643000000000001,12.321999999999999,35.981999999999999,17.991,37.192,18.596,41.625999999999998,20.812999999999999,20.812999999999999]
[null,null,null,"Brasil  110 kV -  H2 Línea 110 kV Brasil - Renca (Carrascal)  2",41.625999999999998,20.812999999999999,24.643000000000001,12.321999999999999,35.981999999999999,17.991,37.192,18.596,41.625999999999998,20.812999999999999,20.812999999999999]
[null,"Buin ",110,"Buin  110 kV -  H1 Línea 110 kV Buin - Lo Espejo (San Bernardo) 2 ",44.645000000000003,5.5919999999999996,49.23,4.3410000000000002,38.725999999999999,4.8419999999999996,48.042000000000002,5.0730000000000004,49.23,44.888999999999996,44.888999999999996]
[null,null,null,"Buin  110 kV -  H2 Línea 110 kV Buin - Lo Espejo (San Bernardo)  1 ",44.645000000000003,5.5919999999999996,49.23,4.3410000000000002,38.725999999999999,4.8419999999999996,48.042000000000002,5.0730000000000004,49.23,44.888999999999996,44.888999999999996]
[null,null,null,"Buin  110 kV -  H3 Línea 110 kV Buin - Florida (La Pintana)  2",44.645000000000003,10.643000000000001,49.23,11.289,38.725999999999999,9.2379999999999995,48.042000000000002,11.089,49.23,37.940999999999995,37.940999999999995]
[null,null,null,"Buin  110 kV -  H4 Línea 110 kV Buin - Florida  (La Pintana) 1",44.645000000000003,10.643000000000001,49.23,11.289,38.725999999999999,9.2379999999999995,48.042000000000002,11.089,49.23,37.940999999999995,37.940999999999995]
[null,null,null,"Buin  110 kV - HT1 Transformador TR01 400 MVA 220/110/13,8 kV ",44.645000000000003,12.266,49.23,18.047999999999998,38.725999999999999,10.644,48.042000000000002,16.300999999999998,49.23,32.379000000000005,32.379000000000005]
[null,null,null,"Buin  110 kV - CCE1A Banco de Condensadores 1",44.645000000000003,0,49.23,0,38.725999999999999,0,48.042000000000002,0,49.23,49.23,49.23]
[null,"Cabildo ",110,"Cabildo  110 kV - HT2 Transformador TR2 13/10 MVA 110/24-14,4 kV ",2.0139999999999998,0,1.2629999999999999,0,1.7410000000000001,0,1.9039999999999999,0,2.0139999999999998,2.0139999999999998,2.0139999999999998]
[null,null,null,"Cabildo  110 kV - HT1 Transformador TR1 30/24/18 MVA 110/25 kV",2.0139999999999998,0,1.2629999999999999,0,1.7410000000000001,0,1.9039999999999999,0,2.0139999999999998,2.0139999999999998,2.0139999999999998]
[null,"Calama ",110,"Calama  110 kV - HT1 Transformador TR01 33/25 MVA 110/23 kV ",7.2060000000000004,5.1999999999999998E-2,8.7119999999999997,4.3999999999999997E-2,6.0049999999999999,4.4999999999999998E-2,8.6769999999999996,4.7E-2,8.7119999999999997,8.6679999999999993,8.6679999999999993]
[null,null,null,"Calama  110 kV - HT4 Transformador TR04 33/25 MVA 110/23 kV ",7.2060000000000004,5.2999999999999999E-2,8.7119999999999997,4.3999999999999997E-2,6.0049999999999999,4.5999999999999999E-2,8.6769999999999996,4.8000000000000001E-2,8.7119999999999997,8.6679999999999993,8.6679999999999993]
[null,null,null,"Calama  110 kV - H3 Línea 110 kV Calama - Valle de los Vientos ",7.2060000000000004,0.41,8.7119999999999997,0.55400000000000005,6.0049999999999999,0.19700000000000001,8.6769999999999996,0.73699999999999999,8.7119999999999997,8.1579999999999995,8.1579999999999995]
[null,null,null,"Calama  110 kV - HT5 Transformador TR1P 55/45/5 MVA 210/110/12,2 kV ",7.2060000000000004,3.379,8.7119999999999997,4.0640000000000001,6.0049999999999999,2.9020000000000001,8.6769999999999996,4.0010000000000003,8.7119999999999997,4.6759999999999993,4.6759999999999993]
[null,null,null,"Calama  110 kV - HTX Transformador 150MVA 210/110/23 kV",7.2060000000000004,3.379,8.7119999999999997,4.0640000000000001,6.0049999999999999,2.9020000000000001,8.6769999999999996,4.0010000000000003,8.7119999999999997,4.6759999999999993,4.6759999999999993]
[null,null,null,"Calama  110 kV - H2 Línea 110 kV Calama - San Pedro ",7.2060000000000004,0,8.7119999999999997,0,6.0049999999999999,0,8.6769999999999996,0,8.7119999999999997,8.7119999999999997,8.7119999999999997]
[null,"Calbuco ",110,"Calbuco  110 kV - HT1 Transformador TR1 16 MVA 115/69/24 kV ",2.625,0,1.831,0,2.2679999999999998,0,2.4390000000000001,0,2.625,2.625,2.625]
[null,"Caldera",110,"Caldera 110 kV - HX1 Línea 110kV Caldera - Punta Padrones",2.7669999999999999,0,1.7969999999999999,0,2.3929999999999998,0,2.544,0,2.7669999999999999,2.7669999999999999,2.7669999999999999]
[null,null,null,"Caldera 110 kV - HX2 Línea 110kV Caldera - EB2",2.7669999999999999,1.4510000000000001,1.7969999999999999,0.89800000000000002,2.3929999999999998,1.256,2.544,1.3129999999999999,2.7669999999999999,1.3159999999999998,1.4510000000000001]
[null,"Caldera",110,"Caldera  110 kV - HT1 Transformador T1 12/10 MVA 110/23-13.2 kV ",2.7669999999999999,0,1.7969999999999999,0,2.3929999999999998,0,2.544,0,2.7669999999999999,2.7669999999999999,2.7669999999999999]
[null,"Canal Melado ",110,"Canal Melado  110 kV - HT Transformador TR 220/110/13.8 kV 70 MVA ",3.6259999999999999,2.9710000000000001,4.7670000000000003,4.0609999999999999,3.1080000000000001,2.577,4.7640000000000002,4.0670000000000002,4.7670000000000003,0.70600000000000041,4.0670000000000002]
[null,"CAP Rengo",154,"CAP Rengo 154 kV -  En Barra",11.798,0,8.7219999999999995,0,10.286,0,10.976000000000001,0,11.798,11.798,11.798]
[null,"Capricornio ",110,"Capricornio  110 kV - HT1 Transformador TR01 80/80/20 MVA 220/110/13,8 kV ",7.5220000000000002,2.8180000000000001,7.5179999999999998,3.669,6.4509999999999996,2.4359999999999999,7.6340000000000003,3.298,7.6340000000000003,4.7040000000000006,4.7040000000000006]
[null,null,null,"Capricornio  110 kV - H2 Línea 110 kV Capricornio - Alto Norte/Tap Off El Negro ",7.5220000000000002,1.7310000000000001,7.5179999999999998,1.4,6.4509999999999996,1.4850000000000001,7.6340000000000003,1.6020000000000001,7.6340000000000003,6.1180000000000003,6.1180000000000003]
[null,null,null,"Capricornio  110 kV - H1 Línea 110 kV Capricornio - Tap Off Uribe/Antofagasta",7.5220000000000002,2.9990000000000001,7.5179999999999998,2.468,6.4509999999999996,2.556,7.6340000000000003,2.7839999999999998,7.6340000000000003,5.05,5.05]
[null,null,null,"Capricornio  110 kV - H3 Línea 110 kV Capricornio - Sierra Miranda ",7.5220000000000002,0,7.5179999999999998,0,6.4509999999999996,0,7.6340000000000003,0,7.6340000000000003,7.6340000000000003,7.6340000000000003]
[null,"Cardones ",110,"Cardones  110 kV - H8 Línea 110 kV Cardones - Central Cenizas ",10.246,0.497,11.926,0.81499999999999995,8.83,0.42899999999999999,11.662000000000001,0.76100000000000001,11.926,11.111000000000001,11.111000000000001]
[null,null,null,"Cardones  110 kV - H3 Línea 110 kV Copayapu - Cardones C2",10.246,0.78,11.926,0.79200000000000004,8.83,0.67300000000000004,11.662000000000001,0.79100000000000004,11.926,11.134,11.134]
[null,null,null,"Cardones  110 kV - H2 Línea 110 kV Cardones - Maintencillo ",10.246,0.99299999999999999,11.926,0.84699999999999998,8.83,0.85399999999999998,11.662000000000001,0.94599999999999995,11.926,11.079000000000001,11.079000000000001]
[null,null,null,"Cardones  110 kV - HT1 AutoTransformador ATR1 75 MVA 220/115/13,8 kV ",10.246,2.3159999999999998,11.926,2.7890000000000001,8.83,1.996,11.662000000000001,2.6549999999999998,11.926,9.1370000000000005,9.1370000000000005]
[null,null,null,"Cardones  110 kV - H4 Línea 110 kV Cardones - Copayapu/Cerrillos/Tierra Amarilla ",10.246,1.4790000000000001,11.926,1.395,8.83,1.2749999999999999,11.662000000000001,1.4430000000000001,11.926,10.531000000000001,10.531000000000001]
[null,null,null,"Cardones  110 kV - HT2 AutoTransformador ATR2 75 MVA 220/115/13,8 kV ",10.246,2.1709999999999998,11.926,2.68,8.83,1.871,11.662000000000001,2.528,11.926,9.2460000000000004,9.2460000000000004]
[null,null,null,"Cardones  110 kV - H6 Línea 110 kV Cardones - Fundición Paipote ",10.246,0,11.926,0,8.83,0,11.662000000000001,0,11.926,11.926,11.926]
[null,null,null,"Cardones  110 kV - HT3 AutoTransformador ATR3 79 MVA 220/115/13,8 kV ",10.246,2.1459999999999999,11.926,2.7229999999999999,8.83,1.85,11.662000000000001,2.5659999999999998,11.926,9.2029999999999994,9.2029999999999994]
[null,null,null,"Cardones  110 kV - H9 Línea 110 kV Cardones - Travesía ",10.246,5.0000000000000001E-3,11.926,5.0000000000000001E-3,8.83,5.0000000000000001E-3,11.662000000000001,5.0000000000000001E-3,11.926,11.920999999999999,11.920999999999999]
[null,null,null,"Cardones  110 kV - H7 Línea 110 kV Cardones - Magnetita ",10.246,0,11.926,0,8.83,0,11.662000000000001,0,11.926,11.926,11.926]
[null,null,null,"Cardones  110 kV - H1 Línea 110 kV Cardones - Refugio ",10.246,0,11.926,3.0000000000000001E-3,8.83,0,11.662000000000001,4.0000000000000001E-3,11.926,11.923,11.923]
[null,"Carrascal ",110,"Carrascal  110 kV - H1 Línea 110 kV Carrascal - Renca/Brasil 1 ",50.143999999999998,25.071999999999999,39.533000000000001,19.766999999999999,43.329000000000001,21.664999999999999,46.613999999999997,23.306999999999999,50.143999999999998,25.071999999999999,25.071999999999999]
[null,null,null,"Carrascal  110 kV - H2 Línea 110 kV Carrascal - Renca/Brasil 2",50.143999999999998,25.071999999999999,39.533000000000001,19.766999999999999,43.329000000000001,21.664999999999999,46.613999999999997,23.306999999999999,50.143999999999998,25.071999999999999,25.071999999999999]
[null,"Casas Viejas ",110,"Casas Viejas  110 kV -  En Barra",3.6419999999999999,0,2.379,0,3.149,0,3.4390000000000001,0,3.6419999999999999,3.6419999999999999,3.6419999999999999]
[null,"Castilla ",110,"Castilla  110 kV -  En Barra",4.3040000000000003,0,2.8780000000000001,0,3.7189999999999999,0,4.0350000000000001,0,4.3040000000000003,4.3040000000000003,4.3040000000000003]
[null,"Castro ",110,"Castro  110 kV - H1 Línea 110 kV Castro - Gamboa",4.9020000000000001,4.6589999999999998,5.6529999999999996,5.391,4.12,3.9129999999999998,5.6050000000000004,5.3310000000000004,5.6529999999999996,0.27400000000000002,5.391]
[null,null,null,"Castro  110 kV - H2 Línea 110 kV Castro - Chonchi ",4.9020000000000001,0.247,5.6529999999999996,0.26500000000000001,4.12,0.21099999999999999,5.6050000000000004,0.27500000000000002,5.6529999999999996,5.3879999999999999,5.3879999999999999]
[null,null,null,"Castro  110 kV - HT1 Transformador TR1 110/23 kV ",4.9020000000000001,0,5.6529999999999996,0,4.12,0,5.6050000000000004,0,5.6529999999999996,5.6529999999999996,5.6529999999999996]
[null,"Central Andes Generación ",110,"Central Andes Generación  110 kV - HT Transformador TR1 63 MVA 110/10,5 kV ",9.3089999999999993,0.8,11.847,1.0369999999999999,8.0220000000000002,0.68300000000000005,11.73,1.0009999999999999,11.847,10.809999999999999,10.809999999999999]
[null,"Central Cenizas ",110,"Central Cenizas  110 kV - HT Transformador TR01 35/30 MVA 110/11 kV ",9.9480000000000004,0.497,11.374000000000001,0.84299999999999997,8.5739999999999998,0.42899999999999999,11.135999999999999,0.78200000000000003,11.374000000000001,10.531000000000001,10.531000000000001]
[null,"Central Chacayes",110,"Central Chacayes 110 kV -  En Barra",10.599,0,11.176,0,9.3030000000000008,0,11.196,0,11.196,11.196,11.196]
[null,"Central Chañares ",110,"Central Chañares  110 kV - HT1 Transformador TR1 72/50 MVA 110/33 kV ",6.4480000000000004,0,6.593,0.70699999999999996,5.5670000000000002,0,6.6059999999999999,0.72799999999999998,6.6059999999999999,6.4480000000000004,6.4480000000000004]
[null,"Central Colmito ",110,"Central Colmito  110 kV - H1 Línea 110 kV Colmito - Torquemada",20.742000000000001,19.294,18.786999999999999,15.92,18.068000000000001,16.858000000000001,20.173999999999999,18.035,20.742000000000001,2.8669999999999991,19.294]
[null,"Central Curillinque",154,"Central Curillinque 154 kV - AT Transformador Central Curillinque 154/13.8 kV",6.0460000000000003,1.133,5.5990000000000002,1.546,5.056,1.0129999999999999,5.9470000000000001,1.3759999999999999,6.0460000000000003,4.9130000000000003,4.9130000000000003]
[null,"Central Diesel Enaex ",110,"Central Diesel Enaex  110 kV -  En Barra",7.2830000000000004,0,7.4989999999999997,0,6.2039999999999997,0,7.5039999999999996,0,7.5039999999999996,7.5039999999999996,7.5039999999999996]
[null,"Central Diesel Tamaya ",110,"Central Diesel Tamaya  110 kV - H4 Línea 110 kV Central Diesel Tamaya - Central Tocopilla ",11.012,3.2320000000000002,13.978999999999999,3.0489999999999999,9.33,2.7989999999999999,14.179,3.1349999999999998,14.179,11.044,11.044]
[null,null,null,"Central Diesel Tamaya  110 kV - H2 Línea 110 kV Central Diesel Tamaya - Central Tocopilla ",11.012,3.6349999999999998,13.978999999999999,3.375,9.33,3.149,14.179,3.4940000000000002,14.179,10.685,10.685]
[null,null,null,"Central Diesel Tamaya  110 kV - H1 Línea 110 kV Central Diesel Tamaya - Salar",11.012,0.86399999999999999,13.978999999999999,0.77900000000000003,9.33,0.74399999999999999,14.179,0.82099999999999995,14.179,13.358000000000001,13.358000000000001]
[null,null,null,"Central Diesel Tamaya  110 kV - H3 Línea 110 kV Central Diesel Tamaya - A",11.012,0.92,13.978999999999999,0.84799999999999998,9.33,0.79200000000000004,14.179,0.88300000000000001,14.179,13.295999999999999,13.295999999999999]
[null,null,null,"Central Diesel Tamaya  110 kV - HT1 Transformador TR1 50/33,3 MVA 110/11 kV ",11.012,0.79500000000000004,13.978999999999999,1.984,9.33,0.621,14.179,2.3090000000000002,14.179,11.994999999999999,11.994999999999999]
[null,null,null,"Central Diesel Tamaya  110 kV - HT2 Transformador TR2 50/33,3 MVA 110/11 kV ",11.012,0.79500000000000004,13.978999999999999,1.984,9.33,0.621,14.179,2.3090000000000002,14.179,11.994999999999999,11.994999999999999]
[null,null,null,"Central Diesel Tamaya  110 kV - HT3 Transformador TR3 50/33,3 MVA 110/11 kV ",11.012,0.79500000000000004,13.978999999999999,1.984,9.33,0.621,14.179,2.3090000000000002,14.179,11.994999999999999,11.994999999999999]
[null,null,null,"Central Diesel Tamaya  110 kV - HT4 Transformador TR04 10,5/9,38/7,5 MVA 110/23 kV ",11.012,0,13.978999999999999,0,9.33,0,14.179,0,14.179,14.179,14.179]
[null,"Central Emelda ",110,"Central Emelda  110 kV - H1 Transformador TR01 110/10.5 kV",8.7899999999999991,0.73099999999999998,10.315,1.2370000000000001,7.577,0.627,10.074,1.1479999999999999,10.315,9.0779999999999994,9.0779999999999994]
[null,null,null,"Central Emelda  110 kV - H2 Transformador TR02 110/11.5 kV",8.7899999999999991,0.73099999999999998,10.315,1.2370000000000001,7.577,0.627,10.074,1.1479999999999999,10.315,9.0779999999999994,9.0779999999999994]
[null,"Central Isla B1",154,"Central Isla B1 154 kV -  En Barra",5.88,0,5.2910000000000004,0,4.8559999999999999,0,5.6840000000000002,0,5.88,5.88,5.88]
[null,"Central Isla B2",154,"Central Isla B2 154 kV -  En Barra",5.88,0,5.2910000000000004,0,4.8559999999999999,0,5.6840000000000002,0,5.88,5.88,5.88]
[null,"Central Javiera",110,"Central Javiera 110 kV - H1 Línea 110 kV Central Javiera - Planta de Óxidos",3.8660000000000001,0,4.593,3.0000000000000001E-3,3.3439999999999999,0,4.7270000000000003,3.0000000000000001E-3,4.7270000000000003,4.7240000000000002,4.7240000000000002]
[null,null,null,"Central Javiera 110 kV - H2 Línea 110 kV Central Javiera - Diego de Almagro",3.8660000000000001,3.8660000000000001,4.593,3.484,3.3439999999999999,3.3439999999999999,4.7270000000000003,3.7719999999999998,4.7270000000000003,1.109,3.8660000000000001]
[null,null,null,"Central Javiera 110 kV - HT1 Transformador TR1 110/22 kV",3.8660000000000001,0,4.593,1.117,3.3439999999999999,0,4.7270000000000003,1.367,4.7270000000000003,3.8660000000000001,3.8660000000000001]
[null,"Central Laguna Verde ",110,"Central Laguna Verde  110 kV - H1 Línea 110kV La Pólvora - Central Laguna verde C1",14.734,6.1989999999999998,13.494999999999999,5.1660000000000004,12.772,5.3780000000000001,14.768000000000001,5.9489999999999998,14.768000000000001,8.8190000000000008,8.8190000000000008]
[null,null,null,"Central Laguna Verde  110 kV - H2 Línea 110kV La Pólvora - Central Laguna Verde C2",14.734,6.1989999999999998,13.494999999999999,5.1660000000000004,12.772,5.3780000000000001,14.768000000000001,5.9489999999999998,14.768000000000001,8.8190000000000008,8.8190000000000008]
[null,null,null,"Central Laguna Verde  110 kV - HT3 AutoTransformador ATR 60 MVA 110/66 kV",14.734,1.111,13.494999999999999,0.97599999999999998,12.772,0.96199999999999997,14.768000000000001,1.097,14.768000000000001,13.671000000000001,13.671000000000001]
[null,null,null,"Central Laguna Verde  110 kV - HT4 Transformador TRTG 28,8 MVA 110/11.5 kV ",14.734,0.40500000000000003,13.494999999999999,0.84099999999999997,12.772,0.35799999999999998,14.768000000000001,0.69299999999999995,14.768000000000001,14.329000000000001,14.329000000000001]
[null,null,null,"Central Laguna Verde  110 kV - H5 Transformador TR1 30 MVA 110/12 kV  ",14.734,0.85699999999999998,13.494999999999999,1.381,12.772,0.73599999999999999,14.768000000000001,1.1739999999999999,14.768000000000001,13.877000000000001,13.877000000000001]
[null,"Central Las Piedras",110,"Central Las Piedras 110 kV -  En Barra",9.2940000000000005,0,7.3659999999999997,0,7.952,0,8.7690000000000001,0,9.2940000000000005,9.2940000000000005,9.2940000000000005]
[null,"Central Licán",110,"Central Licán 110 kV - H1 Línea 110 kV Central Lican - Mantilhue/Antillanca",3.569,3.141,3.6669999999999998,2.992,3.0979999999999999,2.7240000000000002,3.7389999999999999,3.1469999999999998,3.7389999999999999,0.67499999999999982,3.1469999999999998]
[null,"Central Lomas Los Colorados ",110,"Central Lomas Los Colorados  110 kV - HT1 Transformador TR1 110/23 kV",5.0430000000000001,0.47699999999999998,4.34,1.0169999999999999,4.3659999999999997,0.41199999999999998,5.0949999999999998,0.81399999999999995,5.0949999999999998,4.5659999999999998,4.5659999999999998]
[null,"Central Los Hierros ",110,"Central Los Hierros  110 kV - H Línea 110 kV Central Los Hierros - Canal Melado ",2.9809999999999999,2.4140000000000001,3.4039999999999999,2.4940000000000002,2.5499999999999998,2.0880000000000001,3.3580000000000001,2.581,3.4039999999999999,0.9099999999999997,2.581]
[null,"Central Los Hierros II ",110,"Central Los Hierros II  110 kV - H Línea 110 kV Central Los Hierros II - Canal Melado ",3.2570000000000001,3.1339999999999999,3.8130000000000002,3.7240000000000002,2.7879999999999998,2.69,3.782,3.68,3.8130000000000002,0.12300000000000022,3.7240000000000002]
[null,"Central Los Quilos ",110,"Central Los Quilos  110 kV -  En Barra",10.532999999999999,0,11.33,0,9.3849999999999998,0,11.179,0,11.33,11.33,11.33]
[null,"Central Maitenes ",110,"Central Maitenes  110 kV - T4 Transformador TR GE 110/12 kV ",19.015000000000001,0,17.417999999999999,0.64400000000000002,16.334,0,18.571999999999999,0.60299999999999998,19.015000000000001,19.015000000000001,19.015000000000001]
[null,null,null,"Central Maitenes  110 kV - H1 Línea 110 kV Central Maitenes - Tap Off La Laja 1",19.015000000000001,2.6269999999999998,17.417999999999999,1.984,16.334,2.2610000000000001,18.571999999999999,2.4620000000000002,19.015000000000001,16.388000000000002,16.388000000000002]
[null,null,null,"Central Maitenes  110 kV - H2 Línea 110 kV Central Maitenes - Tap Off La Laja 2",19.015000000000001,2.6269999999999998,17.417999999999999,1.984,16.334,2.2610000000000001,18.571999999999999,2.4620000000000002,19.015000000000001,16.388000000000002,16.388000000000002]
[null,null,null,"Central Maitenes  110 kV - HX1 Línea 110 kV Alto Maipo - Maitenes",19.015000000000001,8.4749999999999996,17.417999999999999,7.2649999999999997,16.334,7.2960000000000003,18.571999999999999,7.9749999999999996,19.015000000000001,10.597,10.597]
[null,null,null,"Central Maitenes  110 kV - HX2 Línea 110kV Alfalfal - Central Maitenes",19.015000000000001,5.0179999999999998,17.417999999999999,4.9320000000000004,16.334,4.3559999999999999,18.571999999999999,4.7629999999999999,19.015000000000001,13.997,13.997]
[null,"Central Mejillones ",110,"Central Mejillones  110 kV -  En Barra",7.3440000000000003,0,7.5350000000000001,0,6.2560000000000002,0,7.5709999999999997,0,7.5709999999999997,7.5709999999999997,7.5709999999999997]
[null,"Central Nueva Renca",110,"Central Nueva Renca 110 kV - 52GV Transformador TR01 205MVA 110/15,75kV (UG Vapor)",54.667000000000002,3.8090000000000002,50.243000000000002,5.7869999999999999,47.226999999999997,3.1920000000000002,53.567,5.0750000000000002,54.667000000000002,50.858000000000004,50.858000000000004]
[null,"Central Olivos ",110,"Central Olivos  110 kV -  En Barra",8.4649999999999999,0,9.3610000000000007,0,7.157,0,9.3919999999999995,0,9.3919999999999995,9.3919999999999995,9.3919999999999995]
[null,"Central Parque Solar Los Loros",110,"Central Parque Solar Los Loros 110 kV - H1 Línea 110 kV Central PV Los Loros - Los Loros 1",2.2850000000000001,2.2850000000000001,2.8220000000000001,2.0499999999999998,1.9770000000000001,1.9770000000000001,2.9369999999999998,2.2410000000000001,2.9369999999999998,0.77200000000000024,2.2850000000000001]
[null,null,null,"Central Parque Solar Los Loros 110 kV - HT1 Transformador TR1 24/30 MVA 110/23 kV N°1",2.2850000000000001,0,2.8220000000000001,0.38700000000000001,1.9770000000000001,0,2.9369999999999998,0.501,2.9369999999999998,2.4359999999999999,2.4359999999999999]
[null,null,null,"Central Parque Solar Los Loros 110 kV - HT2 Transformador TR2 24/30 MVA 110/23 kV N°2",2.2850000000000001,0,2.8220000000000001,0.38700000000000001,1.9770000000000001,0,2.9369999999999998,0.501,2.9369999999999998,2.4359999999999999,2.4359999999999999]
[null,"Central Puntilla ",110,"Central Puntilla  110 kV -  En Barra",9.4589999999999996,0,6.9009999999999998,0,8.2059999999999995,0,9.2110000000000003,0,9.4589999999999996,9.4589999999999996,9.4589999999999996]
[null,"Central PV El Salvador",110,"Central PV El Salvador 110 kV - H1 Línea 110kV Central PV El Salvador - Diego de Almagro/El Salvador",5.3520000000000003,0,4.3650000000000002,0,4.6260000000000003,0,5.0650000000000004,0,5.3520000000000003,5.3520000000000003,5.3520000000000003]
[null,"Central Queltehues ",110,"Central Queltehues  110 kV - H1 Línea 110 kV Central Queltehues - Tap Off La Laja 1",6.8769999999999998,2.9329999999999998,5.6130000000000004,1.944,5.843,2.54,6.79,2.698,6.8769999999999998,4.0920000000000005,4.0920000000000005]
[null,null,null,"Central Queltehues  110 kV - H2 Línea 110 kV Central Queltehues - Tap Off La Laja 2",6.8769999999999998,2.9329999999999998,5.6130000000000004,1.944,5.843,2.5409999999999999,6.79,2.698,6.8769999999999998,4.0920000000000005,4.0920000000000005]
[null,null,null,"Central Queltehues  110 kV - HT1 Transformador TR1 28 MVA 110/12 kV ",6.8769999999999998,0.22700000000000001,5.6130000000000004,0.56100000000000005,5.843,0.16800000000000001,6.79,0.46700000000000003,6.8769999999999998,6.6499999999999995,6.6499999999999995]
[null,null,null,"Central Queltehues  110 kV - HT2 Transformador TR2 28 MVA 110/12 kV ",6.8769999999999998,0.222,5.6130000000000004,0.495,5.843,0.16400000000000001,6.79,0.41299999999999998,6.8769999999999998,6.6549999999999994,6.6549999999999994]
[null,null,null,"Central Queltehues  110 kV - HT3 Transformador TR3 28 MVA 110/12 kV ",6.8769999999999998,0.21199999999999999,5.6130000000000004,9.8000000000000004E-2,5.843,0.157,6.79,0.16600000000000001,6.8769999999999998,6.665,6.665]
[null,null,null,"Central Queltehues  110 kV - HT5 Transformador TR Aux 5 MVA 110/12 kV ",6.8769999999999998,0.125,5.6130000000000004,6.0999999999999999E-2,5.843,9.7000000000000003E-2,6.79,0.10199999999999999,6.8769999999999998,6.7519999999999998,6.7519999999999998]
[null,"Central Quintero",110,"Central Quintero 110 kV -  En Barra",21.134,0,8.0150000000000006,0,18.298999999999999,0,18.916,0,21.134,21.134,21.134]
[null,"Central Renca",110,"Central Renca 110 kV - H6 Acoplador de Barras BP1 - BP3",54.667000000000002,2.89,50.243000000000002,6.81,47.226999999999997,2.46,53.567,5.7,54.667000000000002,51.777000000000001,51.777000000000001]
[null,"Central Río Huasco ",110,"Central Río Huasco  110 kV - HT1 Transformador T1 7 MVA 110/6.6 kV",2.74,0.127,2.351,0.29099999999999998,2.3679999999999999,0.115,2.827,0.22900000000000001,2.827,2.6130000000000004,2.6130000000000004]
[null,"Central San Pedro Dalcahue \n",110,"Central San Pedro Dalcahue \n 110 kV - HT-1 Transformador N°2 75 MVA 110/30 kV ",3.6360000000000001,0.78,4.2869999999999999,0.67200000000000004,2.7679999999999998,0.34300000000000003,4.8470000000000004,1.0880000000000001,4.8470000000000004,3.7590000000000003,3.7590000000000003]
[null,null,null,"Central San Pedro Dalcahue \n 110 kV - HT-2 Transformador N°2 40 MVA 110/30 kV ",3.6360000000000001,0,4.2869999999999999,0.84599999999999997,2.7679999999999998,0,4.8470000000000004,1.452,4.8470000000000004,3.6360000000000001,3.6360000000000001]
[null,null,null,"Central San Pedro Dalcahue \n 110 kV - H1 Línea 110 kV Central San Pedro Dalcahue - Chiloé",3.6360000000000001,2.859,4.2869999999999999,2.7719999999999998,2.7679999999999998,2.4630000000000001,4.8470000000000004,2.7730000000000001,4.8470000000000004,2.0740000000000003,2.859]
[null,"Central Santiago Solar ",110,"Central Santiago Solar  110 kV -  H1 Línea 110 kV Central Santiago Solar - Las Vegas ",12.163,3.927,10.945,2.8879999999999999,10.518000000000001,3.387,11.887,3.5449999999999999,12.163,8.3420000000000005,8.3420000000000005]
[null,null,null,"Central Santiago Solar  110 kV -  H2 Línea 110 kV Central Santiago Solar - Tap Off Punta Peuco/Cerro Navia ",12.163,8.2360000000000007,10.945,6.2060000000000004,10.518000000000001,7.1310000000000002,11.887,7.4859999999999998,12.163,4.7389999999999999,8.2360000000000007]
[null,null,null,"Central Santiago Solar  110 kV - HT1 Transformador TR1 110/30 kV 110 MVA ",12.163,0,10.945,1.8640000000000001,10.518000000000001,0,11.887,1.698,12.163,12.163,12.163]
[null,null,110,"Central Tocopilla  110 kV - HR Acoplador ",12.444000000000001,4.0000000000000001E-3,12.677,2E-3,10.634,4.0000000000000001E-3,12.605,4.0000000000000001E-3,12.677,12.674999999999999,12.674999999999999]
[null,"Central Tocopilla ",null,"Central Tocopilla  110 kV - HT1 Transformador TR1 28/23 MVA 110/11,5 kV ",12.444000000000001,0.28599999999999998,12.677,0.221,10.634,0.28199999999999997,12.605,0.26800000000000002,12.677,12.456,12.456]
[null,null,null,"Central Tocopilla  110 kV - HT2 Transformador TR2 28/23 MVA 110/11,5 kV ",12.444000000000001,0.28599999999999998,12.677,0.221,10.634,0.28199999999999997,12.605,0.26800000000000002,12.677,12.456,12.456]
[null,null,null,"Central Tocopilla  110 kV - H1 Línea 110 kV Central Tocopilla - A 1",12.444000000000001,0.627,12.677,0.51100000000000001,10.634,0.53500000000000003,12.605,0.56599999999999995,12.677,12.166,12.166]
[null,null,null,"Central Tocopilla  110 kV - H2 Línea 110 kV Central Tocopilla - A 2",12.444000000000001,0.61799999999999999,12.677,0.52800000000000002,10.634,0.52700000000000002,12.605,0.57699999999999996,12.677,12.148999999999999,12.148999999999999]
[null,null,null,"Central Tocopilla  110 kV - H3 Línea 110 kV Central Tocopilla - Central Diesel Tamaya ",12.444000000000001,1.4039999999999999,12.677,1.649,10.634,1.1599999999999999,12.605,1.538,12.677,11.067,11.067]
[null,null,null,"Central Tocopilla  110 kV - H4 Línea 110 kV Central Tocopilla - Central Diesel Tamaya ",12.444000000000001,1.58,12.677,1.6990000000000001,10.634,1.3049999999999999,12.605,1.6259999999999999,12.677,10.979000000000001,10.979000000000001]
[null,null,null,"Central Tocopilla  110 kV - HAT1 Autotransformador ATR1 100/100/30 MVA 220/110/13,8 kV ",12.444000000000001,3.8330000000000002,12.677,2.6139999999999999,10.634,3.28,12.605,3.379,12.677,10.062999999999999,10.062999999999999]
[null,null,null,"Central Tocopilla  110 kV - HAT2 Autotransformador ATR2 100/100/30 MVA 220/110/13,8 kV ",12.444000000000001,3.8330000000000002,12.677,2.6139999999999999,10.634,3.28,12.605,3.379,12.677,10.062999999999999,10.062999999999999]
[null,null,null,"Central Tocopilla  110 kV - HG12 Transformador TR12 92/75 MVA 110/13,8 kV ",12.444000000000001,0,12.677,1.2090000000000001,10.634,0,12.605,1.266,12.677,12.444000000000001,12.444000000000001]
[null,null,null,"Central Tocopilla  110 kV - HG13 Transformador TR13 92/75 MVA 110/13,8 kV ",12.444000000000001,0,12.677,1.44,10.634,0,12.605,1.508,12.677,12.444000000000001,12.444000000000001]
[null,null,null,"Central Tocopilla  110 kV - HT105 Transformador TR105 15 MVA 115/5 kV ",12.444000000000001,4.0000000000000001E-3,12.677,2E-3,10.634,4.0000000000000001E-3,12.605,4.0000000000000001E-3,12.677,12.674999999999999,12.674999999999999]
[null,null,null,"Central Tocopilla  110 kV - HT141 Transformador TR141 30 MVA 115/5 kV ",12.444000000000001,4.0000000000000001E-3,12.677,8.0000000000000002E-3,10.634,4.0000000000000001E-3,12.605,7.0000000000000001E-3,12.677,12.669,12.669]
[null,"S/E Yungay 154kV",154,"S/E Yungay 154kV 154 kV - ATG1 Transformador TR01 70MVA 154/11,5kV",19.532,1.127,20.052,1.5920000000000001,16.437000000000001,0.91100000000000003,20.030999999999999,1.486,20.052,18.544999999999998,18.544999999999998]
[null,null,null,"S/E Yungay 154kV 154 kV - ATG2 Transformador TR02 70MVA 154/11,5kV",19.532,1.127,20.052,1.5920000000000001,16.437000000000001,0.91100000000000003,20.030999999999999,1.486,20.052,18.544999999999998,18.544999999999998]
[null,null,null,"S/E Yungay 154kV 154 kV - ATG3 Transformador TR03 70MVA 154/11,5kV",19.532,1.127,20.052,1.5920000000000001,16.437000000000001,0.91100000000000003,20.030999999999999,1.486,20.052,18.544999999999998,18.544999999999998]
[null,null,null,"S/E Yungay 154kV 154 kV - ATG4 Transformador TR04 70MVA 154/11,5kV",19.532,0.80400000000000005,20.052,1.1180000000000001,16.437000000000001,0.68799999999999994,20.030999999999999,1.032,20.052,18.998999999999999,18.998999999999999]
[null,"Centro ",110,"Centro  110 kV - H1 Línea 110 kV Centro - Esmeralda ",8.6980000000000004,8.6980000000000004,8.6359999999999992,8.6370000000000005,7.4189999999999996,7.4189999999999996,8.7370000000000001,8.7370000000000001,8.7370000000000001,0,8.7370000000000001]
[null,null,null,"Centro  110 kV - HT1 Transformador TR1 110/13,8 kV ",8.6980000000000004,0,8.6359999999999992,0,7.4189999999999996,0,8.7370000000000001,0,8.7370000000000001,8.7370000000000001,8.7370000000000001]
[null,null,null,"Centro  110 kV - HT1 Transformador TR2 110/23 kV ",8.6980000000000004,0,8.6359999999999992,0,7.4189999999999996,0,8.7370000000000001,0,8.7370000000000001,8.7370000000000001,8.7370000000000001]
[null,"Cerrillos ",110,"Cerrillos  110 kV - H2 Línea 110 kV Cerrillos - Los Loros 1",6.625,0,5.8970000000000002,0.379,5.72,0,6.399,0.34300000000000003,6.625,6.625,6.625]
[null,null,null,"Cerrillos  110 kV - HX Línea 110 kV Cerrillos - Atacama Kozán",6.625,3.5009999999999999,5.8970000000000002,2.8650000000000002,5.72,3.0230000000000001,6.399,3.2669999999999999,6.625,3.1320000000000001,3.5009999999999999]
[null,null,null,"Cerrillos  110 kV - HT1 Transformador T1 30/25/20 MVA 110/24-13,8 kV ",6.625,0,5.8970000000000002,0,5.72,0,6.399,0,6.625,6.625,6.625]
[null,"Cerro Calera ",110,"Cerro Calera  110 kV - HT Transformador TR 30 MVA 110/60/12 kV ",14.555,0.28199999999999997,11.422000000000001,0.47899999999999998,12.57,0.24399999999999999,13.552,0.39100000000000001,14.555,14.273,14.273]
[null,"Cerro Colorado ",110,"Cerro Colorado  110 kV - HL Línea 110 kV Cerro Colorado - Pozo Almonte ",1.788,1.788,1.1850000000000001,1.1870000000000001,1.5289999999999999,1.5289999999999999,1.627,1.627,1.788,0,1.788]
[null,null,null,"Cerro Colorado  110 kV - HT1 Transformador TR1 46/30 MVA 110/12 kV ",1.788,0,1.1850000000000001,0,1.5289999999999999,0,1.627,0,1.788,1.788,1.788]
[null,null,null,"Cerro Colorado  110 kV - HT2 Transformador TR2 46/30 MVA 110/12 kV ",1.788,0,1.1850000000000001,0,1.5289999999999999,0,1.627,0,1.788,1.788,1.788]
[null,"Cerro Dragón ",110,"Cerro Dragón  110 kV - HT1 Transformador Trafo1 110/13.8 kV 33/25 MVA ",3.5489999999999999,8.3000000000000004E-2,3.66,0.06,3.0329999999999999,7.3999999999999996E-2,3.65,7.5999999999999998E-2,3.66,3.6,3.6]
[null,"Cerro Navia",110,"Cerro Navia 110 kV - HT3 AutoTransformador ATR03 399 MVA 220/110/13,8 kV ",61.923999999999999,8.6769999999999996,66.584000000000003,12.962,53.570999999999998,7.5259999999999998,65.378,11.725,66.584000000000003,53.652999999999999,53.652999999999999]
[null,null,null,"Cerro Navia 110 kV - AT2 AutoTransformador ATR02 400 MVA 220/110/13,2 kV ",61.923999999999999,8.6769999999999996,66.584000000000003,12.962,53.570999999999998,7.5259999999999998,65.378,11.725,66.584000000000003,53.652999999999999,53.652999999999999]
[null,null,null,"Cerro Navia 110 kV - HT5 AutoTransformador ATR5 400 MVA 220/110/13,2 kV ",61.923999999999999,8.69,66.584000000000003,11.055999999999999,53.570999999999998,7.5369999999999999,65.378,10.208,66.584000000000003,55.528000000000006,55.528000000000006]
[null,"Cerro Navia (Enel)",110,"Cerro Navia (Enel) 110 kV - H2 Línea 110 kV Cerro Navia - Renca 2",61.923999999999999,8.2799999999999994,66.584000000000003,6.9189999999999996,53.570999999999998,7.1239999999999997,65.378,7.6349999999999998,66.584000000000003,59.665000000000006,59.665000000000006]
[null,null,null,"Cerro Navia (Enel) 110 kV - H11 Línea 110 kV Cerro Navia - Lo Aguirre 1",61.923999999999999,0.104,66.584000000000003,7.5999999999999998E-2,53.570999999999998,9.1999999999999998E-2,65.378,9.2999999999999999E-2,66.584000000000003,66.50800000000001,66.50800000000001]
[null,null,null,"Cerro Navia (Enel) 110 kV - H10 Línea 110 kV Cerro Navia - San Pablo",61.923999999999999,0.10100000000000001,66.584000000000003,7.3999999999999996E-2,53.570999999999998,8.8999999999999996E-2,65.378,0.09,66.584000000000003,66.510000000000005,66.510000000000005]
[null,null,null,"Cerro Navia (Enel) 110 kV - H3 Línea 110 kV Cerro Navia - TO Los Libertadores C1",61.923999999999999,1.55,66.584000000000003,1.339,53.570999999999998,1.339,65.378,1.4450000000000001,66.584000000000003,65.245000000000005,65.245000000000005]
[null,null,null,"Cerro Navia (Enel) 110 kV - H4 Línea 110 kV Cerro Navia - TO Los Libertadores C2",61.923999999999999,1.55,66.584000000000003,1.339,53.570999999999998,1.339,65.378,1.4450000000000001,66.584000000000003,65.245000000000005,65.245000000000005]
[null,null,null,"Cerro Navia (Enel) 110 kV - H5 Línea 110 kV Cerro Navia - San Cristóbal 1",61.923999999999999,3.391,66.584000000000003,2.706,53.570999999999998,2.9380000000000002,65.378,3.089,66.584000000000003,63.878,63.878]
[null,null,null,"Cerro Navia (Enel) 110 kV - H6 Línea 110 kV Cerro Navia - San Cristóbal 2",61.923999999999999,3.391,66.584000000000003,2.706,53.570999999999998,2.9380000000000002,65.378,3.089,66.584000000000003,63.878,63.878]
[null,null,null,"Cerro Navia (Enel) 110 kV - H7 Línea 110 kV Cerro Navia - Chena 1 ",61.923999999999999,4.6559999999999997,66.584000000000003,3.802,53.570999999999998,4.0359999999999996,65.378,4.2629999999999999,66.584000000000003,62.782000000000004,62.782000000000004]
[null,null,null,"Cerro Navia (Enel) 110 kV - H8 Línea 110 kV Cerro Navia - Chena 2 ",61.923999999999999,4.6559999999999997,66.584000000000003,3.802,53.570999999999998,4.0359999999999996,65.378,4.2629999999999999,66.584000000000003,62.782000000000004,62.782000000000004]
[null,null,null,"Cerro Navia (Enel) 110 kV - H1 Línea 110 kV Cerro Navia - Renca 1",61.923999999999999,8.2799999999999994,66.584000000000003,6.9189999999999996,53.570999999999998,7.1239999999999997,65.378,7.6349999999999998,66.584000000000003,59.665000000000006,59.665000000000006]
[null,"Chacabuco ",110,"Chacabuco  110 kV -  H1 Línea 110 kV Chacabuco - San Cristóbal/Cerro Navia 1 ",27.81,13.904999999999999,11.586,5.7930000000000001,24.079000000000001,12.039,24.497,12.249000000000001,27.81,13.904999999999999,13.904999999999999]
[null,null,null,"Chacabuco  110 kV -  H2 Línea 110 kV Chacabuco - San Cristóbal/Cerro Navia 2",27.81,13.904999999999999,11.586,5.7930000000000001,24.079000000000001,12.039,24.497,12.249000000000001,27.81,13.904999999999999,13.904999999999999]
[null,null,null,"Chacabuco  110 kV - HT6 Transformador TR06 25 MVA 110/23,5 kV ",27.81,0,11.586,0,24.079000000000001,0,24.497,0,27.81,27.81,27.81]
[null,null,null,"Chacabuco  110 kV - AT2 Transformador TR02 37,5 MVA 110/23,5 kV ",27.81,0,11.586,0,24.079000000000001,0,24.497,0,27.81,27.81,27.81]
[null,null,null,"Chacabuco  110 kV - AT4 Transformador TR04 22,4 MVA 110/12,5 kV ",27.81,0,11.586,0,24.079000000000001,0,24.497,0,27.81,27.81,27.81]
[null,null,null,"Chacabuco  110 kV - HT8 Transformador TR08 50 MVA 110/23,5 kV ",27.81,0,11.586,0,24.079000000000001,0,24.497,0,27.81,27.81,27.81]
[null,null,null,"Chacabuco  110 kV - HT7 Transformador TR07110/23,5 kV ",27.81,0,11.586,0,24.079000000000001,0,24.497,0,27.81,27.81,27.81]
[null,"Chacaya ",110,"Chacaya  110 kV - HT4 Transformador TR4 10 MVA 110/33 kV ",4.0019999999999998,0,4.6639999999999997,0,3.4620000000000002,0,4.476,0,4.6639999999999997,4.6639999999999997,4.6639999999999997]
[null,null,null,"Chacaya  110 kV - HT3 Transformador TR3 220/110/13,8 kV 80/100 MVA ",4.0019999999999998,3.57,4.6639999999999997,4.3289999999999997,3.4620000000000002,3.0880000000000001,4.476,4.109,4.6639999999999997,0.43199999999999994,4.3289999999999997]
[null,null,null,"Chacaya  110 kV - H3 Línea 110 kV Chacaya - GNL Mejillones ",4.0019999999999998,0,4.6639999999999997,0,3.4620000000000002,0,4.476,0,4.6639999999999997,4.6639999999999997,4.6639999999999997]
[null,null,null,"Chacaya  110 kV - H2 Línea 110 kV Chacaya - Muelle ",4.0019999999999998,0.434,4.6639999999999997,0.33700000000000002,3.4620000000000002,0.375,4.476,0.39,4.6639999999999997,4.327,4.327]
[null,"Chamy ",110,"Chamy  110 kV - H16 Línea 110 kV Chamy - Chuquicamata ",5.95,5.95,4.6079999999999997,4.6079999999999997,5.1120000000000001,5.1120000000000001,5.5019999999999998,5.5019999999999998,5.95,0,5.95]
[null,null,null,"Chamy  110 kV - HT1 Transformador TR01 37/33/25 MVA 100/13,8 kV ",5.95,0,4.6079999999999997,0,5.1120000000000001,0,5.5019999999999998,0,5.95,5.95,5.95]
[null,null,null,"Chamy  110 kV - Acoplador Barras Acoplador ",5.95,0,4.6079999999999997,0,5.1120000000000001,0,5.5019999999999998,0,5.95,5.95,5.95]
[null,"Charrua",154,"Charrua 154 kV - AT1 Transformador ATR Charrúa 220/154 kV N°1",22.536000000000001,11.211,24.149000000000001,12.36,18.928999999999998,9.6319999999999997,23.887,11.888,24.149000000000001,11.999000000000001,12.36]
[null,null,null,"Charrua 154 kV - A2 Línea 154 kV Charrua - Pueblo Seco",22.536000000000001,1.1950000000000001,24.149000000000001,1.1140000000000001,18.928999999999998,1.0309999999999999,23.887,1.1759999999999999,24.149000000000001,23.035,23.035]
[null,null,null,"Charrua 154 kV - ACE1 Banco Condensador Charrua 154 kV 1",22.536000000000001,0,24.149000000000001,0,18.928999999999998,0,23.887,0,24.149000000000001,24.149000000000001,24.149000000000001]
[null,null,null,"Charrua 154 kV - A4 Línea 154 kV Charrúa - Yungay (Ex Campanario)",22.536000000000001,3.9990000000000001,24.149000000000001,4.7530000000000001,18.928999999999998,3.282,23.887,4.51,24.149000000000001,19.396000000000001,19.396000000000001]
[null,null,null,"Charrua 154 kV - A6 Línea 154 kV Charrúa - Chillán",22.536000000000001,0.51400000000000001,24.149000000000001,0.53800000000000003,18.928999999999998,0.44400000000000001,23.887,0.55300000000000005,24.149000000000001,23.611000000000001,23.611000000000001]
[null,null,null,"Charrua 154 kV - A7 Transformador Charrúa 154/69/13.8 kV N°2",22.536000000000001,0.80500000000000005,24.149000000000001,1.397,18.928999999999998,0.73099999999999998,23.887,1.3420000000000001,24.149000000000001,22.752000000000002,22.752000000000002]
[null,null,null,"Charrua 154 kV - A8 Línea 154kV Trupán - Charrúa",22.536000000000001,1.472,24.149000000000001,1.0049999999999999,18.928999999999998,0.96399999999999997,23.887,1.2370000000000001,24.149000000000001,23.144000000000002,23.144000000000002]
[null,null,null,"Charrua 154 kV - A9 Línea 154 kV Charrúa - Los Angeles",22.536000000000001,1.266,24.149000000000001,1.208,18.928999999999998,1.075,23.887,1.246,24.149000000000001,22.941000000000003,22.941000000000003]
[null,null,null,"Charrua 154 kV - A10 Línea 154 kV Charrúa - Concepción 1",22.536000000000001,2.2050000000000001,24.149000000000001,1.869,18.928999999999998,1.895,23.887,2.0670000000000002,24.149000000000001,22.28,22.28]
[null,"Chena ",110,"Chena  110 kV - A6 Línea 110 kV Chena - Ochagavía 1 ",53.241,10.538,54.436999999999998,8.0399999999999991,46.118000000000002,9.1210000000000004,54.664000000000001,9.5640000000000001,54.664000000000001,46.396999999999998,46.396999999999998]
[null,null,null,"Chena  110 kV - A5 Línea 110 kV Chena - Ochagavía 2",53.241,10.538,54.436999999999998,8.0399999999999991,46.118000000000002,9.1210000000000004,54.664000000000001,9.5640000000000001,54.664000000000001,46.396999999999998,46.396999999999998]
[null,null,null,"Chena  110 kV -  H3 Línea 110 kV Chena - Cerro Navia 1",53.241,6.47,54.436999999999998,4.9530000000000003,46.118000000000002,5.5970000000000004,54.664000000000001,5.8479999999999999,54.664000000000001,49.483999999999995,49.483999999999995]
[null,null,null,"Chena  110 kV -  H4 Línea 110 kV Chena - Cerro Navia 2",53.241,6.47,54.436999999999998,4.9530000000000003,46.118000000000002,5.5970000000000004,54.664000000000001,5.8479999999999999,54.664000000000001,49.483999999999995,49.483999999999995]
[null,null,null,"Chena  110 kV - HT1 Transformador TR01 400 MVA 220/110/13,8 kV ",53.241,9.6620000000000008,54.436999999999998,14.257,46.118000000000002,8.3840000000000003,54.664000000000001,12.577999999999999,54.664000000000001,43.579000000000001,43.579000000000001]
[null,null,null,"Chena  110 kV - CCE1A Banco de Condensadores 1",53.241,0,54.436999999999998,0,46.118000000000002,0,54.664000000000001,0,54.664000000000001,54.664000000000001,54.664000000000001]
[null,null,null,"Chena  110 kV - AT2 Transformador TR02 400 MVA 220/110/13,8 kV ",53.241,9.6630000000000003,54.436999999999998,14.263,46.118000000000002,8.3849999999999998,54.664000000000001,12.631,54.664000000000001,43.578000000000003,43.578000000000003]
[null,"Chillán",154,"Chillán 154 kV - AT3 Transformador Chillán TR3 75MVA 154/66 kV ",4.4809999999999999,1.419,3.641,1.482,3.8620000000000001,1.2250000000000001,4.266,1.466,4.4809999999999999,3.0619999999999998,3.0619999999999998]
[null,"Chiloé",110,"Chiloé 110 kV - HT1 Transformador Chiloe 90 MVA 220/110/23 kV",5.3380000000000001,2.379,5.9720000000000004,3.1619999999999999,4.2859999999999996,2.069,6.0880000000000001,3.0019999999999998,6.0880000000000001,3.0860000000000003,3.1619999999999999]
[null,null,null,"Chiloé 110 kV - H1 Línea 110 kV Chiloe - Ancud 1",5.3380000000000001,0.60399999999999998,5.9720000000000004,0.56699999999999995,4.2859999999999996,0.52500000000000002,6.0880000000000001,0.58699999999999997,6.0880000000000001,5.5010000000000003,5.5010000000000003]
[null,null,null,"Chiloé 110 kV - H2 Línea 110 kV Chiloe - Pid Pid/Dalcahue 1",5.3380000000000001,1.2729999999999999,5.9720000000000004,1.196,4.2859999999999996,1.109,6.0880000000000001,1.262,6.0880000000000001,4.8260000000000005,4.8260000000000005]
[null,null,null,"Chiloé 110 kV - H3 Línea 110 kV Chiloe - Degañ 1",5.3380000000000001,0.45800000000000002,5.9720000000000004,0.41099999999999998,4.2859999999999996,0.38900000000000001,6.0880000000000001,0.432,6.0880000000000001,5.6559999999999997,5.6559999999999997]
[null,null,null,"Chiloé 110 kV - H4 Línea 110 kV Chiloe - San Pedro 1",5.3380000000000001,0.70599999999999996,5.9720000000000004,0.70399999999999996,4.2859999999999996,0.32800000000000001,6.0880000000000001,0.91300000000000003,6.0880000000000001,5.2680000000000007,5.2680000000000007]
[null,null,null,"Chiloé 110 kV - HR1 Acoplador ",5.3380000000000001,0,5.9720000000000004,0,4.2859999999999996,0,6.0880000000000001,0,6.0880000000000001,6.0880000000000001,6.0880000000000001]
[null,"Chirre",110,"Chirre 110 kV -  En Barra",4.702,0,4.6139999999999999,0,4.1139999999999999,0,4.673,0,4.702,4.702,4.702]
[null,"Choapa ",110,"Choapa  110 kV - H4 Línea 110 kV Choapa - Illapel ",8.4979999999999993,1.119,9.423,0.95399999999999996,7.1859999999999999,0.96099999999999997,9.4529999999999994,1.077,9.4529999999999994,8.4689999999999994,8.4689999999999994]
[null,null,null,"Choapa  110 kV - H5 Línea 110 kV Choapa - Central Olivos ",8.4979999999999993,2.0299999999999998,9.423,2.3109999999999999,7.1859999999999999,1.5720000000000001,9.4529999999999994,2.2829999999999999,9.4529999999999994,7.17,7.17]
[null,null,null,"Choapa  110 kV - H1 Línea 110 kV Choapa - Quereo",8.4979999999999993,0,9.423,0,7.1859999999999999,0,9.4529999999999994,0,9.4529999999999994,9.4529999999999994,9.4529999999999994]
[null,null,null,"Choapa  110 kV - HT AutoTransformador ATR1 75/60 MVA 220/115/23 kV ",8.4979999999999993,2.2909999999999999,9.423,2.7480000000000002,7.1859999999999999,1.9930000000000001,9.4529999999999994,2.6059999999999999,9.4529999999999994,6.8469999999999995,6.8469999999999995]
[null,null,null,"Choapa  110 kV - HTX AutoTransformador ATR2 75/60 MVA 220/115/23 kV ",8.4979999999999993,2.2909999999999999,9.423,2.7480000000000002,7.1859999999999999,1.9930000000000001,9.4529999999999994,2.6059999999999999,9.4529999999999994,6.8469999999999995,6.8469999999999995]
[null,null,null,"Choapa  110 kV - H3 Línea 110 kV Choapa - Quinquimo ",8.4979999999999993,0.92900000000000005,9.423,0.78300000000000003,7.1859999999999999,0.80700000000000005,9.4529999999999994,0.89100000000000001,9.4529999999999994,8.64,8.64]
[null,"Chonchi",110,"Chonchi 110 kV - HT1 Transformador TR1 30-24 MVA 115.69/24 kV ",4.3579999999999997,0,4.4669999999999996,0,3.6779999999999999,0,4.4690000000000003,0,4.4690000000000003,4.4690000000000003,4.4690000000000003]
[null,null,null,"Chonchi 110 kV - HX Línea 220kV (energizada en 110kV) Gamboa - Chonchi",4.3579999999999997,3.1469999999999998,4.4669999999999996,3.2519999999999998,3.6779999999999999,2.6520000000000001,4.4690000000000003,3.1640000000000001,4.4690000000000003,1.3050000000000002,3.2519999999999998]
[null,null,null,"Chonchi 110 kV - H2 Línea 110 kV Chonchi - Quellon",4.3579999999999997,0.373,4.4669999999999996,0.26300000000000001,3.6779999999999999,0.32100000000000001,4.4690000000000003,0.32900000000000001,4.4690000000000003,4.2039999999999997,4.2039999999999997]
[null,"Chuquicamata",110,"Chuquicamata 100 kV - HATR1 Transformador ATR1 220/110/13.8",10.552,2.6949999999999998,12.411,3.7370000000000001,9.0090000000000003,2.2999999999999998,12.077999999999999,3.5529999999999999,12.411,8.6739999999999995,8.6739999999999995]
[null,null,null,"Chuquicamata 100 kV - HT2 Transformador ATR2 220/110/13.8",10.552,2.6949999999999998,12.411,3.7370000000000001,9.0090000000000003,2.2999999999999998,12.077999999999999,3.5529999999999999,12.411,8.6739999999999995,8.6739999999999995]
[null,null,null,"Chuquicamata 100 kV - HR Acoplador",10.552,0,12.411,0,9.0090000000000003,0,12.077999999999999,0,12.411,12.411,12.411]
[null,null,null,"Chuquicamata 100 kV - H16 Línea 110 kV Chuquicamata - Chamy 1",10.552,0,12.411,0,9.0090000000000003,0,12.077999999999999,0,12.411,12.411,12.411]
[null,null,null,"Chuquicamata 100 kV - H12  Línea 110 kV Chuquicamata - K1 1",10.552,0.56200000000000006,12.411,0.53100000000000003,9.0090000000000003,0.47899999999999998,12.077999999999999,0.55200000000000005,12.411,11.879999999999999,11.879999999999999]
[null,null,null,"Chuquicamata 100 kV - H10 Línea 110 kV Chuquicamata - 10 1",10.552,0.69599999999999995,12.411,0.69,9.0090000000000003,0.59299999999999997,12.077999999999999,0.70399999999999996,12.411,11.721,11.721]
[null,null,null,"Chuquicamata 100 kV - H11 Línea 110 kV Chuquicamata - 10A 1",10.552,0.59799999999999998,12.411,0.627,9.0090000000000003,0.51,12.077999999999999,0.61199999999999999,12.411,11.783999999999999,11.783999999999999]
[null,null,null,"Chuquicamata 100 kV - H13 Línea 110 kV Chuquicamata - KM6 1",10.552,1.1839999999999999,12.411,1.2989999999999999,9.0090000000000003,1.0089999999999999,12.077999999999999,1.266,12.411,11.112,11.112]
[null,null,null,"Chuquicamata 100 kV - H14 Línea 110 kV Chuquicamata - A 1",10.552,1.071,12.411,0.88400000000000001,9.0090000000000003,0.91700000000000004,12.077999999999999,0.98299999999999998,12.411,11.526999999999999,11.526999999999999]
[null,null,null,"Chuquicamata 100 kV - H15 Línea 110 kV Chuquicamata - A 2",10.552,1.071,12.411,0.92200000000000004,9.0090000000000003,0.91700000000000004,12.077999999999999,0.98499999999999999,12.411,11.488999999999999,11.488999999999999]
[null,"Chuschampis ",110,"Chuschampis  110 kV -  En Barra",3.7879999999999998,0,2.4500000000000002,0,3.2709999999999999,0,3.5489999999999999,0,3.7879999999999998,3.7879999999999998,3.7879999999999998]
[null,"Cipreses",154,"Cipreses 154 kV - A1 Línea 154 kV Cipreses - Itahue1/Curillinque",6.3280000000000003,2.44,6.0430000000000001,2.25,5.2039999999999997,2.1259999999999999,6.3440000000000003,2.3929999999999998,6.3440000000000003,3.9510000000000005,3.9510000000000005]
[null,null,null,"Cipreses 154 kV - A2 Línea 154 kV Cipreses - Itahue 2",6.3280000000000003,1.587,6.0430000000000001,1.2509999999999999,5.2039999999999997,1.379,6.3440000000000003,1.4670000000000001,6.3440000000000003,4.8770000000000007,4.8770000000000007]
[null,null,null,"Cipreses 154 kV - A3 Línea 154 kV Cipreses - Central Isla 1",6.3280000000000003,0.51100000000000001,6.0430000000000001,0.34300000000000003,5.2039999999999997,0.438,6.3440000000000003,0.45100000000000001,6.3440000000000003,5.8930000000000007,5.8930000000000007]
[null,null,null,"Cipreses 154 kV - A4 Línea 154 kV Cipreses - Central Isla 2",6.3280000000000003,0.51100000000000001,6.0430000000000001,0.34300000000000003,5.2039999999999997,0.438,6.3440000000000003,0.45100000000000001,6.3440000000000003,5.8930000000000007,5.8930000000000007]
[null,null,null,"Cipreses 154 kV - AT1 Transformador Cipreses TR01 32MVA 154/13,8 kV U1",6.3280000000000003,0.47199999999999998,6.0430000000000001,0.7,5.2039999999999997,0.31900000000000001,6.3440000000000003,0.67700000000000005,6.3440000000000003,5.8559999999999999,5.8559999999999999]
[null,null,null,"Cipreses 154 kV - AT2 Transformador Cipreses TR02 32MVA154/13.8 kV U2",6.3280000000000003,0.41299999999999998,6.0430000000000001,0.58799999999999997,5.2039999999999997,0.25900000000000001,6.3440000000000003,0.58799999999999997,6.3440000000000003,5.915,5.915]
[null,null,null,"Cipreses 154 kV - AT3 Transformador Cipreses TR03 161/13.8/6.9 kV U3",6.3280000000000003,0.41299999999999998,6.0430000000000001,0.58799999999999997,5.2039999999999997,0.25900000000000001,6.3440000000000003,0.58799999999999997,6.3440000000000003,5.915,5.915]
[null,"Club Hípico ",110,"Club Hípico  110 kV - H1 Línea 110 kV Club Hípico - Ochagavia/Florida 1 ",43.917000000000002,21.957999999999998,23.876999999999999,11.938000000000001,38.015999999999998,19.007999999999999,38.932000000000002,19.466000000000001,43.917000000000002,21.959000000000003,21.959000000000003]
[null,null,null,"Club Hípico  110 kV - H2 Línea 110 kV Club Hípico - Ochagavia/Florida 2",43.917000000000002,21.957999999999998,23.876999999999999,11.938000000000001,38.015999999999998,19.007999999999999,38.932000000000002,19.466000000000001,43.917000000000002,21.959000000000003,21.959000000000003]
[null,null,null,"Club Hípico  110 kV - HT3 Transformador TR3 25 MVA 110/12,5 kV ",43.917000000000002,0,23.876999999999999,0,38.015999999999998,0,38.932000000000002,0,43.917000000000002,43.917000000000002,43.917000000000002]
[null,"Codelco Ventanas 1 ",110,"Codelco Ventanas 1  110 kV - A12 Transformador TR1 ",18.158000000000001,0,19.811,0.10100000000000001,15.728999999999999,0,19.216999999999999,0.111,19.811,19.71,19.71]
[null,null,null,"Codelco Ventanas 1  110 kV - A22 Transformador TR2 ",18.158000000000001,0,19.811,0.191,15.728999999999999,0,19.216999999999999,0.21,19.811,19.62,19.62]
[null,"Codelco Ventanas 2 ",110,"Codelco Ventanas 2  110 kV - HT3 Transformador TR3",16.283999999999999,0,17.739999999999998,0.122,14.105,0,17.161999999999999,0.13400000000000001,17.739999999999998,17.617999999999999,17.617999999999999]
[null,null,null,"Codelco Ventanas 2  110 kV - HT4 Transformador TR4",16.283999999999999,0,17.739999999999998,0.19700000000000001,14.105,0,17.161999999999999,0.216,17.739999999999998,17.542999999999999,17.542999999999999]
[null,null,null,"Codelco Ventanas 2  110 kV - HT5 Transformador TR5",16.283999999999999,0,17.739999999999998,0.25600000000000001,14.105,0,17.161999999999999,0.28100000000000003,17.739999999999998,17.483999999999998,17.483999999999998]
[null,"Colaco ",110,"Colaco  110 kV - HT1 Transformador TR1 110/24 kV 16 MVA ",4.4249999999999998,0,4.2039999999999997,0,3.8029999999999999,0,4.3280000000000003,0,4.4249999999999998,4.4249999999999998,4.4249999999999998]
[null,null,null,"Colaco  110 kV - H1 Línea 110 kV Colaco - Pargua ",4.4249999999999998,2.09,4.2039999999999997,2.1779999999999999,3.8029999999999999,1.784,4.3280000000000003,2.125,4.4249999999999998,2.335,2.335]
[null,"Colón ",110,"Colón  110 kV -  H1 Línea 110 kV Colón - Minero 1 ",18.870999999999999,9.4350000000000005,20.306999999999999,10.153,16.417999999999999,8.2089999999999996,19.704000000000001,9.8520000000000003,20.306999999999999,10.153999999999998,10.153999999999998]
[null,null,null,"Colón  110 kV -  H2 Línea 110 kV Colón - Minero 2",18.870999999999999,9.4350000000000005,20.306999999999999,10.153,16.417999999999999,8.2089999999999996,19.704000000000001,9.8520000000000003,20.306999999999999,10.153999999999998,10.153999999999998]
[null,null,null,"Colón  110 kV - HT1 Transformador TR1 20 MVA 110/13,8/4,16 kV ",18.870999999999999,0,20.306999999999999,0,16.417999999999999,0,19.704000000000001,0,20.306999999999999,20.306999999999999,20.306999999999999]
[null,null,null,"Colón  110 kV - HT2 Transformador TR2 20 MVA 110/13,8/4,16 kV ",18.870999999999999,0,20.306999999999999,0,16.417999999999999,0,19.704000000000001,0,20.306999999999999,20.306999999999999,20.306999999999999]
[null,null,null,"Colón  110 kV - HT3 Transformador TR3 20 MVA 110/13,8/4,16 kV ",18.870999999999999,0,20.306999999999999,0,16.417999999999999,0,19.704000000000001,0,20.306999999999999,20.306999999999999,20.306999999999999]
[null,null,null,"Colón  110 kV - HT4 Transformador TR4 20 MVA 110/13,8/4,16 kV ",18.870999999999999,0,20.306999999999999,0,16.417999999999999,0,19.704000000000001,0,20.306999999999999,20.306999999999999,20.306999999999999]
[null,"Concepción",154,"Concepción 154 kV - AT1 Transformador Concepción TR1 30MVA 154/66 kV N°1",15.52,0.35799999999999998,20.85,0.79500000000000004,13.318,0.307,21.507000000000001,0.91700000000000004,21.507000000000001,20.59,20.59]
[null,null,null,"Concepción 154 kV - AT2 Transformador Concepción TR2 56MVA 154/66 kV N°2",15.52,0.45,20.85,0.56299999999999994,13.318,0.38700000000000001,21.507000000000001,0.56499999999999995,21.507000000000001,20.942,20.942]
[null,null,null,"Concepción 154 kV - AT3 Transformador Concepción TR3 56MVA154/66 kV N°3",15.52,0.45900000000000002,20.85,0.67600000000000005,13.318,0.39400000000000002,21.507000000000001,0.69699999999999995,21.507000000000001,20.810000000000002,20.810000000000002]
[null,null,null,"Concepción 154 kV - AT7 Transformador Concepción ATR7 261MVA 225/161/13.2 kV N°7",15.52,3.7970000000000002,20.85,8.6370000000000005,13.318,3.27,21.507000000000001,10.202,21.507000000000001,12.213000000000001,12.213000000000001]
[null,null,null,"Concepción 154 kV - A3 Línea 154 kV Concepción - San Vicente 1",15.52,3.2930000000000001,20.85,3.3109999999999999,13.318,2.8180000000000001,21.507000000000001,3.3010000000000002,21.507000000000001,18.206000000000003,18.206000000000003]
[null,null,null,"Concepción 154 kV - A4 Línea 154 kV Concepción - Charrúa",15.52,2.5049999999999999,20.85,2.335,13.318,2.1509999999999998,21.507000000000001,2.42,21.507000000000001,19.087000000000003,19.087000000000003]
[null,null,null,"Concepción 154 kV - A6 Línea 154 kV Concepción - San Vicente 2",15.52,3.2930000000000001,20.85,3.3109999999999999,13.318,2.8180000000000001,21.507000000000001,3.3010000000000002,21.507000000000001,18.206000000000003,18.206000000000003]
[null,null,null,"Concepción 154 kV - A7 Línea 154 kV Concepción - Alonso de Ribera",15.52,1.381,20.85,1.238,13.318,1.1870000000000001,21.507000000000001,1.304,21.507000000000001,20.203000000000003,20.203000000000003]
[null,"Concon ",110,"Concon  110 kV - H3 Línea 110 kV Concon - Tap Off Achupallas/Reñaca ",22.106000000000002,2.706,19.600999999999999,2.0510000000000002,19.268999999999998,2.3420000000000001,21.331,2.5739999999999998,22.106000000000002,19.400000000000002,19.400000000000002]
[null,null,null,"Concon  110 kV - HT1 Transformador TR1 25 MVA 110/12 kV ",22.106000000000002,4.9000000000000002E-2,19.600999999999999,2.9000000000000001E-2,19.268999999999998,4.2000000000000003E-2,21.331,4.2000000000000003E-2,22.106000000000002,22.057000000000002,22.057000000000002]
[null,null,null,"Concon  110 kV - HT2 Transformador TR2 25 MVA 110/12 kV  ",22.106000000000002,4.9000000000000002E-2,19.600999999999999,2.9000000000000001E-2,19.268999999999998,4.2000000000000003E-2,21.331,4.2999999999999997E-2,22.106000000000002,22.057000000000002,22.057000000000002]
[null,null,null,"Concon  110 kV - H4 Línea 110 kV Concon - Bosquemar ",22.106000000000002,1.087,19.600999999999999,0.77900000000000003,19.268999999999998,0.94,21.331,1.002,22.106000000000002,21.019000000000002,21.019000000000002]
[null,"Cóndores ",110,"Cóndores  110 kV - HT1 Transformador TR01 195/195/39 MVA 220/115/13,8 kV ",4.1100000000000003,4.0279999999999996,4.8959999999999999,4.827,3.5030000000000001,3.43,4.7709999999999999,4.7039999999999997,4.8959999999999999,8.2000000000000739E-2,4.827]
[null,null,null,"Cóndores  110 kV - H1 Línea 110 kV Cóndores - Cerro Dragón/Alto Hospicio ",4.1100000000000003,8.2000000000000003E-2,4.8959999999999999,7.0000000000000007E-2,3.5030000000000001,7.3999999999999996E-2,4.7709999999999999,7.4999999999999997E-2,4.8959999999999999,4.8259999999999996,4.8259999999999996]
[null,null,null,"Cóndores  110 kV - H3 Línea 110 kV Cóndores - Pacífico ",4.1100000000000003,0,4.8959999999999999,0,3.5030000000000001,0,4.7709999999999999,0,4.8959999999999999,4.8959999999999999,4.8959999999999999]
[null,null,null,"Cóndores  110 kV - H2 Línea 110 kV Cóndores - Palafitos ",4.1100000000000003,0,4.8959999999999999,0,3.5030000000000001,0,4.7709999999999999,0,4.8959999999999999,4.8959999999999999,4.8959999999999999]
[null,"Convento Viejo",154,"Convento Viejo 154 kV - A3 Transformador Convento Viejo TR01 20MVA 154/66 kV ",11.353999999999999,0.189,8.2899999999999991,0.61899999999999999,9.8510000000000009,0.157,10.429,0.46400000000000002,11.353999999999999,11.164999999999999,11.164999999999999]
[null,null,null,"Convento Viejo 154 kV - A1 Línea 154 kV Convento Viejo - Itahue",11.353999999999999,6.3150000000000004,8.2899999999999991,4.1970000000000001,9.8510000000000009,5.4539999999999997,10.429,5.67,11.353999999999999,5.0389999999999988,6.3150000000000004]
[null,null,null,"Convento Viejo 154 kV - A2 Línea 154 kV Convento Viejo - Tinguiririca",11.353999999999999,4.8520000000000003,8.2899999999999991,3.4780000000000002,9.8510000000000009,4.24,10.429,4.4409999999999998,11.353999999999999,6.5019999999999989,6.5019999999999989]
[null,"Copayapu ",110,"Copayapu  110 kV - H1 Línea 110 kV Copayapu - Galleguillos ",10.111000000000001,0.01,11.446999999999999,1.0999999999999999E-2,8.7149999999999999,8.9999999999999993E-3,11.166,0.01,11.446999999999999,11.436,11.436]
[null,null,null,"Copayapu  110 kV - HX1 Línea 110 kV Copayapu - Copiapó",10.111000000000001,8.9999999999999993E-3,11.446999999999999,0.01,8.7149999999999999,7.0000000000000001E-3,11.166,0.01,11.446999999999999,11.436999999999999,11.436999999999999]
[null,null,null,"Copayapu  110 kV - HX2 Línea 110 kV Copayapu - Cardones C2",10.111000000000001,2.7040000000000002,11.446999999999999,3.4649999999999999,8.7149999999999999,2.331,11.166,3.2770000000000001,11.446999999999999,7.9819999999999993,7.9819999999999993]
[null,null,null,"Copayapu  110 kV - H2 Línea 110 kV Copayapu - Cardones ",10.111000000000001,5.1239999999999997,11.446999999999999,5.7640000000000002,8.7149999999999999,4.4169999999999998,11.166,5.6159999999999997,11.446999999999999,5.6829999999999989,5.7640000000000002]
[null,null,null,"Copayapu  110 kV - H3 Línea 110 kV Copayapu - Tierra Amarilla ",10.111000000000001,1.4810000000000001,11.446999999999999,1.407,8.7149999999999999,1.2749999999999999,11.166,1.4550000000000001,11.446999999999999,10.039999999999999,10.039999999999999]
[null,null,null,"Copayapu  110 kV - H4 Línea 110 kV Copayapu - Cerrillos ",10.111000000000001,0.81100000000000005,11.446999999999999,0.81899999999999995,8.7149999999999999,0.69899999999999995,11.166,0.81399999999999995,11.446999999999999,10.628,10.628]
[null,"Copiapó ",110,"Copiapó  110 kV - H1 Línea 110 kV Copayapu - Copiapó",5.8019999999999996,4.3159999999999998,4.7889999999999997,3.56,5.0119999999999996,3.7280000000000002,5.5069999999999997,4.1319999999999997,5.8019999999999996,1.4859999999999998,4.3159999999999998]
[null,null,null,"Copiapó  110 kV - H2 Línea 110 kV Copiapó - Hernán Fuentes ",5.8019999999999996,1.504,4.7889999999999997,1.2370000000000001,5.0119999999999996,1.2989999999999999,5.5069999999999997,1.3879999999999999,5.8019999999999996,4.298,4.298]
[null,null,null,"Copiapó  110 kV - HT3 Transformador T3 24/20/16 MVA 110/24-13,8 kV ",5.8019999999999996,0,4.7889999999999997,0,5.0119999999999996,0,5.5069999999999997,0,5.8019999999999996,5.8019999999999996,5.8019999999999996]
[null,null,null,"Copiapó  110 kV - HT4 Transformador T4 25/20/16 MVA 110/24-13,8 kV ",5.8019999999999996,0,4.7889999999999997,0,5.0119999999999996,0,5.5069999999999997,0,5.8019999999999996,5.8019999999999996,5.8019999999999996]
[null,"Copihues ",110,"Copihues  110 kV - H1 Línea 110 kV Copihues - Aihuapi ",3.0510000000000002,2.254,3.0939999999999999,1.871,2.6859999999999999,1.97,3.2269999999999999,2.1680000000000001,3.2269999999999999,1.2229999999999999,2.254]
[null,null,null,"Copihues  110 kV - HT1 Transformador TR1 30 MVA 115/69/13,8 kV ",3.0510000000000002,0.442,3.0939999999999999,0.99199999999999999,2.6859999999999999,0.42099999999999999,3.2269999999999999,0.82,3.2269999999999999,2.609,2.609]
[null,null,null,"Copihues  110 kV - H2 Línea 110 kV Copihues - Central Correntoso",3.0510000000000002,0.378,3.0939999999999999,0.252,2.6859999999999999,0.32500000000000001,3.2269999999999999,0.33900000000000002,3.2269999999999999,2.8879999999999999,2.8879999999999999]
[null,"Cordillera ",110,"Cordillera  110 kV - H1 Línea 110 kV Cordillera - Minero 1 ",17.585000000000001,8.7929999999999993,18.074999999999999,9.0370000000000008,15.295999999999999,7.6479999999999997,17.914999999999999,8.9580000000000002,18.074999999999999,9.0379999999999985,9.0379999999999985]
[null,null,null,"Cordillera  110 kV - H2 Línea 110 kV Cordillera - Minero 2",17.585000000000001,8.7929999999999993,18.074999999999999,9.0370000000000008,15.295999999999999,7.6479999999999997,17.914999999999999,8.9580000000000002,18.074999999999999,9.0379999999999985,9.0379999999999985]
[null,null,null,"Cordillera  110 kV - HT39 Transformador TR39 110/33 kV",17.585000000000001,0,18.074999999999999,0,15.295999999999999,0,17.914999999999999,0,18.074999999999999,18.074999999999999,18.074999999999999]
[null,null,null,"Cordillera  110 kV - HT40 Transformador TR40 110/33 kV",17.585000000000001,0,18.074999999999999,0,15.295999999999999,0,17.914999999999999,0,18.074999999999999,18.074999999999999,18.074999999999999]
[null,null,null,"Cordillera  110 kV - HT41 Transformador TR41 110/33 kV",17.585000000000001,0,18.074999999999999,0,15.295999999999999,0,17.914999999999999,0,18.074999999999999,18.074999999999999,18.074999999999999]
[null,null,null,"Cordillera  110 kV - HT42 Transformador TR42 110/33 kV",17.585000000000001,0,18.074999999999999,0,15.295999999999999,0,17.914999999999999,0,18.074999999999999,18.074999999999999,18.074999999999999]
[null,null,null,"Cordillera  110 kV - HT43 Transformador TR43 110/13,8 kV",17.585000000000001,0,18.074999999999999,0,15.295999999999999,0,17.914999999999999,0,18.074999999999999,18.074999999999999,18.074999999999999]
[null,null,null,"Cordillera  110 kV - HT44 Transformador TR44 110/13,8 kV",17.585000000000001,0,18.074999999999999,0,15.295999999999999,0,17.914999999999999,0,18.074999999999999,18.074999999999999,18.074999999999999]
[null,null,null,"Cordillera  110 kV - HT45 Transformador TR46 110/33 kV",17.585000000000001,0,18.074999999999999,0,15.295999999999999,0,17.914999999999999,0,18.074999999999999,18.074999999999999,18.074999999999999]
[null,null,null,"Cordillera  110 kV - HT46 Transformador TR45 110/33 kV",17.585000000000001,0,18.074999999999999,0,15.295999999999999,0,17.914999999999999,0,18.074999999999999,18.074999999999999,18.074999999999999]
[null,null,null,"Cordillera  110 kV - HCE1 Condensador N°1",17.585000000000001,0,18.074999999999999,0,15.295999999999999,0,17.914999999999999,0,18.074999999999999,18.074999999999999,18.074999999999999]
[null,"Coronel",154,"Coronel 154 kV - AT3-4 Transformador Coronel TR4 60/60/20MVA 154/66/13.8 kV ",11.956,0.76800000000000002,14.065,0.75900000000000001,10.266,0.65800000000000003,13.58,0.80200000000000005,14.065,13.305999999999999,13.305999999999999]
[null,null,null,"Coronel 154 kV - AT5 Transformador Coronel TR5 40/56MVA 154/69/13.2 kV ",11.956,0.57999999999999996,14.065,0.86199999999999999,10.266,0.497,13.58,0.88200000000000001,14.065,13.202999999999999,13.202999999999999]
[null,null,null,"Coronel 154 kV - AT6 Transformador Coronel TR6 40/56MVA154/69/13.2 kV",11.956,0.46300000000000002,14.065,0.755,10.266,0.39700000000000002,13.58,0.77400000000000002,14.065,13.309999999999999,13.309999999999999]
[null,null,null,"Coronel 154 kV - A1 Línea 154 kV Coronel - Bocamina",11.956,9.5180000000000007,14.065,10.773,10.266,8.1760000000000002,13.58,10.260999999999999,14.065,3.3190000000000008,10.773]
[null,"Costanera ",110,"Costanera  110 kV -  En Barra",9.2539999999999996,0,6.3879999999999999,0,8.0269999999999992,0,8.8940000000000001,0,9.2539999999999996,9.2539999999999996,9.2539999999999996]
[null,"Cristalerías",110,"Cristalerías 110 kV - HT1  Línea 110 kV Cristalerías - Las Vegas ",12.717000000000001,12.717000000000001,8.4740000000000002,8.4740000000000002,10.958,10.958,11.834,11.834,12.717000000000001,0,12.717000000000001]
[null,"Cunco ",110,"Cunco  110 kV -  H1 Línea 110 kV Cunco - Río Toltén ",1.99,1.651,1.7070000000000001,1.242,1.7090000000000001,1.4279999999999999,1.887,1.508,1.99,0.46500000000000008,1.651]
[null,null,null,"Cunco  110 kV -  H2 Línea 110 kV Cunco - Melipeuco ",1.99,0.34,1.7070000000000001,0.46700000000000003,1.7090000000000001,0.28000000000000003,1.887,0.42299999999999999,1.99,1.65,1.65]
[null,null,null,"Cunco  110 kV - HT1 Transformador TR1 16 MVA 110/23 kV",1.99,0,1.7070000000000001,0,1.7090000000000001,0,1.887,0,1.99,1.99,1.99]
[null,"Dalcahue ",110,"Dalcahue  110 kV -  H1 Línea 110 kV Dalcahue - Chiloe ",4.5430000000000001,2.097,4.1420000000000003,1.774,3.782,1.6830000000000001,4.3600000000000003,1.9490000000000001,4.5430000000000001,2.4460000000000002,2.4460000000000002]
[null,null,null,"Dalcahue  110 kV -  H2 Línea 110 kV Dalcahue - Pid Pid ",4.5430000000000001,2.4489999999999998,4.1420000000000003,2.371,3.782,2.1040000000000001,4.3600000000000003,2.4119999999999999,4.5430000000000001,2.0940000000000003,2.4489999999999998]
[null,null,null,"Dalcahue  110 kV - HT1 Transformador TR1 110/23 kV",4.5430000000000001,0,4.1420000000000003,0,3.782,0,4.3600000000000003,0,4.5430000000000001,4.5430000000000001,4.5430000000000001]
[null,"Degañ ",110,"Degañ  110 kV - HT1  Transformador Degañ TR1 110/23 kV",5.3150000000000004,0.45800000000000002,5.9139999999999997,0.41099999999999998,4.2699999999999996,0.378,6.0170000000000003,0.432,6.0170000000000003,5.585,5.585]
[null,"Desalant",110,"Desalant 110 kV -  H1 Línea 110 kV Desalant - Mejillones/Antofagasta ",7.4550000000000001,7.4550000000000001,5.524,5.524,6.375,6.375,6.8419999999999996,6.8419999999999996,7.4550000000000001,0,7.4550000000000001]
[null,"Diego de Almagro",110,"Diego de Almagro 110 kV - HT1 Transformador TR1 28 MVA ",9.7249999999999996,0.52400000000000002,13.186999999999999,0.67500000000000004,8.3789999999999996,0.44900000000000001,13.448,0.66600000000000004,13.448,12.782,12.782]
[null,null,null,"Diego de Almagro 110 kV -  H5 Línea 110 kV Diego de Almagro - Central Javiera/Tal Tal (ELECDA)",9.7249999999999996,0,13.186999999999999,0.13700000000000001,8.3789999999999996,0,13.448,0.216,13.448,13.232000000000001,13.232000000000001]
[null,null,null,"Diego de Almagro 110 kV -  H3 Línea 110 kV Diego de Almagro - Llanta 2 ",9.7249999999999996,0,13.186999999999999,0,8.3789999999999996,0,13.448,0,13.448,13.448,13.448]
[null,null,null,"Diego de Almagro 110 kV - HT2 Transformador TR2 ",9.7249999999999996,0.52400000000000002,13.186999999999999,0.67500000000000004,8.3789999999999996,0.44900000000000001,13.448,0.66600000000000004,13.448,12.782,12.782]
[null,null,null,"Diego de Almagro 110 kV -  H1 Línea 110 kV Diego de Almagro - Central PV El Salvador",9.7249999999999996,0,13.186999999999999,1E-3,8.3789999999999996,0,13.448,1E-3,13.448,13.447000000000001,13.447000000000001]
[null,null,null,"Diego de Almagro 110 kV -  H2 Línea 110 kV Diego de Almagro - Llanta 1",9.7249999999999996,0,13.186999999999999,0,8.3789999999999996,0,13.448,0,13.448,13.448,13.448]
[null,null,null,"Diego de Almagro 110 kV - HT3 Autotransformador ATR3 120 MVA 220/110/13,8 kV ",9.7249999999999996,3.2229999999999999,13.186999999999999,5.84,8.3789999999999996,2.7850000000000001,13.448,6.4249999999999998,13.448,7.3469999999999995,7.3469999999999995]
[null,null,null,"Diego de Almagro 110 kV -  H8 Línea 110 kV Diego de Almagro - Central Emelda ",9.7249999999999996,1.429,13.186999999999999,1.6859999999999999,8.3789999999999996,1.226,13.448,1.694,13.448,11.754000000000001,11.754000000000001]
[null,null,null,"Diego de Almagro 110 kV -  H6 Línea 110 kV Diego de Almagro - Manto Verde ",9.7249999999999996,0,13.186999999999999,0,8.3789999999999996,0,13.448,0,13.448,13.448,13.448]
[null,null,null,"Diego de Almagro 110 kV -  H9 Línea 110 kV Diego de Almagro - Tap Off Chañares/El Salado",9.7249999999999996,0,13.186999999999999,0.14499999999999999,8.3789999999999996,0,13.448,0.22800000000000001,13.448,13.22,13.22]
[null,null,null,"Diego de Almagro 110 kV - HT4 Autotransformador ATR4 120/90 MVA 220/110/13,8 kV ",9.7249999999999996,3.2269999999999999,13.186999999999999,3.105,8.3789999999999996,2.7879999999999998,13.448,3.1629999999999998,13.448,10.285,10.285]
[null,null,null,"Diego de Almagro 110 kV -  H7 Línea 110 kV Diego de Almagro - Minera Franke",9.7249999999999996,0,13.186999999999999,0,8.3789999999999996,0,13.448,0,13.448,13.448,13.448]
[null,null,null,"Diego de Almagro 110 kV - H10 Línea 110 kV Diego de Almagro - Central Andes Generación ",9.7249999999999996,0.79700000000000004,13.186999999999999,0.92600000000000005,8.3789999999999996,0.68100000000000005,13.448,0.92500000000000004,13.448,12.523,12.523]
[null,"Dos Amigos ",110,"Dos Amigos  110 kV -  En Barra",2.9409999999999998,0,2.2770000000000001,0,2.54,0,2.8959999999999999,0,2.9409999999999998,2.9409999999999998,2.9409999999999998]
[null,"EB2",110,"EB2 110 kV - HT1 Transformador TR1 7,5MVA 110/4,16kV",3.528,0,2.2759999999999998,0,3.0510000000000002,0,3.214,0,3.528,3.528,3.528]
[null,"EKA Chile ",154,"EKA Chile  154 kV -  En Barra",13.69,0,14.593,0,11.75,0,14.35,0,14.593,14.593,14.593]
[null,"El Bato",110,"El Bato 110 kV - HX Línea 110kV El bato - Ventanas",25.446999999999999,25.446999999999999,29.228000000000002,29.228000000000002,22.047999999999998,22.047999999999998,28.045000000000002,28.045000000000002,29.228000000000002,0,29.228000000000002]
[null,null,null,"El Bato 110 kV - HTX Transformador 110/12kV",25.446999999999999,0,29.228000000000002,0,22.047999999999998,0,28.045000000000002,0,29.228000000000002,29.228000000000002,29.228000000000002]
[null,"El Cobre ",110,"El Cobre  110 kV -  H1 Línea 110 kV El Cobre - La Calera ",4.6970000000000001,4.6970000000000001,3.0569999999999999,3.0579999999999998,4.0640000000000001,4.0640000000000001,4.2809999999999997,4.282,4.6970000000000001,0,4.6970000000000001]
[null,"El Cobre (Codelco)",110,"El Cobre (Codelco) 110 kV -  H1 Línea 110 kV El Cobre (Codelco) - Minero 1",17.199000000000002,8.6,16.829999999999998,8.4149999999999991,14.959,7.4790000000000001,17.065000000000001,8.5329999999999995,17.199000000000002,8.599000000000002,8.6]
[null,null,null,"El Cobre (Codelco) 110 kV -  H2 Línea 110 kV El Cobre (Codelco) - Minero 2",17.199000000000002,8.6,16.829999999999998,8.4149999999999991,14.959,7.4790000000000001,17.065000000000001,8.5329999999999995,17.199000000000002,8.599000000000002,8.6]
[null,null,null,"El Cobre (Codelco) 110 kV - HT1 Transformador TR3 110/13,8 kV ",17.199000000000002,0,16.829999999999998,0,14.959,0,17.065000000000001,0,17.199000000000002,17.199000000000002,17.199000000000002]
[null,null,null,"El Cobre (Codelco) 110 kV - HT2 Transformador TR4 110/13,8 kV ",17.199000000000002,0,16.829999999999998,0,14.959,0,17.065000000000001,0,17.199000000000002,17.199000000000002,17.199000000000002]
[null,null,null,"El Cobre (Codelco) 110 kV - HT3 Transformador TR2 110/13,8 kV ",17.199000000000002,0,16.829999999999998,0,14.959,0,17.065000000000001,0,17.199000000000002,17.199000000000002,17.199000000000002]
[null,null,null,"El Cobre (Codelco) 110 kV - HT4 Transformador TR1 110/13,8 kV ",17.199000000000002,0,16.829999999999998,0,14.959,0,17.065000000000001,0,17.199000000000002,17.199000000000002,17.199000000000002]
[null,null,null,"El Cobre (Codelco) 110 kV - HT7 Transformador T7 40-45-50MVA, 110/13,8kV",17.199000000000002,0,16.829999999999998,0,14.959,0,17.065000000000001,0,17.199000000000002,17.199000000000002,17.199000000000002]
[null,null,null,"El Cobre (Codelco) 110 kV - HT8 Transformador T8 40-45-50MVA, 110/13,8kV",17.199000000000002,0,16.829999999999998,0,14.959,0,17.065000000000001,0,17.199000000000002,17.199000000000002,17.199000000000002]
[null,null,null,"El Cobre (Codelco) 110 kV - T9 Transformador T9 40-45-50MVA, 110/13,8kV",17.199000000000002,0,16.829999999999998,0,14.959,0,17.065000000000001,0,17.199000000000002,17.199000000000002,17.199000000000002]
[null,"El Empalme ",110,"El Empalme  110 kV -  H1 Línea 110 kV El Empalme - Molinos (Enlasa)",4.16,2.4359999999999999,3.4590000000000001,1.9650000000000001,3.5840000000000001,2.105,3.8919999999999999,2.258,4.16,1.7240000000000002,2.4359999999999999]
[null,null,null,"El Empalme  110 kV -  H2 Línea 110kV Ilique - El Empalme",4.16,0,3.4590000000000001,0,3.5840000000000001,0,3.8919999999999999,0,4.16,4.16,4.16]
[null,null,null,"El Empalme  110 kV -  H3 Línea 110 kV El Empalme - Colaco",4.16,1.724,3.4590000000000001,1.494,3.5840000000000001,1.48,3.8919999999999999,1.637,4.16,2.4359999999999999,2.4359999999999999]
[null,null,null,"El Empalme  110 kV - HT1 Transformador TR1 16/11 MVA 115/24 kV ",4.16,0,3.4590000000000001,0,3.5840000000000001,0,3.8919999999999999,0,4.16,4.16,4.16]
[null,"El Espino",110,"El Espino 110 kV - HX1 Línea 110kV El Espino-Combarbalá",3.7959999999999998,2.0880000000000001,2.952,1.7430000000000001,3.2330000000000001,1.754,3.6349999999999998,2.0329999999999999,3.7959999999999998,1.7079999999999997,2.0880000000000001]
[null,null,null,"El Espino 110 kV - HX2 Línea 110kV Illapel - El Espino",3.7959999999999998,1.7110000000000001,2.952,1.212,3.2330000000000001,1.4810000000000001,3.6349999999999998,1.6040000000000001,3.7959999999999998,2.085,2.085]
[null,"El Lince",110,"El Lince 110 kV - HT  Línea 110 kV El Lince - Mejillones ",1.78,1.78,1.0169999999999999,1.0189999999999999,1.5349999999999999,1.5349999999999999,1.6180000000000001,1.619,1.78,0,1.78]
[null,"El Peñón ",110,"El Peñón  110 kV - HT1 Transformador T1 30/24/18 MVA 115/25 kV ",9.3320000000000007,0,7.4240000000000004,0,7.9850000000000003,0,8.8149999999999995,0,9.3320000000000007,9.3320000000000007,9.3320000000000007]
[null,null,null,"El Peñón  110 kV -  H3 Línea 110 kV El Peñón -  Minera Teck CDA",9.3320000000000007,0,7.4240000000000004,1E-3,7.9850000000000003,0,8.8149999999999995,1E-3,9.3320000000000007,9.3320000000000007,9.3320000000000007]
[null,null,null,"El Peñón  110 kV -  H1 Línea 110 kV El Peñón - La Ruca C1 ",9.3320000000000007,0.66100000000000003,7.4240000000000004,0.55900000000000005,7.9850000000000003,0.56499999999999995,8.8149999999999995,0.66200000000000003,9.3320000000000007,8.6710000000000012,8.6710000000000012]
[null,null,null,"El Peñón  110 kV -  H2 Línea 110 kV El Peñón - Pan de Azúcar  ",9.3320000000000007,3.1829999999999998,7.4240000000000004,2.536,7.9850000000000003,2.76,8.8149999999999995,3.0179999999999998,9.3320000000000007,6.1490000000000009,6.1490000000000009]
[null,null,null,"El Peñón  110 kV -  H4 Línea 110 kV El Peñón - Central Las Piedras ",9.3320000000000007,1.7070000000000001,7.4240000000000004,0.876,7.9850000000000003,1.39,8.8149999999999995,1.4359999999999999,9.3320000000000007,7.6250000000000009,7.6250000000000009]
[null,null,null,"El Peñón  110 kV -  H5 Línea 110 kV El Peñón - La Ruca C2",9.3320000000000007,0.66600000000000004,7.4240000000000004,0.55600000000000005,7.9850000000000003,0.56899999999999995,8.8149999999999995,0.66,9.3320000000000007,8.6660000000000004,8.6660000000000004]
[null,null,null,"El Peñón  110 kV -  H7 Línea 110 kV El Peñón - Pan de Azúcar ",9.3320000000000007,3.1829999999999998,7.4240000000000004,2.536,7.9850000000000003,2.76,8.8149999999999995,3.0179999999999998,9.3320000000000007,6.1490000000000009,6.1490000000000009]
[null,null,null,"El Peñón  110 kV - HT3 Transformador TR3 30 MVA 110/69/13,8 kV ",9.3320000000000007,0,7.4240000000000004,0.41299999999999998,7.9850000000000003,0,8.8149999999999995,0.34899999999999998,9.3320000000000007,9.3320000000000007,9.3320000000000007]
[null,"El Romeral (CMP)",110,"El Romeral (CMP) 110 kV - L1 Línea 110 kV Romeral - Tap Off El Romeral ",3.9969999999999999,0,2.8839999999999999,0,3.4569999999999999,0,3.7930000000000001,0,3.9969999999999999,3.9969999999999999,3.9969999999999999]
[null,"El Salado ",110,"El Salado  110 kV - HT1 Transformador TR1 110/23 kV ",3.6549999999999998,0,2.4359999999999999,0,3.161,0,3.3450000000000002,0,3.6549999999999998,3.6549999999999998,3.6549999999999998]
[null,"El Salto ",110,"El Salto  110 kV - H1 Línea 110 kV El Salto - Los Almendros 1",35.875999999999998,5.3719999999999999,33.975999999999999,3.8959999999999999,31.068999999999999,4.6520000000000001,35.540999999999997,4.8289999999999997,35.875999999999998,30.711999999999996,30.711999999999996]
[null,null,null,"El Salto  110 kV - H2 Línea 110 kV El Salto - Los Almendros 2",35.875999999999998,5.3719999999999999,33.975999999999999,3.8959999999999999,31.068999999999999,4.6520000000000001,35.540999999999997,4.8289999999999997,35.875999999999998,30.711999999999996,30.711999999999996]
[null,null,null,"El Salto  110 kV - H5 Línea 110 kV El Salto - San Cristóbal 1 ",35.875999999999998,5.851,33.975999999999999,4.0720000000000001,31.068999999999999,5.0659999999999998,35.540999999999997,5.2430000000000003,35.875999999999998,30.297999999999995,30.297999999999995]
[null,null,null,"El Salto  110 kV - H6 Línea 110 kV El Salto - San Cristóbal 2",35.875999999999998,5.851,33.975999999999999,4.0720000000000001,31.068999999999999,5.0659999999999998,35.540999999999997,5.2430000000000003,35.875999999999998,30.297999999999995,30.297999999999995]
[null,null,null,"El Salto  110 kV - HT1 Transformador TR1 400 MVA 220/110/13,2 kV ",35.875999999999998,6.7530000000000001,33.975999999999999,9.0440000000000005,31.068999999999999,5.8479999999999999,35.540999999999997,8.0340000000000007,35.875999999999998,29.122999999999998,29.122999999999998]
[null,null,null,"El Salto  110 kV - HT2 Transformador TR2 400 MVA 220/110/13,2 kV ",35.875999999999998,6.7530000000000001,33.975999999999999,9.0440000000000005,31.068999999999999,5.8479999999999999,35.540999999999997,8.0340000000000007,35.875999999999998,29.122999999999998,29.122999999999998]
[null,null,null,"El Salto  110 kV - HCE Banco de CCEE 80 MVAr",35.875999999999998,0,33.975999999999999,0,31.068999999999999,0,35.540999999999997,0,35.875999999999998,35.875999999999998,35.875999999999998]
[null,"El Salvador ",110,"El Salvador  110 kV -  H1 Línea 110 kV El Salvador - Diego de Almagro",4.9279999999999999,1.7090000000000001,4.2770000000000001,1.38,4.26,1.4770000000000001,4.6660000000000004,1.53,4.9279999999999999,3.2189999999999999,3.2189999999999999]
[null,null,null,"El Salvador  110 kV -  H2 Línea 110 kV El Salvador  - Llanta 1",4.9279999999999999,1.585,4.2770000000000001,1.425,4.26,1.37,4.6660000000000004,1.5529999999999999,4.9279999999999999,3.343,3.343]
[null,null,null,"El Salvador  110 kV - HT3 Transformador TR3 20/15 MVA 110/12,5 kV ",4.9279999999999999,1.6E-2,4.2770000000000001,0.01,4.26,1.4E-2,4.6660000000000004,1.4E-2,4.9279999999999999,4.9119999999999999,4.9119999999999999]
[null,null,null,"El Salvador  110 kV - HT1 Transformador TR1 20/15 MVA 110/12,5 kV ",4.9279999999999999,3.2000000000000001E-2,4.2770000000000001,1.7999999999999999E-2,4.26,2.7E-2,4.6660000000000004,2.8000000000000001E-2,4.9279999999999999,4.8959999999999999,4.8959999999999999]
[null,null,null,"El Salvador  110 kV -  H3 Línea 110 kV El Salvador - Llanta 2",4.9279999999999999,1.651,4.2770000000000001,1.4770000000000001,4.26,1.427,4.6660000000000004,1.61,4.9279999999999999,3.2770000000000001,3.2770000000000001]
[null,null,null,"El Salvador  110 kV - HT2 Transformador TR2 20/15 MVA 110/12,5 kV ",4.9279999999999999,1.6E-2,4.2770000000000001,0.01,4.26,1.4E-2,4.6660000000000004,1.4E-2,4.9279999999999999,4.9119999999999999,4.9119999999999999]
[null,null,null,"El Salvador  110 kV - H4 Línea 110 kV El Salvador - Línea Lixiviación",4.9279999999999999,0,4.2770000000000001,0,4.26,0,4.6660000000000004,0,4.9279999999999999,4.9279999999999999,4.9279999999999999]
[null,"Esmeralda ",110,"Esmeralda  110 kV - HT1 Transformador ATR Esmeralda 220/110 kV",9.0120000000000005,3.5339999999999998,9.1579999999999995,4.4279999999999999,7.6820000000000004,3.0409999999999999,9.1910000000000007,4.1159999999999997,9.1910000000000007,5.4780000000000006,5.4780000000000006]
[null,null,null,"Esmeralda  110 kV -  H2 Línea 110 kV Esmeralda - Centro ",9.0120000000000005,0,9.1579999999999995,0,7.6820000000000004,0,9.1910000000000007,0,9.1910000000000007,9.1910000000000007,9.1910000000000007]
[null,null,null,"Esmeralda  110 kV -  H3 Línea 110kV Guardiamarina - Esmeralda",9.0120000000000005,2.1219999999999999,9.1579999999999995,1.7609999999999999,7.6820000000000004,1.81,9.1910000000000007,1.9670000000000001,9.1910000000000007,7.3969999999999994,7.3969999999999994]
[null,null,null,"Esmeralda  110 kV -  H1 Línea 110 kV Esmeralda - Sur",9.0120000000000005,0,9.1579999999999995,0,7.6820000000000004,0,9.1910000000000007,0,9.1910000000000007,9.1910000000000007,9.1910000000000007]
[null,null,null,"Esmeralda  110 kV -  H4 Línea 110 kV Esmeralda - Tap Off Uribe/Uribe ",9.0120000000000005,3.3740000000000001,9.1579999999999995,2.988,7.6820000000000004,2.847,9.1910000000000007,3.1480000000000001,9.1910000000000007,6.17,6.17]
[null,"Esperanza (HASA)",110,"Esperanza (HASA) 110 kV -  HT Transformador TR2 30 MVA 110/66 kV",26.419,7.4999999999999997E-2,22.896000000000001,0.34,22.675000000000001,6.5000000000000002E-2,25.030999999999999,0.28199999999999997,26.419,26.344000000000001,26.344000000000001]
[null,null,null,"Esperanza (HASA) 110 kV - H1 Línea 110 kV  Esperanza (HASA) - Río Aconcagua C1",26.419,6.1520000000000001,22.896000000000001,5.0090000000000003,22.675000000000001,5.35,25.030999999999999,5.6980000000000004,26.419,20.266999999999999,20.266999999999999]
[null,null,null,"Esperanza (HASA) 110 kV -  H2 Línea 110 kV  Esperanza (HASA) - Río Aconcagua C2",26.419,6.1520000000000001,22.896000000000001,5.0090000000000003,22.675000000000001,5.35,25.030999999999999,5.6980000000000004,26.419,20.266999999999999,20.266999999999999]
[null,"Estación de Bombeo Sierra Gorda N°1",110,"Estación de Bombeo Sierra Gorda N°1 110 kV - HT1  Transformador TR01 70/70/12 MVA 220/110/13,8 kV y Transformador TR Reserva 70/70/12 MVA 220/110/13,8 kV ",2.9239999999999999,2.9239999999999999,4.181,4.181,2.5339999999999998,2.5339999999999998,4.6100000000000003,4.6109999999999998,4.6100000000000003,0,4.6109999999999998]
[null,null,null,"Estación de Bombeo Sierra Gorda N°1 110 kV - HT2  Transformador TR02 37,5 MVA 110/6,9 kV ",2.9239999999999999,0,4.181,0,2.5339999999999998,0,4.6100000000000003,0,4.6100000000000003,4.6100000000000003,4.6100000000000003]
[null,null,null,"Estación de Bombeo Sierra Gorda N°1 110 kV - H3 Línea 110 kV Estación de Bombeo Sierra Gorda N° 1 - Estación de Bombeo Sierra Gorda N° 2",2.9239999999999999,0,4.181,0,2.5339999999999998,0,4.6100000000000003,1E-3,4.6100000000000003,4.609,4.609]
[null,"Estación de Bombeo Sierra Gorda N°2",110,"Estación de Bombeo Sierra Gorda N°2 110 kV - HT1 Transformador TR01 37,5 MVA 110/6,9 kV ",1.5780000000000001,0,1.4550000000000001,0,1.367,0,1.573,0,1.5780000000000001,1.5780000000000001,1.5780000000000001]
[null,"Fatima",154,"Fatima 154 kV - A1 Línea 154kV Fatima - Alto Jahuel C1",14.339,3.44,12.71,3.327,12.456,2.9849999999999999,13.706,3.3220000000000001,14.339,10.899000000000001,10.899000000000001]
[null,null,null,"Fatima 154 kV - A2 Línea 154kV Fatima - Alto Jahuel C2",14.339,3.44,12.71,3.327,12.456,2.9849999999999999,13.706,3.3220000000000001,14.339,10.899000000000001,10.899000000000001]
[null,null,null,"Fatima 154 kV - AX1 Línea 154kV Fatima - Tap Off Paine C1",14.339,3.222,12.71,2.2890000000000001,12.456,2.8029999999999999,13.706,2.9060000000000001,14.339,11.117000000000001,11.117000000000001]
[null,null,null,"Fatima 154 kV - AX2 Línea 154kV Fatima - Tap Off Paine C2",14.339,2.843,12.71,2.0659999999999998,12.456,2.4750000000000001,13.706,2.573,14.339,11.496,11.496]
[null,null,null,"Fatima 154 kV - AT3 Transformador Fatima 75MVA 154/66 kV",14.339,0.70499999999999996,12.71,0.41599999999999998,12.456,0.61099999999999999,13.706,0.61799999999999999,14.339,13.634,13.634]
[null,null,null,"Fatima 154 kV - ATX Transformador Fatima TR2 75MVA 154/66 kV",14.339,0.71499999999999997,12.71,1.2969999999999999,12.456,0.61899999999999999,13.706,1.1499999999999999,14.339,13.624000000000001,13.624000000000001]
[null,"Florida ",110,"Florida  110 kV -  H1 Línea 110 kV  Florida - Buin 1",38.237000000000002,5.0979999999999999,21.704999999999998,2.7639999999999998,33.119999999999997,4.4269999999999996,34.162999999999997,4.5350000000000001,38.237000000000002,33.139000000000003,33.139000000000003]
[null,null,null,"Florida  110 kV -  H2 Línea 110 kV  Florida - Buin 2",38.237000000000002,5.0979999999999999,21.704999999999998,2.7639999999999998,33.119999999999997,4.4269999999999996,34.162999999999997,4.5350000000000001,38.237000000000002,33.139000000000003,33.139000000000003]
[null,null,null,"Florida  110 kV -  H3 Línea 110 kV  Florida - Los Almendros 2",38.237000000000002,4.1470000000000002,21.704999999999998,2.2599999999999998,33.119999999999997,3.597,34.162999999999997,3.681,38.237000000000002,34.090000000000003,34.090000000000003]
[null,null,null,"Florida  110 kV -  H4 Línea 110 kV  Florida - Los Almendros 1",38.237000000000002,4.1470000000000002,21.704999999999998,2.2599999999999998,33.119999999999997,3.597,34.162999999999997,3.681,38.237000000000002,34.090000000000003,34.090000000000003]
[null,null,null,"Florida  110 kV -  H5 Línea 110 kV  Florida - Ochagavía 1 ",38.237000000000002,6.4390000000000001,21.704999999999998,3.18,33.119999999999997,5.5819999999999999,34.162999999999997,5.6559999999999997,38.237000000000002,31.798000000000002,31.798000000000002]
[null,null,null,"Florida  110 kV -  H6 Línea 110 kV  Florida - Ochagavía 2 ",38.237000000000002,6.4390000000000001,21.704999999999998,3.18,33.119999999999997,5.5819999999999999,34.162999999999997,5.6559999999999997,38.237000000000002,31.798000000000002,31.798000000000002]
[null,null,null,"Florida  110 kV - HT1 Transformador TR01 25 MVA 110/12 kV ",38.237000000000002,0.47,21.704999999999998,0.20300000000000001,33.119999999999997,0.46200000000000002,34.162999999999997,0.46100000000000002,38.237000000000002,37.767000000000003,37.767000000000003]
[null,null,null,"Florida  110 kV -  H7 Línea 110 kV  Florida - Las Vizcachas 1",38.237000000000002,3.12,21.704999999999998,2.3780000000000001,33.119999999999997,2.6520000000000001,34.162999999999997,2.9239999999999999,38.237000000000002,35.117000000000004,35.117000000000004]
[null,null,null,"Florida  110 kV -  H8 Línea 110 kV  Florida - Las Vizcachas 2",38.237000000000002,3.2930000000000001,21.704999999999998,2.722,33.119999999999997,2.8119999999999998,34.162999999999997,3.1379999999999999,38.237000000000002,34.944000000000003,34.944000000000003]
[null,"FPC",154,"FPC 154 kV - A1 acoplador ",12.5,0.26,12.63,0.18,10.73,0.23,12.89,0.24,12.89,12.65,12.65]
[null,"Fundición Chagres ",110,"Fundición Chagres  110 kV -  H2 Línea 110 kV Fundición Chagres - San Felipe 1\nLínea 110 kV Fundición Chagres - Esperanza (HASA) 1",19.579999999999998,9.0790000000000006,12.975,6.11,16.962,7.8719999999999999,17.736999999999998,8.2319999999999993,19.579999999999998,10.500999999999998,10.500999999999998]
[null,null,null,"Fundición Chagres  110 kV -  H1 Línea 110 kV Fundición Chagres - Nueva Panquehue",19.579999999999998,1.5780000000000001,12.975,1.0409999999999999,16.962,1.411,17.736999999999998,1.462,19.579999999999998,18.001999999999999,18.001999999999999]
[null,null,null,"Fundición Chagres  110 kV -  H3 Línea 110 kV Fundición Chagres - Río Aconcagua",19.579999999999998,8.9260000000000002,12.975,5.8259999999999996,16.962,7.6849999999999996,17.736999999999998,8.0440000000000005,19.579999999999998,10.653999999999998,10.653999999999998]
[null,null,null,"Fundición Chagres  110 kV - HT11 Transformador TR1 110/12 kV ",19.579999999999998,0,12.975,0,16.962,0,17.736999999999998,0,19.579999999999998,19.579999999999998,19.579999999999998]
[null,null,null,"Fundición Chagres  110 kV - HT12 Transformador TR2 110/12 kV ",19.579999999999998,0,12.975,0,16.962,0,17.736999999999998,0,19.579999999999998,19.579999999999998,19.579999999999998]
[null,null,null,"Fundición Chagres  110 kV - A Paño Acoplador",19.579999999999998,0,12.975,0,16.962,0,17.736999999999998,0,19.579999999999998,19.579999999999998,19.579999999999998]
[null,"Fundición Paipote",110,"Fundición Paipote 110 kV -  HL Línea 110 kV Fundición Paipote - Cardones ",4.5620000000000003,4.5620000000000003,3.431,3.431,3.9430000000000001,3.9430000000000001,4.3579999999999997,4.3579999999999997,4.5620000000000003,0,4.5620000000000003]
[null,null,null,"Fundición Paipote 110 kV - HT1 Autotransformador ATR1",4.5620000000000003,0,3.431,0,3.9430000000000001,0,4.3579999999999997,0,4.5620000000000003,4.5620000000000003,4.5620000000000003]
[null,null,null,"Fundición Paipote 110 kV - HT2 Autotransformador ATR2",4.5620000000000003,0,3.431,0,3.9430000000000001,0,4.3579999999999997,0,4.5620000000000003,4.5620000000000003,4.5620000000000003]
[null,"Galleguillos ",110,"Galleguillos  110 kV -  H1 Línea 110 kV Galleguillos - Copayapu 1",5.0860000000000003,2.4969999999999999,4.0839999999999996,2.008,4.3940000000000001,2.157,4.7430000000000003,2.2389999999999999,5.0860000000000003,2.5890000000000004,2.5890000000000004]
[null,null,null,"Galleguillos  110 kV -  H2 Línea 110 kV Galleguillos - Hernán Fuentes ",5.0860000000000003,2.1320000000000001,4.0839999999999996,1.702,4.3940000000000001,1.8420000000000001,4.7430000000000003,2.0619999999999998,5.0860000000000003,2.9540000000000002,2.9540000000000002]
[null,null,null,"Galleguillos  110 kV -  H3 Línea 110 kV Galleguillos - Impulsión/Caldera",5.0860000000000003,0.54,4.0839999999999996,0.40500000000000003,4.3940000000000001,0.46600000000000003,4.7430000000000003,0.504,5.0860000000000003,4.5460000000000003,4.5460000000000003]
[null,"Gamboa",110,"Gamboa 110 kV - HX1 Línea 110kV Pid Pid - Gamboa",5.0380000000000003,1.42,6.0190000000000001,1.232,4.2309999999999999,1.139,6.0350000000000001,1.36,6.0350000000000001,4.7869999999999999,4.7869999999999999]
[null,null,null,"Gamboa 110 kV - HX2 Línea 110kV Gamboa-Castro",5.0380000000000003,8.8999999999999996E-2,6.0190000000000001,7.2999999999999995E-2,4.2309999999999999,7.8E-2,6.0350000000000001,8.1000000000000003E-2,6.0350000000000001,5.9539999999999997,5.9539999999999997]
[null,null,null,"Gamboa 110 kV - HX3 Línea 220kV (energizada en 110kV) Gamboa - Chonchi",5.0380000000000003,0.28999999999999998,6.0190000000000001,0.24,4.2309999999999999,0.25600000000000001,6.0350000000000001,0.26500000000000001,6.0350000000000001,5.7789999999999999,5.7789999999999999]
[null,null,null,"Gamboa 110 kV - HXT1 Transformador 90 MVA 220/110/23 kV Gamboa 1",5.0380000000000003,1.659,6.0190000000000001,2.266,4.2309999999999999,1.405,6.0350000000000001,2.1890000000000001,6.0350000000000001,3.8460000000000001,3.8460000000000001]
[null,null,null,"Gamboa 110 kV - HXT2 Transformador 90 MVA 220/110/23 kV Gamboa 2",5.0380000000000003,1.659,6.0190000000000001,2.266,4.2309999999999999,1.405,6.0350000000000001,2.1890000000000001,6.0350000000000001,3.8460000000000001,3.8460000000000001]
[null,"GNL Mejillones",110,"GNL Mejillones 110 kV - H1 Línea GNL Mejillones 110kV - Chacaya",3.1640000000000001,3.1640000000000001,2.8980000000000001,2.8980000000000001,2.738,2.738,3.1480000000000001,3.1480000000000001,3.1640000000000001,0,3.1640000000000001]
[null,"GNL Quintero",110,"GNL Quintero 110 kV - HA2 Línea 110 kV GNL Quintero - Ventanas",22.093,16.754999999999999,10.548,10.6,19.131,14.528,19.957999999999998,15.096,22.093,5.338000000000001,16.754999999999999]
[null,null,null,"GNL Quintero 110 kV - HB2 Línea 110 kV GNL Quintero - Central Quintero",22.093,5.3710000000000004,10.548,2.77,19.131,4.6310000000000002,19.957999999999998,5.0970000000000004,22.093,16.722000000000001,16.722000000000001]
[null,null,null,"GNL Quintero 110 kV - HA1 Transformador TR1 30/50 MVA 110/6.6 kV",22.093,0,10.548,0,19.131,0,19.957999999999998,0,22.093,22.093,22.093]
[null,null,null,"GNL Quintero 110 kV - HB1 Transformador TR2 30/50 MVA 110/6.6 kV",22.093,0,10.548,0,19.131,0,19.957999999999998,0,22.093,22.093,22.093]
[null,null,null,"GNL Quintero 110 kV - HA3 Línea 110 kV GNL Quintero - ENAP 1",22.093,0,10.548,0,19.131,0,19.957999999999998,0,22.093,22.093,22.093]
[null,null,null,"GNL Quintero 110 kV - HB3 Línea 110 kV GNL Quintero - ENAP 2",22.093,0,10.548,0,19.131,0,19.957999999999998,0,22.093,22.093,22.093]
[null,"Guayaques ",110,"Guayaques  110 kV - HT3 Transformador TR02 37,5 MVA 110/3,45 kV ",1.746,0,0.88200000000000001,0,1.5109999999999999,0,1.589,0,1.746,1.746,1.746]
[null,null,null,"Guayaques  110 kV - HT1 Transformador TR01 37,5 MVA 110/3,45 kV ",1.746,0,0.88200000000000001,0,1.5109999999999999,0,1.589,0,1.746,1.746,1.746]
[null,"Hernán Fuentes ",110,"Hernán Fuentes  110 kV - HT1 Transformador T1 12/10 MVA 110/23 kV ",5.1740000000000004,0,4.1360000000000001,0,4.4710000000000001,0,4.87,0,5.1740000000000004,5.1740000000000004,5.1740000000000004]
[null,null,null,"Hernán Fuentes  110 kV -  H3 Línea 110 kV Hernán Fuentes - Impulsión/Caldera/Galleguillos",5.1740000000000004,2.117,4.1360000000000001,1.6859999999999999,4.4710000000000001,1.829,4.87,1.9410000000000001,5.1740000000000004,3.0570000000000004,3.0570000000000004]
[null,null,null,"Hernán Fuentes  110 kV -  H1 Línea 110 kV Hernán Fuentes - Copiapo",5.1740000000000004,3.0870000000000002,4.1360000000000001,2.4620000000000002,4.4710000000000001,2.6680000000000001,4.87,2.9540000000000002,5.1740000000000004,2.0870000000000002,3.0870000000000002]
[null,"Huachipato",154,"Huachipato 154 kV - AT1 Transformador TR1 50MVA 154/13.8 kV ",14.872,0,17.044,0,12.757,0,16.484000000000002,0,17.044,17.044,17.044]
[null,null,null,"Huachipato 154 kV - AT2 Transformador TR2 50MVA 154/13.8 kV ",14.872,0,17.044,0,12.757,0,16.484000000000002,0,17.044,17.044,17.044]
[null,null,null,"Huachipato 154 kV - AT3 Transformador TR3 50MVA 154/13.8 kV ",14.872,0,17.044,0,12.757,0,16.484000000000002,0,17.044,17.044,17.044]
[null,null,null,"Huachipato 154 kV - AT5 Transformador TR4 50MVA 154/13,8 kV ",14.872,0,17.044,0,12.757,0,16.484000000000002,0,17.044,17.044,17.044]
[null,"Hualpen",154,"Hualpen 154 kV - A1 Línea 154 kV Hualpen - San Vicente 1",15.645,3.375,19.564,3.5880000000000001,13.41,2.8959999999999999,19.321000000000002,3.5510000000000002,19.564,15.975999999999999,15.975999999999999]
[null,null,null,"Hualpen 154 kV - A2 Línea 154 kV Hualpen - San Vicente 2",15.645,3.375,19.564,3.5830000000000002,13.41,2.8959999999999999,19.321000000000002,3.5459999999999998,19.564,15.981,15.981]
[null,null,null,"Hualpen 154 kV - A3 Línea 154 kV Hualpen - Petropower",15.645,0.79300000000000004,19.564,0.83299999999999996,13.41,0.66900000000000004,19.321000000000002,0.83899999999999997,19.564,18.731000000000002,18.731000000000002]
[null,null,null,"Hualpen 154 kV - A4 Línea 154 kV Hualpen - Mapal",15.645,3.5049999999999999,19.564,3.4129999999999998,13.41,3.004,19.321000000000002,3.3889999999999998,19.564,16.151,16.151]
[null,null,null,"Hualpen 154 kV - AT1 Transformador Hualpen ATR1 300MVA 225/15/66 kV",15.645,4.6429999999999998,19.564,8.2050000000000001,13.41,3.9820000000000002,19.321000000000002,8.3209999999999997,19.564,11.359,11.359]
[null,"Huasco",110,"Huasco 110 kV - H1 Línea 110 kV Central Huasco - Maintencillo 1 ",6.0419999999999998,2.2570000000000001,6.7329999999999997,1.9630000000000001,5.1829999999999998,1.9390000000000001,6.87,2.177,6.87,4.7699999999999996,4.7699999999999996]
[null,null,null,"Huasco 110 kV - H2 Línea 110 kV Central Huasco - Maintencillo 2",6.0419999999999998,2.2879999999999998,6.7329999999999997,1.994,5.1829999999999998,1.9650000000000001,6.87,2.2080000000000002,6.87,4.7389999999999999,4.7389999999999999]
[null,null,null,"Huasco 110 kV - H3 Línea 110 kV Central Huasco - Pellets 2",6.0419999999999998,0,6.7329999999999997,0,5.1829999999999998,0,6.87,0,6.87,6.87,6.87]
[null,null,null,"Huasco 110 kV - H4 Línea 110 kV Central Huasco - Pellets 1",6.0419999999999998,0,6.7329999999999997,0,5.1829999999999998,0,6.87,0,6.87,6.87,6.87]
[null,null,null,"Huasco 110 kV - HT3 Transformador 110/11.5KV 28MVA 2",6.0419999999999998,0.52200000000000002,6.7329999999999997,0.94299999999999995,5.1829999999999998,0.44900000000000001,6.87,0.85499999999999998,6.87,6.0150000000000006,6.0150000000000006]
[null,null,null,"Huasco 110 kV - HT4 Transformador 110/11.5KV 28MVA 3",6.0419999999999998,0.52300000000000002,6.7329999999999997,0.94399999999999995,5.1829999999999998,0.45,6.87,0.85499999999999998,6.87,6.0150000000000006,6.0150000000000006]
[null,null,null,"Huasco 110 kV - HT5 Transformador 110/11.5KV 28MVA 1",6.0419999999999998,0.52300000000000002,6.7329999999999997,0.94399999999999995,5.1829999999999998,0.45,6.87,0.85499999999999998,6.87,6.0150000000000006,6.0150000000000006]
[null,"Illapel ",110,"Illapel  110 kV - HT2 Transformador TR02 13 MVA 110/24/13,8 kV ",4.0999999999999996,0,2.9430000000000001,0,3.508,0,3.855,0,4.0999999999999996,4.0999999999999996,4.0999999999999996]
[null,null,null,"Illapel  110 kV - HT1 Transformador TR01 25 MVA 110/66 kV",4.0999999999999996,0.17599999999999999,2.9430000000000001,0.24399999999999999,3.508,0.152,3.855,0.26200000000000001,4.0999999999999996,3.9239999999999995,3.9239999999999995]
[null,null,null,"Illapel  110 kV -  H3 Línea 110 kV Illapel - Punitaqui/Ovalle ",4.0999999999999996,1.4510000000000001,2.9430000000000001,1.0669999999999999,3.508,1.2270000000000001,3.855,1.377,4.0999999999999996,2.6489999999999996,2.6489999999999996]
[null,null,null,"Illapel  110 kV -  H1 Línea 110 kV Illapel - Salamanca ",4.0999999999999996,0,2.9430000000000001,1E-3,3.508,0,3.855,1E-3,4.0999999999999996,4.0999999999999996,4.0999999999999996]
[null,null,null,"Illapel  110 kV -  H2 Línea 110 kV Illapel - Choapa ",4.0999999999999996,2.496,2.9430000000000001,1.64,3.508,2.1480000000000001,3.855,2.2810000000000001,4.0999999999999996,1.6039999999999996,2.496]
[null,"Impulsión",110,"Impulsión 110 kV - HT Transformador TR1 110/23 kV ",4.0090000000000003,0,2.9390000000000001,0,3.4660000000000002,0,3.7269999999999999,0,4.0090000000000003,4.0090000000000003,4.0090000000000003]
[null,"Incahuasi ",110,"Incahuasi  110 kV - H1 Línea 110 kV Incahuasi - Las Compañias/Tap Off El Romeral",2.5739999999999998,1.284,1.8220000000000001,0.85699999999999998,2.2250000000000001,1.1120000000000001,2.4860000000000002,1.2190000000000001,2.5739999999999998,1.2899999999999998,1.2899999999999998]
[null,"Itahue",154,"Itahue 154 kV - A1 Línea 154 kV Itahue - Cipreses C1",15.973000000000001,0.999,19.972000000000001,0.88400000000000001,13.752000000000001,0.81899999999999995,19.765000000000001,0.93899999999999995,19.972000000000001,19.088000000000001,19.088000000000001]
[null,null,null,"Itahue 154 kV - A2 Línea 154 kV Itahue - Cipreses C2",15.973000000000001,0.92400000000000004,19.972000000000001,0.81,13.752000000000001,0.751,19.765000000000001,0.86499999999999999,19.972000000000001,19.162000000000003,19.162000000000003]
[null,null,null,"Itahue 154 kV - A3 Línea 154 kV Itahue - Tinguiririca 1",15.973000000000001,2.2610000000000001,19.972000000000001,1.9970000000000001,13.752000000000001,1.964,19.765000000000001,2.1259999999999999,19.972000000000001,17.975000000000001,17.975000000000001]
[null,null,null,"Itahue 154 kV - A4 Línea 154 kV Itahue - Tinguiririca 2/Convento Viejo",15.973000000000001,2.2610000000000001,19.972000000000001,1.9970000000000001,13.752000000000001,1.964,19.765000000000001,2.1259999999999999,19.972000000000001,17.975000000000001,17.975000000000001]
[null,null,null,"Itahue 154 kV - A5 Línea 154 kV Itahue - Charrúa (Parral/Linares)",15.973000000000001,2.4039999999999999,19.972000000000001,2.2650000000000001,13.752000000000001,2.0819999999999999,19.765000000000001,2.3420000000000001,19.972000000000001,17.707000000000001,17.707000000000001]
[null,null,null,"Itahue 154 kV - AT Transformador Itahue TR01 75MVA 154/13.8 kV N°1",15.973000000000001,0.435,19.972000000000001,0.53400000000000003,13.752000000000001,0.376,19.765000000000001,0.56399999999999995,19.972000000000001,19.438000000000002,19.438000000000002]
[null,null,null,"Itahue 154 kV - AT2 Transformador Itahue TR02 56MVA 154/69/13.8 kV N°2",15.973000000000001,0.28100000000000003,19.972000000000001,0.39900000000000002,13.752000000000001,0.24299999999999999,19.765000000000001,0.42699999999999999,19.972000000000001,19.573,19.573]
[null,null,null,"Itahue 154 kV - AT4 Transformador ATR Itahue N°4",15.973000000000001,5.9080000000000004,19.972000000000001,9.3949999999999996,13.752000000000001,5.1210000000000004,19.765000000000001,9.1639999999999997,19.972000000000001,10.601000000000001,10.601000000000001]
[null,null,null,"Itahue 154 kV - AT5 Transformador Itahue TR05N 154/66/13.2 kV N°5",15.973000000000001,0.56899999999999995,19.972000000000001,1.732,13.752000000000001,0.49299999999999999,19.765000000000001,2.0489999999999999,19.972000000000001,18.240000000000002,18.240000000000002]
[null,"K1 ",100,"K1  100 kV - H12 Línea 100 kV K1 - Chuquicamata",9.9429999999999996,4.423,10.54,4.42,8.4960000000000004,3.78,10.340999999999999,4.3810000000000002,10.54,6.1199999999999992,6.1199999999999992]
[null,null,null,"K1  100 kV - H23 Línea 100 kV K1 - 10",9.9429999999999996,5.532,10.54,6.1260000000000003,8.4960000000000004,4.726,10.340999999999999,5.9989999999999997,10.54,4.4139999999999988,6.1260000000000003]
[null,null,null,"K1  100 kV - HT1 Transformador TR01 26,6/20 MVA 100/13,8 kV ",9.9429999999999996,0,10.54,0,8.4960000000000004,0,10.340999999999999,0,10.54,10.54,10.54]
[null,null,null,"K1  100 kV - HT2 Transformador TR02 26,6/20 MVA 100/13,8 kV ",9.9429999999999996,0,10.54,0,8.4960000000000004,0,10.340999999999999,0,10.54,10.54,10.54]
[null,null,null,"K1  100 kV - HT3 Transformador TR03 25/20 MVA 100/13,8 kV ",9.9429999999999996,0,10.54,0,8.4960000000000004,0,10.340999999999999,0,10.54,10.54,10.54]
[null,null,null,"K1  100 kV - HAB Paño Acoplador ",9.9429999999999996,0,10.54,0,8.4960000000000004,0,10.340999999999999,0,10.54,10.54,10.54]
[null,"KM6",100,"KM6 100 kV - H13 Línea 100 kV KM6 - Chuquicamata",9.9789999999999992,2.5379999999999998,11.007,2.9620000000000002,8.5250000000000004,2.17,10.708,2.8140000000000001,11.007,8.0449999999999999,8.0449999999999999]
[null,null,null,"KM6 100 kV - H22 Línea 100 kV KM6 - 10A",9.9789999999999992,3.972,11.007,4.09,8.5250000000000004,3.3959999999999999,10.708,4.077,11.007,6.9169999999999998,6.9169999999999998]
[null,null,null,"KM6 100 kV - H24 Línea 100 kV KM6 - Sopladores",9.9789999999999992,0,11.007,0,8.5250000000000004,0,10.708,0,11.007,11.007,11.007]
[null,null,null,"KM6 100 kV - H25 Línea 100 kV KM6 - Salar C1",9.9789999999999992,1.7350000000000001,11.007,1.978,8.5250000000000004,1.48,10.708,1.913,11.007,9.0289999999999999,9.0289999999999999]
[null,null,null,"KM6 100 kV - H26 Línea 100 kV KM6 - Salar C2",9.9789999999999992,1.7350000000000001,11.007,1.978,8.5250000000000004,1.48,10.708,1.913,11.007,9.0289999999999999,9.0289999999999999]
[null,null,null,"KM6 100 kV - HT1 Transformador KM6 TR01 25/20 MVA 100/13.8 kV ",9.9789999999999992,0,11.007,0,8.5250000000000004,0,10.708,0,11.007,11.007,11.007]
[null,null,null,"KM6 100 kV - HT2 Transformador KM6 TR02 33/25 MVA 100/13.8 kV",9.9789999999999992,0,11.007,0,8.5250000000000004,0,10.708,0,11.007,11.007,11.007]
[null,null,null,"KM6 100 kV - HT3 Transformador KM6 TR03 25/20 MVA 100/13.8 kV",9.9789999999999992,0,11.007,0,8.5250000000000004,0,10.708,0,11.007,11.007,11.007]
[null,null,null,"KM6 100 kV - HACOP Paño Acoplador ",9.9789999999999992,0,11.007,0,8.5250000000000004,0,10.708,0,11.007,11.007,11.007]
[null,"La Calera",110,"La Calera 110 kV - H5 Línea 110 kV La Calera - El Cobre",14.555,0,11.422000000000001,1E-3,12.57,0,13.552,1E-3,14.555,14.555,14.555]
[null,null,null,"La Calera 110 kV - HT1 Transformador TR1 30 MVA 115/44 kV",14.555,0.30599999999999999,11.422000000000001,0.16,12.57,0.26300000000000001,13.552,0.26700000000000002,14.555,14.249000000000001,14.249000000000001]
[null,null,null,"La Calera 110 kV - HT2 Transformador TR2 22,5 MVA 115/12 kV",14.555,0,11.422000000000001,0,12.57,0,13.552,0,14.555,14.555,14.555]
[null,null,null,"La Calera 110 kV - HT3 Transformador TR3 25 MVA 115/12 kV",14.555,0,11.422000000000001,0,12.57,0,13.552,0,14.555,14.555,14.555]
[null,"La Cisterna",110,"La Cisterna 110 kV - H1 Línea 110 kV La Cisterna - Chena/Ochagavía 1",39.404000000000003,19.702000000000002,21.353000000000002,10.677,34.121000000000002,17.061,35.076999999999998,17.538,39.404000000000003,19.702000000000002,19.702000000000002]
[null,null,null,"La Cisterna 110 kV - H2 Línea 110 kV La Cisterna - Chena/Ochagavía 2",39.404000000000003,19.702000000000002,21.353000000000002,10.677,34.121000000000002,17.061,35.076999999999998,17.538,39.404000000000003,19.702000000000002,19.702000000000002]
[null,null,null,"La Cisterna 110 kV - HT5 Transformador TR05 50 MVA 110/13.2 kV",39.404000000000003,0,21.353000000000002,0,34.121000000000002,0,35.076999999999998,0,39.404000000000003,39.404000000000003,39.404000000000003]
[null,"La Dehesa",110,"La Dehesa 110 kV - HT1 Transformador TR01 25MVA 110/13.2 kV ",22.259,0,11.218,0,19.28,0,19.835000000000001,0,22.259,22.259,22.259]
[null,null,null,"La Dehesa 110 kV - HT2 Transformador TR02 50MVA 110/12.5 kV",22.259,0,11.218,0,19.28,0,19.835000000000001,0,22.259,22.259,22.259]
[null,null,null,"La Dehesa 110 kV - HT3 Transformador TR03 50MVA 110/23.5 kV",22.259,0,11.218,0,19.28,0,19.835000000000001,0,22.259,22.259,22.259]
[null,null,null,"La Dehesa 110 kV - H4 Transformador TR04 20MVA  110/23 kV ",22.259,0,11.218,0,19.28,0,19.835000000000001,0,22.259,22.259,22.259]
[null,"La Pintana",110,"La Pintana 110 kV - H1 Línea 110 kV La Pintana - Buin / Florida 1",32.171999999999997,16.085999999999999,16.367999999999999,8.1839999999999993,27.882999999999999,13.942,28.527999999999999,14.263999999999999,32.171999999999997,16.085999999999999,16.085999999999999]
[null,null,null,"La Pintana 110 kV - H2 Línea 110 kV La Pintana - Buin / Florida 2",32.171999999999997,16.085999999999999,16.367999999999999,8.1839999999999993,27.882999999999999,13.942,28.527999999999999,14.263999999999999,32.171999999999997,16.085999999999999,16.085999999999999]
[null,null,null,"La Pintana 110 kV - A-T4 Transformador TR04 25MVA 110/12.5 kV",32.171999999999997,0,16.367999999999999,0,27.882999999999999,0,28.527999999999999,0,32.171999999999997,32.171999999999997,32.171999999999997]
[null,"La Portada",110,"La Portada 110 kV - H1 Línea 110kV Guardiamarina - La Portada",7.9870000000000001,7.9669999999999996,6.2169999999999996,6.2069999999999999,6.8230000000000004,6.806,7.3319999999999999,7.3150000000000004,7.9870000000000001,2.0000000000000462E-2,7.9669999999999996]
[null,null,null,"La Portada 110 kV - HT1 Transformador TR1 110/23 kV ",7.9870000000000001,2.1000000000000001E-2,6.2169999999999996,1.0999999999999999E-2,6.8230000000000004,1.7000000000000001E-2,7.3319999999999999,1.7999999999999999E-2,7.9870000000000001,7.9660000000000002,7.9660000000000002]
[null,null,null,"La Portada 110 kV - HT3 Transformador TR3 110/23 kV",7.9870000000000001,0,6.2169999999999996,0,6.8230000000000004,0,7.3319999999999999,0,7.9870000000000001,7.9870000000000001,7.9870000000000001]
[null,"La Reina",110,"La Reina 110 kV -  H1 Línea 110 kV La Reina - Florida/Los Almendros 1",20.794,10.397,8.5370000000000008,4.2690000000000001,18.012,9.0060000000000002,18.22,9.11,20.794,10.397,10.397]
[null,null,null,"La Reina 110 kV -  H2 Línea 110 kV La Reina - Florida/Los Almendros 2",20.794,10.397,8.5370000000000008,4.2690000000000001,18.012,9.0060000000000002,18.22,9.11,20.794,10.397,10.397]
[null,"Lagunillas",154,"Lagunillas 154 kV -  A2 Línea 154kV Lagunillas - Hualpén ",13.625999999999999,3.5379999999999998,17.245000000000001,5.0439999999999996,11.683999999999999,3.024,17.088000000000001,4.976,17.245000000000001,5.0439999999999996,5.0439999999999996]
[null,null,null,"Lagunillas 154 kV -  A3 Línea 154kV Lagunillas - Hualpén ",13.625999999999999,7.8970000000000002,17.245000000000001,9.1910000000000007,11.683999999999999,6.7720000000000002,17.088000000000001,9.109,17.245000000000001,9.1910000000000007,9.1910000000000007]
[null,null,null,"Lagunillas 154 kV -  A4 ATR Lagunilla 220/154 kV",13.625999999999999,10.343,17.245000000000001,13.66,11.683999999999999,8.8650000000000002,17.088000000000001,13.516,17.245000000000001,13.66,13.66]
[null,null,null,"Lagunillas 154 kV -  A5 ATR Lagunilla 220/154 kV",13.625999999999999,3.5379999999999998,17.245000000000001,5.0439999999999996,11.683999999999999,3.024,17.088000000000001,4.976,17.245000000000001,5.0439999999999996,5.0439999999999996]
[null,null,null,"Lagunillas 154 kV - A5 Línea 154kV Lagunillas - Bocamina",13.625999999999999,3.5379999999999998,17.245000000000001,5.0439999999999996,11.683999999999999,3.024,17.088000000000001,4.976,17.245000000000001,5.0439999999999996,5.0439999999999996]
[null,null,null,"Lagunillas 154 kV -  A6 Línea 154kV Lagunillas - Bocamina",13.625999999999999,7.8970000000000002,17.245000000000001,9.1910000000000007,11.683999999999999,6.7720000000000002,17.088000000000001,9.109,17.245000000000001,9.1910000000000007,9.1910000000000007]
[null,"Las Acacias",110,"Las Acacias 110 kV -  H1 Línea 110 kV Las Acacias - Buin/Lo Espejo 1",41.813000000000002,20.905999999999999,20.908000000000001,10.454000000000001,36.228000000000002,18.114000000000001,36.951999999999998,18.475999999999999,41.813000000000002,20.907000000000004,20.907000000000004]
[null,null,null,"Las Acacias 110 kV -  H2 Línea 110 kV Las Acacias - Buin/Lo Espejo 2",41.813000000000002,20.905999999999999,20.908000000000001,10.454000000000001,36.228000000000002,18.114000000000001,36.951999999999998,18.475999999999999,41.813000000000002,20.907000000000004,20.907000000000004]
[null,"Las Arañas ",110,"Las Arañas  110 kV - HL1 Línea 110 kV Las Arañas - Quelentaro",3.46,3.46,3.6640000000000001,3.177,2.9969999999999999,2.9969999999999999,3.59,3.4409999999999998,3.6640000000000001,0.4870000000000001,3.46]
[null,null,null,"Las Arañas  110 kV - HT2 AutoTransformador ATR2 40/40/8 MVA 110/66/13.8 kV",3.46,0,3.6640000000000001,0.251,2.9969999999999999,0,3.59,0.26700000000000002,3.6640000000000001,3.46,3.46]
[null,null,null,"Las Arañas  110 kV - HT1 AutoTransformador ATR1 40/40/8 MVA 110/66/13.8 kV",3.46,0,3.6640000000000001,0.251,2.9969999999999999,0,3.59,0.26700000000000002,3.6640000000000001,3.46,3.46]
[null,"Las Compañias ",110,"Las Compañias  110 kV - H2 Línea 110 kV Las Compañias - Maintencillo/Tap Off Romeral 1",5.6079999999999997,0.72099999999999997,4.6669999999999998,0.52900000000000003,4.8479999999999999,0.623,5.36,0.69,5.6079999999999997,4.8869999999999996,4.8869999999999996]
[null,null,null,"Las Compañias  110 kV - H1 Línea 110 kV Las Compañias - Pan de Azucar 1",5.6079999999999997,4.9130000000000003,4.6669999999999998,4.149,4.8479999999999999,4.2469999999999999,5.36,4.68,5.6079999999999997,0.6949999999999994,4.9130000000000003]
[null,null,null,"Las Compañias  110 kV - HT Transformador TR1 110/14.2 kV",5.6079999999999997,0,4.6669999999999998,0,4.8479999999999999,0,5.36,0,5.6079999999999997,5.6079999999999997,5.6079999999999997]
[null,"Las Luces",110,"Las Luces 110 kV - HT1 Transformador Las Luces 110/33 kV N°1",1.3120000000000001,0,0.97299999999999998,0,1.1359999999999999,0,1.2689999999999999,0,1.3120000000000001,1.3120000000000001,1.3120000000000001]
[null,null,null,"Las Luces 110 kV - H2 Línea 110 kV Las Luces - Tal Tal (ELECDA)  1",1.3120000000000001,0,0.97299999999999998,2E-3,1.1359999999999999,0,1.2689999999999999,2E-3,1.3120000000000001,1.3120000000000001,1.3120000000000001]
[null,"Las Vegas",110,"Las Vegas 110 kV -  H1 Línea 110 kV Las Vegas - San Pedro/Cerro Calera/Calera 1",26.513000000000002,3.5289999999999999,23.312000000000001,2.8620000000000001,22.741,3.0659999999999998,25.29,3.2050000000000001,26.513000000000002,22.984000000000002,22.984000000000002]
[null,null,null,"Las Vegas 110 kV -  H3 Línea 110 kV Las Vegas - Central Santiago Solar 1",26.513000000000002,2.0030000000000001,23.312000000000001,1.6020000000000001,22.741,1.742,25.29,1.845,26.513000000000002,24.51,24.51]
[null,null,null,"Las Vegas 110 kV -  H4 Línea 110 kV Las Vegas - Cerro Navia (Enel)/Tap Off Punta Peuco 2",26.513000000000002,2.0030000000000001,23.312000000000001,1.5349999999999999,22.741,1.742,25.29,1.8220000000000001,26.513000000000002,24.51,24.51]
[null,null,null,"Las Vegas 110 kV -  H6 Línea 110 kV Las Vegas - Esperanza (HASA) C1",26.513000000000002,12.052,23.312000000000001,10.006,22.741,10.513999999999999,25.29,11.246,26.513000000000002,14.461000000000002,14.461000000000002]
[null,null,null,"Las Vegas 110 kV -  H2 Línea 110 kV Las Vegas - San Pedro/Cerro Calera/Calera 2",26.513000000000002,3.5289999999999999,23.312000000000001,2.8620000000000001,22.741,3.0659999999999998,25.29,3.2050000000000001,26.513000000000002,22.984000000000002,22.984000000000002]
[null,null,null,"Las Vegas 110 kV - HR Acoplador",26.513000000000002,0,23.312000000000001,0,22.741,0,25.29,0,26.513000000000002,26.513000000000002,26.513000000000002]
[null,null,null,"Las Vegas 110 kV - HT4 Transformador TR4 160 MVA 110/15 kV",26.513000000000002,3.2080000000000002,23.312000000000001,4.3550000000000004,22.741,2.4590000000000001,25.29,3.976,26.513000000000002,23.305,23.305]
[null,null,null,"Las Vegas 110 kV - HT1 Transformador TR1 28 MVA 110/44 kV",26.513000000000002,6.8000000000000005E-2,23.312000000000001,0.04,22.741,5.8999999999999997E-2,25.29,0.06,26.513000000000002,26.445,26.445]
[null,null,null,"Las Vegas 110 kV - HT2 Transformador TR2 30 MVA 110/44 kV",26.513000000000002,6.6000000000000003E-2,23.312000000000001,3.9E-2,22.741,5.7000000000000002E-2,25.29,5.8000000000000003E-2,26.513000000000002,26.447000000000003,26.447000000000003]
[null,null,null,"Las Vegas 110 kV - HT3 Tranaformador TR3 25 MVA 110/13.2 kV",26.513000000000002,9.1999999999999998E-2,23.312000000000001,5.5E-2,22.741,8.2000000000000003E-2,25.29,7.9000000000000001E-2,26.513000000000002,26.421000000000003,26.421000000000003]
[null,null,null,"Las Vegas 110 kV - HT5 Transformador TR5 30 MVA 115/13.2 kV",26.513000000000002,0,23.312000000000001,0,22.741,0,25.29,0,26.513000000000002,26.513000000000002,26.513000000000002]
[null,null,null,"Las Vegas 110 kV - H7 Línea 110 kV Las Vegas - Cristalerías (Llay Llay)",26.513000000000002,0,23.312000000000001,0,22.741,0,25.29,0,26.513000000000002,26.513000000000002,26.513000000000002]
[null,"Las Vizcachas",110,"Las Vizcachas 110 kV - H1 Línea 110kV Las Vizcachas - Puente Alto (EEPA)",20.359000000000002,0.34100000000000003,13.696999999999999,0.77800000000000002,17.606000000000002,0.32500000000000001,18.684000000000001,0.56699999999999995,20.359000000000002,20.018000000000001,20.018000000000001]
[null,"Leyda",110,"Leyda 110 kV - HT1 Transformador TR1 12,5/10 MVA 115/13.8 kV",5.4630000000000001,0,4.4409999999999998,0,4.7309999999999999,0,5.1150000000000002,0,5.4630000000000001,5.4630000000000001,5.4630000000000001]
[null,null,null,"Leyda 110 kV - H1 Línea 110 kV Leyda - Alto Melipilla C2",5.4630000000000001,3.4809999999999999,4.4409999999999998,2.7509999999999999,4.7309999999999999,3.0139999999999998,5.1150000000000002,3.2109999999999999,5.4630000000000001,1.9820000000000002,3.4809999999999999]
[null,null,null,"Leyda 110 kV - H2 Línea 110 kV Leyda - San Antonio C2",5.4630000000000001,1.9830000000000001,4.4409999999999998,1.6910000000000001,4.7309999999999999,1.718,5.1150000000000002,1.909,5.4630000000000001,3.48,3.48]
[null,"Linares",154,"Linares 154 kV - AT1 Transformador TR01 60/75MVA",6.11,0.82299999999999995,5.8109999999999999,1.165,5.2789999999999999,0.70699999999999996,6.1680000000000001,1.137,6.1680000000000001,5.2870000000000008,5.2870000000000008]
[null,"Llanta C1",110,"Llanta C1 110 kV -  En Barra",4.9340000000000002,0,4.8920000000000003,0,4.2640000000000002,0,5.125,0,5.125,5.125,5.125]
[null,"Llanta C2",110,"Llanta C2 110 kV -  En Barra",5.069,0,5.0810000000000004,0,4.38,0,5.3040000000000003,0,5.3040000000000003,5.3040000000000003,5.3040000000000003]
[null,"Lo Aguirre",110,"Lo Aguirre 110 kV - H1 Línea 110 kV Lo Aguirre - Cerro Navia (Enel)/Lo Prado 2",7.23,7.23,4.4909999999999997,4.4909999999999997,6.2640000000000002,6.2640000000000002,6.7779999999999996,6.7779999999999996,7.23,0,7.23]
[null,"Lo Boza",110,"Lo Boza 110 kV - H1 Línea 110 kV Lo Boza - San Cristóbal/Cerro Navia (Enel) 1",35.447000000000003,17.724,17.763000000000002,8.8819999999999997,30.684999999999999,15.343,31.402000000000001,15.701000000000001,35.447000000000003,17.723000000000003,17.724]
[null,null,null,"Lo Boza 110 kV - H2 Línea 110 kV Lo Boza - San Cristóbal/Cerro Navia (Enel) 2",35.447000000000003,17.724,17.763000000000002,8.8819999999999997,30.684999999999999,15.343,31.402000000000001,15.701000000000001,35.447000000000003,17.723000000000003,17.724]
[null,null,null,"Lo Boza 110 kV - HT3 Transformador TR03 12,5 MVA 110/23.5 kV ",35.447000000000003,0,17.763000000000002,0,30.684999999999999,0,31.402000000000001,0,35.447000000000003,35.447000000000003,35.447000000000003]
[null,"Lo Espejo",110,"Lo Espejo 110 kV -  En Barra",51.759,0,40.994,0,44.832000000000001,0,48.13,0,51.759,51.759,51.759]
[null,"Lo Espejo (FFCC)",110,"Lo Espejo (FFCC) 110 kV -  En Barra",47.048999999999999,0,28.396999999999998,0,40.737000000000002,0,42.220999999999997,0,47.048999999999999,47.048999999999999,47.048999999999999]
[null,"Lo Prado",110,"Lo Prado 110 kV - H1 Línea 110 kV Lo Prado - Lo Aguirre",7.25,7.056,4.6070000000000002,4.524,6.2809999999999997,6.1130000000000004,6.8159999999999998,6.6589999999999998,7.25,0.19399999999999995,7.056]
[null,"Lo Valledor",110,"Lo Valledor 110 kV - H1 Línea 110 kV Lo Valledor - Cerro Navia (Enel)/Chena 1",28.856999999999999,14.429,12.925000000000001,6.4619999999999997,24.992999999999999,12.496,25.59,12.795,28.856999999999999,14.427999999999999,14.429]
[null,null,null,"Lo Valledor 110 kV - HT1 Transformador TR01 25 MVA 110/13.2 kV",28.856999999999999,0,12.925000000000001,0,24.992999999999999,0,25.59,0,28.856999999999999,28.856999999999999,28.856999999999999]
[null,null,null,"Lo Valledor 110 kV - HT4 Transformador TR04 110/12.5 kV",28.856999999999999,0,12.925000000000001,0,24.992999999999999,0,25.59,0,28.856999999999999,28.856999999999999,28.856999999999999]
[null,null,null,"Lo Valledor 110 kV - HT3 Transformador TR03 50 MVA 110/12.5 kV",28.856999999999999,0,12.925000000000001,0,24.992999999999999,0,25.59,0,28.856999999999999,28.856999999999999,28.856999999999999]
[null,null,null,"Lo Valledor 110 kV - HT2 Transformador TR02 25 MVA 110/12.5 kV",28.856999999999999,0,12.925000000000001,0,24.992999999999999,0,25.59,0,28.856999999999999,28.856999999999999,28.856999999999999]
[null,null,null,"Lo Valledor 110 kV - H2 Línea 110 kV Lo Valledor - Cerro Navia (Enel)/ Chena 2",28.856999999999999,14.429,12.925000000000001,6.4619999999999997,24.992999999999999,12.496,25.59,12.795,28.856999999999999,14.427999999999999,14.429]
[null,"Lord Cochrane",110,"Lord Cochrane 110 kV - HT1 Transformador TR01 44,7 MVA 110/12.5 kV ",48.33,0,38.567999999999998,0,41.802,0,46.167999999999999,0,48.33,48.33,48.33]
[null,null,null,"Lord Cochrane 110 kV - HT2 Transformador TR02 44,7 MVA 110/12.5 kV ",48.33,0,38.567999999999998,0,41.802,0,46.167999999999999,0,48.33,48.33,48.33]
[null,"Los Almendros",110,"Los Almendros 110 kV -  H1 Línea 110 kV Los Almendros - Los Dominicos/El Salto 1",32.997999999999998,6.4829999999999997,29.957000000000001,4.4749999999999996,28.587,5.6180000000000003,32.045999999999999,5.7889999999999997,32.997999999999998,26.514999999999997,26.514999999999997]
[null,null,null,"Los Almendros 110 kV -  H2 Línea 110 kV Los Almendros - El Salto C2",32.997999999999998,5.7610000000000001,29.957000000000001,4.0369999999999999,28.587,4.992,32.045999999999999,5.15,32.997999999999998,27.236999999999998,27.236999999999998]
[null,null,null,"Los Almendros 110 kV -  H3 Línea 110 kV Los Almendros - Florida C1",32.997999999999998,4.7990000000000004,29.957000000000001,3.2839999999999998,28.587,4.1550000000000002,32.045999999999999,4.3070000000000004,32.997999999999998,28.198999999999998,28.198999999999998]
[null,null,null,"Los Almendros 110 kV -  H4 Línea 110 kV Los Almendros - Andes/Florida C2",32.997999999999998,4.7990000000000004,29.957000000000001,3.2839999999999998,28.587,4.1550000000000002,32.045999999999999,4.3070000000000004,32.997999999999998,28.198999999999998,28.198999999999998]
[null,null,null,"Los Almendros 110 kV - HT1 Transformador TR01 400 MVA 220/110 kV",32.997999999999998,11.291,29.957000000000001,14.954000000000001,28.587,9.7850000000000001,32.045999999999999,13.026,32.997999999999998,21.706999999999997,21.706999999999997]
[null,"Los Angeles",154,"Los Angeles 154 kV - AT3 Transformador Los Ángeles TR03 56MVA 154/66 kV N°3",6.1150000000000002,0.79600000000000004,6.0209999999999999,1.0549999999999999,5.2460000000000004,0.67900000000000005,6.3739999999999997,0.97,6.3739999999999997,5.4039999999999999,5.4039999999999999]
[null,null,null,"Los Angeles 154 kV - AT4 Transformador Los Ángeles TR04 56MVA 154/66 kV N°4",6.1150000000000002,1.196,6.0209999999999999,1.452,5.2460000000000004,1.02,6.3739999999999997,1.375,6.3739999999999997,4.9989999999999997,4.9989999999999997]
[null,null,null,"Los Angeles 154 kV - A1 Línea 154 kV Los Ángeles - Charrúa",6.1150000000000002,4.1550000000000002,6.0209999999999999,3.2170000000000001,5.2460000000000004,3.573,6.3739999999999997,3.871,6.3739999999999997,2.8039999999999998,4.1550000000000002]
[null,null,null,"Los Angeles 154 kV - A2 Línea 154 kV Los Ángeles - Negrete Cuel /Tap Santa Luisa/Santa Fe",6.1150000000000002,0,6.0209999999999999,0.31900000000000001,5.2460000000000004,0,6.3739999999999997,0.31900000000000001,6.3739999999999997,6.1150000000000002,6.1150000000000002]
[null,"Los Colorados",110,"Los Colorados 110 kV - H1 Transformador TR01 110/13.2 kV ",3.0680000000000001,0,2.0270000000000001,0,2.6480000000000001,0,2.9449999999999998,0,3.0680000000000001,3.0680000000000001,3.0680000000000001]
[null,"Los Dominicos",110,"Los Dominicos 110 kV - H1 Línea 110 kV Los Dominicos - Los Almendros/El Salto 1",22.413,11.250999999999999,11.821,5.9260000000000002,19.417000000000002,9.7479999999999993,20.036999999999999,10.06,22.413,11.162000000000001,11.250999999999999]
[null,null,null,"Los Dominicos 110 kV - H2 Línea 110 kV Los Dominicos - Los Almendros/ El Salto 2",22.413,11.162000000000001,11.821,5.8949999999999996,19.417000000000002,9.67,20.036999999999999,9.9770000000000003,22.413,11.250999999999999,11.250999999999999]
[null,"Los Libertadores",110,"Los Libertadores 110 kV - HX1 Línea 110kV TO Libertadores-Libertadores C2",28.635000000000002,14.318,18.567,9.2829999999999995,24.783000000000001,12.391,26.04,13.02,28.635000000000002,14.317000000000002,14.318]
[null,null,null,"Los Libertadores 110 kV - HX2 Línea 110kV TO Libertadores-Libertadores C1",28.635000000000002,14.318,18.567,9.2829999999999995,24.783000000000001,12.391,26.04,13.02,28.635000000000002,14.317000000000002,14.318]
[null,"Los Loros",110,"Los Loros 110 kV - HT1 Transformador T1 20/16/12 MVA 110/24-13,8 kV",2.5350000000000001,0,2.883,0,2.1930000000000001,0,2.9780000000000002,0,2.9780000000000002,2.9780000000000002,2.9780000000000002]
[null,null,null,"Los Loros 110 kV - H1 Línea 110 kV Los Loros - Central PV Los Loros 1",2.5350000000000001,0,2.883,0.70699999999999996,2.1930000000000001,0,2.9780000000000002,0.81399999999999995,2.9780000000000002,2.5350000000000001,2.5350000000000001]
[null,"Los Maquis",110,"Los Maquis 110 kV - H3 Línea 110 kV Los Maquis - Aconcagua/Fundición Chagres 1",10.583,2.7789999999999999,11.606,2.6619999999999999,9.43,2.4550000000000001,11.374000000000001,2.794,11.606,8.9439999999999991,8.9439999999999991]
[null,null,null,"Los Maquis 110 kV - H4 Línea 110 kV Los Maquis - Aconcagua / Totoralillo / Esperanza (HASA) 2",10.583,2.827,11.606,2.8109999999999999,9.43,2.625,11.374000000000001,2.8740000000000001,11.606,8.7949999999999999,8.7949999999999999]
[null,null,null,"Los Maquis 110 kV - H5 Línea 110 kV Los Maquis - Central Los Quilos 1",10.583,0.59,11.606,0.89300000000000002,9.43,0.51600000000000001,11.374000000000001,0.76400000000000001,11.606,10.712999999999999,10.712999999999999]
[null,null,null,"Los Maquis 110 kV - HS Transformador TR01 95 MVA 220/110/12 kV",10.583,4.4889999999999999,11.606,5.3070000000000004,9.43,3.9,11.374000000000001,4.9489999999999998,11.606,6.4250000000000007,6.4250000000000007]
[null,"Los Placeres (Placeres)",110,"Los Placeres (Placeres) 110 kV - HT1 Transformador TR1 110/12 kV ",16.303000000000001,0,10.303000000000001,0,14.134,0,14.802,0,16.303000000000001,16.303000000000001,16.303000000000001]
[null,null,null,"Los Placeres (Placeres) 110 kV - HT2 Transformador TR2 110/12 kV ",16.303000000000001,0,10.303000000000001,0,14.134,0,14.802,0,16.303000000000001,16.303000000000001,16.303000000000001]
[null,"Macul",110,"Macul 110 kV - H1 Línea 110 kV Macul - Ochagavia/Florida 1",34.067,17.033000000000001,15.282999999999999,7.6420000000000003,29.501999999999999,14.750999999999999,29.969000000000001,14.984,34.067,17.033999999999999,17.033999999999999]
[null,null,null,"Macul 110 kV - H2 Línea 110 kV Macul - Ochagavia/Florida 2",34.067,17.033000000000001,15.282999999999999,7.6420000000000003,29.501999999999999,14.750999999999999,29.969000000000001,14.984,34.067,17.033999999999999,17.033999999999999]
[null,null,null,"Macul 110 kV - H4 Transformador TR04 50 MVA 110/12.5 kV ",34.067,0,15.282999999999999,0,29.501999999999999,0,29.969000000000001,0,34.067,34.067,34.067]
[null,null,null,"Macul 110 kV - H6 Transformador TR06 50 MVA 110/20.4 kV",34.067,0,15.282999999999999,0,29.501999999999999,0,29.969000000000001,0,34.067,34.067,34.067]
[null,"Magnetita",110,"Magnetita 110 kV - H7 Transformador TR 28MVA 110/4,16kV",3.9809999999999999,0,4.1989999999999998,0,3.4430000000000001,0,4.1840000000000002,0,4.1989999999999998,4.1989999999999998,4.1989999999999998]
[null,"Maipo",110,"Maipo 110 kV - H1 Línea 110 kV Maipo - Puente Alto (CMPC)/Pirque ",3.6360000000000001,1.042,3.867,1.163,3.2,0.95799999999999996,3.7749999999999999,1.1020000000000001,3.867,2.7039999999999997,2.7039999999999997]
[null,"Maipú",110,"Maipú 110 kV - H1 Línea 110 kV Maipu - Cerro Navia (Enel)/Chena 1",49.878,24.939,39.76,19.88,43.201000000000001,21.6,46.423000000000002,23.210999999999999,49.878,24.939,24.939]
[null,null,null,"Maipú 110 kV - H2 Línea 110 kV Maipu - Cerro Navia (Enel)/Chena 2",49.878,24.939,39.76,19.88,43.201000000000001,21.6,46.423000000000002,23.210999999999999,49.878,24.939,24.939]
[null,"Maitencillo",110,"Maitencillo 110 kV - H1 Línea 110 kV Maitencillo - Pan de Azucar",10.577999999999999,0.64800000000000002,12.05,0.56100000000000005,8.9730000000000008,0.56100000000000005,11.882,0.627,12.05,11.489000000000001,11.489000000000001]
[null,null,null,"Maitencillo 110 kV - HT2 Transformador ATR2 90 MVA 220/115/13.2 kV",10.577999999999999,3.18,12.05,3.6230000000000002,8.9730000000000008,2.7450000000000001,11.882,3.4860000000000002,12.05,8.4269999999999996,8.4269999999999996]
[null,null,null,"Maitencillo 110 kV - H2 Línea 110 kV Maitencillo - Huasco C2",10.577999999999999,0.68100000000000005,12.05,0.747,8.9730000000000008,0.58599999999999997,11.882,0.7,12.05,11.303000000000001,11.303000000000001]
[null,null,null,"Maitencillo 110 kV - HT1 Transformador ATR1 90 MVA 220/115/13.2 kV",10.577999999999999,3.0870000000000002,12.05,3.52,8.9730000000000008,2.665,11.882,3.375,12.05,8.5300000000000011,8.5300000000000011]
[null,null,null,"Maitencillo 110 kV - H3 Línea 110 kV Maitencillo - Huasco 1",10.577999999999999,0.67200000000000004,12.05,0.73399999999999999,8.9730000000000008,0.57799999999999996,11.882,0.68899999999999995,12.05,11.316000000000001,11.316000000000001]
[null,null,null,"Maitencillo 110 kV - H4 Línea 110 kV Maitencillo - Vallenar",10.577999999999999,0.123,12.05,0.182,8.9730000000000008,0.112,11.882,0.16500000000000001,12.05,11.868,11.868]
[null,null,null,"Maitencillo 110 kV - HTX Transformador 67MVA 110/13.2kV",10.577999999999999,1.389,12.05,1.99,8.9730000000000008,1.032,11.882,2,12.05,10.06,10.06]
[null,null,null,"Maitencillo 110 kV - H5 Línea 110 kV Maitencillo - Cardones/Tap Off Punta Toro",10.577999999999999,0.98699999999999999,12.05,0.84199999999999997,8.9730000000000008,0.85399999999999998,11.882,0.94099999999999995,12.05,11.208,11.208]
[null,"Malloco",110,"Malloco 110 kV - HT1 Transformador TR01 22,4 MVA 110/12.5 kV",7.3230000000000004,0,4.2460000000000004,0,6.3440000000000003,0,6.8949999999999996,0,7.3230000000000004,7.3230000000000004,7.3230000000000004]
[null,null,null,"Malloco 110 kV - HT2 Transformador TR02 22,4 MVA 110/12.5 kV ",7.3230000000000004,0,4.2460000000000004,0,6.3440000000000003,0,6.8949999999999996,0,7.3230000000000004,7.3230000000000004,7.3230000000000004]
[null,null,null,"Malloco 110 kV - HT3 Transformador TR03 37,5 MVA 110/23.5 kV ",7.3230000000000004,0,4.2460000000000004,0,6.3440000000000003,0,6.8949999999999996,0,7.3230000000000004,7.3230000000000004,7.3230000000000004]
[null,null,null,"Malloco 110 kV - H4 Transformador TR04 50 MVA 110/23.5 kV ",7.3230000000000004,0,4.2460000000000004,0,6.3440000000000003,0,6.8949999999999996,0,7.3230000000000004,7.3230000000000004,7.3230000000000004]
[null,"Mantilhue",110,"Mantilhue 110 kV - H1 Línea 110 kV Mantilhue - Chirre",3.58,2.637,3.6819999999999999,2.2360000000000002,3.1070000000000002,2.31,3.7509999999999999,2.508,3.7509999999999999,1.4459999999999997,2.637]
[null,null,null,"Mantilhue 110 kV - H2 Línea 110 kV Mantilhue - Mocho",3.58,0.52500000000000002,3.6819999999999999,0.77900000000000003,3.1070000000000002,0.436,3.7509999999999999,0.68799999999999994,3.7509999999999999,3.0629999999999997,3.0629999999999997]
[null,"Mantos de la Luna",110,"Mantos de la Luna 110 kV - H1 Línea 110 kV Mantos de la Luna - Tap Off Barriles ",1.119,1.119,0.70899999999999996,0.70899999999999996,0.96899999999999997,0.96899999999999997,1.006,1.006,1.119,0,1.119]
[null,"Manto Verde",110,"Manto Verde 110 kV - HT1 Transformador TR1 110/13.8 kV ",2.6869999999999998,0,1.7110000000000001,0,2.3250000000000002,0,2.4500000000000002,0,2.6869999999999998,2.6869999999999998,2.6869999999999998]
[null,null,null,"Manto Verde 110 kV - HT2 Transformador TR2 110/13.8 kV",2.6869999999999998,0,1.7110000000000001,0,2.3250000000000002,0,2.4500000000000002,0,2.6869999999999998,2.6869999999999998,2.6869999999999998]
[null,null,null,"Manto Verde 110 kV - H1 Línea 110 kV Manto Verde - Diego de Almagro",2.6869999999999998,2.6869999999999998,1.7110000000000001,1.7110000000000001,2.3250000000000002,2.3250000000000002,2.4500000000000002,2.4500000000000002,2.6869999999999998,0,2.6869999999999998]
[null,null,null,"Manto Verde 110 kV - H2 Línea 110 kV Manto Verde - Planta Bombeo 2/Planta Desaladora y Planta Bombeo 1 ",2.6869999999999998,0,1.7110000000000001,0,2.3250000000000002,0,2.4500000000000002,0,2.6869999999999998,2.6869999999999998,2.6869999999999998]
[null,"Mapal",154,"Mapal 154 kV -  AT Transformador TR1 24MVA 154/15kV",12.803000000000001,0,12.618,0,10.994,0,13.03,0,13.03,13.03,13.03]
[null,"Marbella",110,"Marbella 110 kV -  H1 Línea 110 kV Marbella - Casas Viejas C1",3.9169999999999998,1.252,2.5830000000000002,0.81399999999999995,3.387,1.081,3.6989999999999998,1.179,3.9169999999999998,2.665,2.665]
[null,null,null,"Marbella 110 kV - HT1 Transformador TR1 13 MVA 110/24 kV ",3.9169999999999998,0,2.5830000000000002,0,3.387,0,3.6989999999999998,0,3.9169999999999998,3.9169999999999998,3.9169999999999998]
[null,null,null,"Marbella 110 kV - H2 Línea 110 kV Marbella - Quillota C1",3.9169999999999998,2.665,2.5830000000000002,1.7689999999999999,3.387,2.306,3.6989999999999998,2.52,3.9169999999999998,1.2519999999999998,2.665]
[null,"Marga Marga",110,"Marga Marga 110 kV - HT1 Transformador TR1 115/13.6 kV",20.652999999999999,0,14.244,0,17.934999999999999,0,18.859000000000002,0,20.652999999999999,20.652999999999999,20.652999999999999]
[null,null,null,"Marga Marga 110 kV - HT2 Transformador TR2 115/14.2 kV",20.652999999999999,0,14.244,0,17.934999999999999,0,18.859000000000002,0,20.652999999999999,20.652999999999999,20.652999999999999]
[null,null,null,"Marga Marga 110 kV - HT3 Transformador TR3 115/15.3 kV",20.652999999999999,0,14.244,0,17.934999999999999,0,18.859000000000002,0,20.652999999999999,20.652999999999999,20.652999999999999]
[null,"Mariscal",110,"Mariscal 110 kV - H1 Línea 110 kV Mariscal - La Pintana/Santa Rosa Sur 2",23.559000000000001,11.78,11.628,5.8140000000000001,20.414000000000001,10.207000000000001,20.798999999999999,10.398999999999999,23.559000000000001,11.779000000000002,11.78]
[null,null,null,"Mariscal 110 kV - H2 Línea 110 kV Mariscal - La Pintana/Santa Rosa Sur 1",23.559000000000001,11.78,11.628,5.8140000000000001,20.414000000000001,10.207000000000001,20.798999999999999,10.398999999999999,23.559000000000001,11.779000000000002,11.78]
[null,null,null,"Mariscal 110 kV - HT1 Transformador TR01 50 MVA 110/12 kV",23.559000000000001,0,11.628,0,20.414000000000001,0,20.798999999999999,0,23.559000000000001,23.559000000000001,23.559000000000001]
[null,null,null,"Mariscal 110 kV - HT2 Transformador TR02 30 MVA 110/23 kV ",23.559000000000001,0,11.628,0,20.414000000000001,0,20.798999999999999,0,23.559000000000001,23.559000000000001,23.559000000000001]
[null,null,null,"Mariscal 110 kV - HT3 Transformador TR03 30 MVA 110/23 kV ",23.559000000000001,0,11.628,0,20.414000000000001,0,20.798999999999999,0,23.559000000000001,23.559000000000001,23.559000000000001]
[null,"Mauco",110,"Mauco 110 kV - HL1 Línea 110 kV Mauco - Torquemada 1",18.643000000000001,8.4469999999999992,16.326000000000001,6.5629999999999997,16.297000000000001,7.3070000000000004,17.904,7.7309999999999999,18.643000000000001,10.196000000000002,10.196000000000002]
[null,null,null,"Mauco 110 kV - HL2 Línea 110 kV Mauco - Torquemada 2",18.643000000000001,8.4469999999999992,16.326000000000001,6.5629999999999997,16.297000000000001,7.3070000000000004,17.904,7.7309999999999999,18.643000000000001,10.196000000000002,10.196000000000002]
[null,null,null,"Mauco 110 kV - HT1 Transformador TR1 110/12 kV ",18.643000000000001,0,16.326000000000001,0,16.297000000000001,0,17.904,0,18.643000000000001,18.643000000000001,18.643000000000001]
[null,null,null,"Mauco 110 kV - HT2 Transformador TR2110/12 kV ",18.643000000000001,0,16.326000000000001,0,16.297000000000001,0,17.904,0,18.643000000000001,18.643000000000001,18.643000000000001]
[null,"Maule",154,"Maule 154 kV -  A1 Línea 154kV Maule - Itahue",11.087999999999999,3.2829999999999999,14.211,3.03,9.5839999999999996,2.8359999999999999,14.231999999999999,3.1680000000000001,14.231999999999999,11.181000000000001,11.181000000000001]
[null,null,null,"Maule 154 kV -  A2 Línea 154kV Maule - Linares/Yerbas Buenas",11.087999999999999,1.6559999999999999,14.211,1.581,9.5839999999999996,1.4279999999999999,14.231999999999999,1.637,14.231999999999999,12.63,12.63]
[null,null,null,"Maule 154 kV -  AT Interruptor común Trafo 01 y Trafo 02.",11.087999999999999,1.21,14.211,1.397,9.5839999999999996,1.048,14.231999999999999,1.409,14.231999999999999,12.822999999999999,12.822999999999999]
[null,null,null,"Maule 154 kV - HTX Transformador ATR5 300MVA 220/154/24kV",11.087999999999999,4.9820000000000002,14.211,8.2390000000000008,9.5839999999999996,4.3079999999999998,14.231999999999999,8.27,14.231999999999999,6.105999999999999,8.27]
[null,"Mayaca",110,"Mayaca 110 kV - HTX Transformador 30MVA 110/12kV",15.826000000000001,0,9.5549999999999997,0,13.676,0,14.278,0,15.826000000000001,15.826000000000001,15.826000000000001]
[null,null,null,"Mayaca 110 kV - HX1 Línea 110kV TO Mayaca - Mayaca C1",15.826000000000001,7.9130000000000003,9.5549999999999997,4.7779999999999996,13.676,6.8380000000000001,14.278,7.1390000000000002,15.826000000000001,7.9130000000000003,7.9130000000000003]
[null,null,null,"Mayaca 110 kV - HX2 Línea 110kV TO Mayaca - Mayaca C2",15.826000000000001,7.9130000000000003,9.5549999999999997,4.7770000000000001,13.676,6.8380000000000001,14.278,7.1390000000000002,15.826000000000001,7.9130000000000003,7.9130000000000003]
[null,"MDP Teno (Paneles MDP)",154,"MDP Teno (Paneles MDP) 154 kV - A1 Línea 154 kV MDP Teno - Teno",6.9740000000000002,6.9740000000000002,4.0839999999999996,4.085,6.032,6.032,6.266,6.266,6.9740000000000002,0,6.9740000000000002]
[null,"Mejillones",110,"Mejillones 110 kV - H4 Línea 110 kV Mejillones - Central Diesel Enaex 1",7.6959999999999997,6.9000000000000006E-2,8.3320000000000007,4.8000000000000001E-2,6.5490000000000004,5.3999999999999999E-2,8.2720000000000002,5.8999999999999997E-2,8.3320000000000007,8.2840000000000007,8.2840000000000007]
[null,null,null,"Mejillones 110 kV - H5 Línea 110 kV Mejillones - Chacaya C1",7.6959999999999997,0.90700000000000003,8.3320000000000007,0.93799999999999994,6.5490000000000004,0.78500000000000003,8.2720000000000002,0.93300000000000005,8.3320000000000007,7.394000000000001,7.394000000000001]
[null,null,null,"Mejillones 110 kV - H1 Línea 110 kV Mejillones - Antofagasta/Desalant 1",7.6959999999999997,2.02,8.3320000000000007,1.6479999999999999,6.5490000000000004,1.738,8.2720000000000002,1.88,8.3320000000000007,6.6840000000000011,6.6840000000000011]
[null,null,null,"Mejillones 110 kV - H2 Línea 110 kV Mejillones - El Lince ",7.6959999999999997,0,8.3320000000000007,2E-3,6.5490000000000004,0,8.2720000000000002,2E-3,8.3320000000000007,8.33,8.33]
[null,null,null,"Mejillones 110 kV - HT Transformador TR01 80/80/20 MVA 220/115/13.8 kV ",7.6959999999999997,3.9620000000000002,8.3320000000000007,4.7279999999999998,6.5490000000000004,3.4260000000000002,8.2720000000000002,4.45,8.3320000000000007,3.8220000000000001,4.7279999999999998]
[null,null,null,"Mejillones 110 kV - H3/HT2 Transformador TR03 30/25 MVA 110/13.8 kV",7.6959999999999997,0.80400000000000005,8.3320000000000007,1.02,6.5490000000000004,0.60399999999999998,8.2720000000000002,0.98599999999999999,8.3320000000000007,7.3120000000000012,7.3120000000000012]
[null,"Melipeuco",110,"Melipeuco 110 kV - H1 Línea 110 kV Melipeuco - Río Tolten/Cunco",1.534,1.1619999999999999,1.78,0.996,1.3120000000000001,1.006,1.776,1.091,1.78,0.78400000000000003,1.1619999999999999]
[null,"Melipulli",110,"Melipulli 110 kV - H1 Línea 110 kV Melipulli - Alto Bonito/Central Trapén/Molinos (Enlasa) 1",4.7409999999999997,1.952,5.4829999999999997,1.631,4.0839999999999996,1.679,5.3280000000000003,1.79,5.4829999999999997,3.8519999999999994,3.8519999999999994]
[null,null,null,"Melipulli 110 kV - HT11 Transformador T11 60 MVA 230/115/69 kV",4.7409999999999997,1.978,5.4829999999999997,3.1179999999999999,4.0839999999999996,1.7090000000000001,5.3280000000000003,2.9159999999999999,5.4829999999999997,2.7629999999999999,3.1179999999999999]
[null,"Metro",110,"Metro 110 kV - ITRA1 Transformador TRA1 110/20 kV ",48.28,0,38.523000000000003,0,41.758000000000003,0,46.122,0,48.28,48.28,48.28]
[null,null,null,"Metro 110 kV - ITRB1 Transformador TRB2 110/20 kV ",48.28,0,38.523000000000003,0,41.758000000000003,0,46.122,0,48.28,48.28,48.28]
[null,null,null,"Metro 110 kV - ITRC1 Transformador TRC1 110/20 kV",48.28,0,38.523000000000003,0,41.758000000000003,0,46.122,0,48.28,48.28,48.28]
[null,"Minera Franke",110,"Minera Franke 110 kV -  En Barra",1.603,0,1.0469999999999999,0,1.3879999999999999,0,1.5289999999999999,0,1.603,1.603,1.603]
[null,"Minera Maricunga",110,"Minera Maricunga 110 kV - 00-BK-101 Transformador  ATR1 110/23 kV",1.163,0,0.67600000000000005,0,1.006,0,1.0409999999999999,0,1.163,1.163,1.163]
[null,null,null,"Minera Maricunga 110 kV - 00-BK-102 Transformador ATR2 110/23 kV N°2",1.163,0,0.67600000000000005,0,1.006,0,1.0409999999999999,0,1.163,1.163,1.163]
[null,"Minera Teck CDA",110,"Minera Teck CDA 110 kV - H1 Transformador TR 12/15 MVA 220/13.2 kV",3.4359999999999999,3.4359999999999999,2.222,2.2229999999999999,2.964,2.964,3.2320000000000002,3.2330000000000001,3.4359999999999999,0,3.4359999999999999]
[null,"Minera Valle Central",154,"Minera Valle Central 154 kV - AT1 Transformador TR1 154/4,16kV",10.417999999999999,0.20799999999999999,8.56,0.11600000000000001,9.0500000000000007,0.185,10.465,0.191,10.465,10.273999999999999,10.273999999999999]
[null,null,null,"Minera Valle Central 154 kV - AT2 Transformador TR2 154/4,16kV",10.417999999999999,0.20799999999999999,8.56,0.11600000000000001,9.0500000000000007,0.185,10.465,0.191,10.465,10.273999999999999,10.273999999999999]
[null,null,null,"Minera Valle Central 154 kV - AT3 Transformador 154/23 kV N°3 ",10.417999999999999,4.2999999999999997E-2,8.56,2.3E-2,9.0500000000000007,3.6999999999999998E-2,10.465,3.9E-2,10.465,10.426,10.426]
[null,"Minero",110,"Minero 110 kV - H1 Línea 110 kV Minero - Colón 1",19.495000000000001,0,21.463999999999999,0,16.963999999999999,0,20.762,0,21.463999999999999,21.463999999999999,21.463999999999999]
[null,null,null,"Minero 110 kV - H2 Línea 110 kV Minero - Colón 2",19.495000000000001,0,21.463999999999999,0,16.963999999999999,0,20.762,0,21.463999999999999,21.463999999999999,21.463999999999999]
[null,null,null,"Minero 110 kV - H3 Línea 110 kV Minero - Cordillera 1",19.495000000000001,0,21.463999999999999,0,16.963999999999999,0,20.762,0,21.463999999999999,21.463999999999999,21.463999999999999]
[null,null,null,"Minero 110 kV - H4 Línea 110 kV Minero - Cordillera 2",19.495000000000001,0,21.463999999999999,0,16.963999999999999,0,20.762,0,21.463999999999999,21.463999999999999,21.463999999999999]
[null,null,null,"Minero 110 kV - H5 Línea 110 kV Minero - Sauzal 3",19.495000000000001,2.3849999999999998,21.463999999999999,2.2669999999999999,16.963999999999999,2.0539999999999998,20.762,2.3180000000000001,21.463999999999999,19.196999999999999,19.196999999999999]
[null,null,null,"Minero 110 kV - H6 Línea 110 kV Minero - Interconexión Chacayes/Sauzal 1",19.495000000000001,2.589,21.463999999999999,2.5099999999999998,16.963999999999999,2.2469999999999999,20.762,2.5329999999999999,21.463999999999999,18.954000000000001,18.954000000000001]
[null,null,null,"Minero 110 kV - H7 Línea 110 kV Minero - Interconexión Chacayes/Sauzal 2",19.495000000000001,2.589,21.463999999999999,2.5099999999999998,16.963999999999999,2.2469999999999999,20.762,2.5329999999999999,21.463999999999999,18.954000000000001,18.954000000000001]
[null,null,null,"Minero 110 kV - H8 Línea 110 kV Minero -  Sewell 1",19.495000000000001,0,21.463999999999999,0,16.963999999999999,0,20.762,0,21.463999999999999,21.463999999999999,21.463999999999999]
[null,null,null,"Minero 110 kV - H9 Línea 110 kV Minero -  Sewell 2",19.495000000000001,0,21.463999999999999,0,16.963999999999999,0,20.762,0,21.463999999999999,21.463999999999999,21.463999999999999]
[null,null,null,"Minero 110 kV - HR Paño Acoplador ",19.495000000000001,0,21.463999999999999,0,16.963999999999999,0,20.762,0,21.463999999999999,21.463999999999999,21.463999999999999]
[null,null,null,"Minero 110 kV - HT1 Transformador  TR1 230/115/13.8 kV ",19.495000000000001,3.9980000000000002,21.463999999999999,4.7480000000000002,16.963999999999999,3.49,20.762,4.4610000000000003,21.463999999999999,16.715999999999998,16.715999999999998]
[null,null,null,"Minero 110 kV - HT2 Transformador  TR2 230/115/13.8 kV ",19.495000000000001,3.9980000000000002,21.463999999999999,4.7480000000000002,16.963999999999999,3.49,20.762,4.4610000000000003,21.463999999999999,16.715999999999998,16.715999999999998]
[null,null,null,"Minero 110 kV - HT3 Transformador  TR3  230/115/13.8 kV ",19.495000000000001,3.9980000000000002,21.463999999999999,4.7480000000000002,16.963999999999999,3.49,20.762,4.4610000000000003,21.463999999999999,16.715999999999998,16.715999999999998]
[null,null,null,"Minero 110 kV - H10 Línea 110 kV Minero - El Cobre (Codelco) 1",19.495000000000001,0,21.463999999999999,0,16.963999999999999,0,20.762,0,21.463999999999999,21.463999999999999,21.463999999999999]
[null,null,null,"Minero 110 kV - H11 Línea 110 kV Minero - El Cobre (Codelco) 2",19.495000000000001,0,21.463999999999999,0,16.963999999999999,0,20.762,0,21.463999999999999,21.463999999999999,21.463999999999999]
[null,"Minsal",110,"Minsal 110 kV - H1 Transformador TR01 25/20 MVA 110/23 kV ",1.36,0,1.153,0,1.177,0,1.286,0,1.36,1.36,1.36]
[null,null,null,"Minsal 110 kV - H2 Transformador TR02 30 MVA 110/23 kV",1.36,0,1.153,0,1.177,0,1.286,0,1.36,1.36,1.36]
[null,"Miraflores",110,"Miraflores 110 kV - H3 Línea 110 kV Miraflores - San Pedro (AES GENER) 1",24.66,3.9260000000000002,18.044,2.8359999999999999,21.427,3.4079999999999999,22.559000000000001,3.673,24.66,20.734000000000002,20.734000000000002]
[null,null,null,"Miraflores 110 kV - H4 Línea 110 kV Miraflores - San Pedro (AES GENER) 2",24.66,3.9260000000000002,18.044,2.8359999999999999,21.427,3.4079999999999999,22.559000000000001,3.673,24.66,20.734000000000002,20.734000000000002]
[null,null,null,"Miraflores 110 kV - H5 Línea 110 kV Miraflores - Agua Santa 3",24.66,5.68,18.044,3.855,21.427,4.9219999999999997,22.559000000000001,5.0999999999999996,24.66,18.98,18.98]
[null,null,null,"Miraflores 110 kV - H6 Línea 110 kV Miraflores - Agua Santa 4",24.66,5.68,18.044,3.855,21.427,4.9219999999999997,22.559000000000001,5.0999999999999996,24.66,18.98,18.98]
[null,null,null,"Miraflores 110 kV - HS Paño Acoplador ",24.66,0,18.044,1E-3,21.427,0,22.559000000000001,1E-3,24.66,24.66,24.66]
[null,null,null,"Miraflores 110 kV - HT1 Transformador TR1 110/12 kV ",24.66,0,18.044,0,21.427,0,22.559000000000001,0,24.66,24.66,24.66]
[null,null,null,"Miraflores 110 kV - HT2 Transformador TR2 110/12 kV ",24.66,0,18.044,0,21.427,0,22.559000000000001,0,24.66,24.66,24.66]
[null,null,null,"Miraflores 110 kV - HT3 Transformador TR3 110/13.6 kV",24.66,0,18.044,0,21.427,0,22.559000000000001,0,24.66,24.66,24.66]
[null,null,null,"Miraflores 110 kV - H1 Línea 110 kV Miraflores - Ventanas/Torquemada 1",24.66,2.843,18.044,2.3879999999999999,21.427,2.4860000000000002,22.559000000000001,2.605,24.66,21.817,21.817]
[null,null,null,"Miraflores 110 kV - H2 Línea 110 kV Miraflores - Ventanas/Torquemada 2",24.66,2.843,18.044,2.3879999999999999,21.427,2.4860000000000002,22.559000000000001,2.605,24.66,21.817,21.817]
[null,null,null,"Miraflores 110 kV - H10 Línea 110 kV Miraflores -  Marga Marga 1",24.66,0,18.044,1E-3,21.427,0,22.559000000000001,1E-3,24.66,24.66,24.66]
[null,null,null,"Miraflores 110 kV - H11 Línea 110 kV Miraflores -  Marga Marga 2",24.66,0,18.044,1E-3,21.427,0,22.559000000000001,1E-3,24.66,24.66,24.66]
[null,"Mocho",110,"Mocho 110 kV - H1 Línea 110 kV Mocho - Mantilhue",2.9780000000000002,2.4430000000000001,3.222,2.1680000000000001,2.5739999999999998,2.1280000000000001,3.2759999999999998,2.3769999999999998,3.2759999999999998,1.0539999999999998,2.4430000000000001]
[null,"Molinos (Enlasa)",110,"Molinos (Enlasa) 110 kV - HT Transformador TR1 100/80 MVA 110/23 kV ",4.7089999999999996,1.55,4.1859999999999999,0.94199999999999995,4.0579999999999998,1.34,4.5199999999999996,1.373,4.7089999999999996,3.2439999999999998,3.2439999999999998]
[null,null,null,"Molinos (Enlasa) 110 kV - H1 Línea 110 kV Molinos (Enlasa) - Alto Bonito 1",4.7089999999999996,2.073,4.1859999999999999,2.2759999999999998,4.0579999999999998,1.7889999999999999,4.5199999999999996,2.1949999999999998,4.7089999999999996,2.6359999999999997,2.6359999999999997]
[null,null,null,"Molinos (Enlasa) 110 kV - H2 Línea 110 kV Molinos (Enlasa) -  El Empalme 1",4.7089999999999996,1.0980000000000001,4.1859999999999999,0.97699999999999998,4.0579999999999998,0.94199999999999995,4.5199999999999996,1.028,4.7089999999999996,3.6109999999999998,3.6109999999999998]
[null,"Monterrico",154,"Monterrico 154 kV - A1 Línea 154kV Monterrico - Parral",6.3529999999999998,1.6779999999999999,6.1509999999999998,1.4930000000000001,5.4740000000000002,1.4510000000000001,6.4459999999999997,1.625,6.4459999999999997,4.8209999999999997,4.8209999999999997]
[null,null,null,"Monterrico 154 kV - AX Línea 154kV Monterrico - Pueblo Seco",6.3529999999999998,3.1,6.1509999999999998,2.3929999999999998,5.4740000000000002,2.6680000000000001,6.4459999999999997,2.8119999999999998,6.4459999999999997,3.758,3.758]
[null,null,null,"Monterrico 154 kV - ATX Transformador TR2 60/75 MVA 154/66/13,2kV",6.3529999999999998,0.79500000000000004,6.1509999999999998,1.137,5.4740000000000002,0.68400000000000005,6.4459999999999997,1.091,6.4459999999999997,5.5579999999999998,5.5579999999999998]
[null,null,null,"Monterrico 154 kV - AT1 Transformador TR1 75MVA 154/66/13,2kV",6.3529999999999998,0.79500000000000004,6.1509999999999998,1.137,5.4740000000000002,0.68400000000000005,6.4459999999999997,1.091,6.4459999999999997,5.5579999999999998,5.5579999999999998]
[null,"Muelle",110,"Muelle 110 kV - H1 Línea 110 kV Muelle - Chacaya C1",2.2229999999999999,1.7170000000000001,1.401,1.1890000000000001,1.9239999999999999,1.486,2.0670000000000002,1.625,2.2229999999999999,0.50599999999999978,1.7170000000000001]
[null,null,null,"Muelle 110 kV - H4 Línea 110 kV Muelle - Tap Off Antucoya/Tap Off Licancabur/Tap Off Sairecabur 1",2.2229999999999999,0.50600000000000001,1.401,0.21199999999999999,1.9239999999999999,0.438,2.0670000000000002,0.44600000000000001,2.2229999999999999,1.7169999999999999,1.7169999999999999]
[null,null,null,"Muelle 110 kV - H2 Transformador Muelle 110/24 kV N°1",2.2229999999999999,0,1.401,0,1.9239999999999999,0,2.0670000000000002,0,2.2229999999999999,2.2229999999999999,2.2229999999999999]
[null,"Ochagavia",110,"Ochagavia 110 kV - H1 Línea 110 kV Ochagavia - Metro 1",48.595999999999997,19.863,29.042000000000002,12.487,42.06,17.158000000000001,43.368000000000002,17.530999999999999,48.595999999999997,28.732999999999997,28.732999999999997]
[null,null,null,"Ochagavia 110 kV - H2 Línea 110 kV Ochagavia - Florida 2",48.595999999999997,4.6589999999999998,29.042000000000002,2.5209999999999999,42.06,4.0339999999999998,43.368000000000002,4.1349999999999998,48.595999999999997,43.936999999999998,43.936999999999998]
[null,null,null,"Ochagavia 110 kV - H3 Línea 110 kV Ochagavia - Florida 1",48.595999999999997,4.6589999999999998,29.042000000000002,2.5209999999999999,42.06,4.0339999999999998,43.368000000000002,4.1349999999999998,48.595999999999997,43.936999999999998,43.936999999999998]
[null,null,null,"Ochagavia 110 kV - H4 Línea 110 kV Ochagavia - Chena 1",48.595999999999997,9.7579999999999991,29.042000000000002,5.7670000000000003,42.06,8.4619999999999997,43.368000000000002,8.8179999999999996,48.595999999999997,38.837999999999994,38.837999999999994]
[null,null,null,"Ochagavia 110 kV - H5 Línea 110 kV Ochagavia - Chena 2",48.595999999999997,9.7579999999999991,29.042000000000002,5.7670000000000003,42.06,8.4619999999999997,43.368000000000002,8.8179999999999996,48.595999999999997,38.837999999999994,38.837999999999994]
[null,null,null,"Ochagavia 110 kV - HT1 Transformador TR01 40 MVA 105/12 kV ",48.595999999999997,0,29.042000000000002,0,42.06,0,43.368000000000002,0,48.595999999999997,48.595999999999997,48.595999999999997]
[null,null,null,"Ochagavia 110 kV - AC1 Banco de Condensadores 1 ",48.595999999999997,0,29.042000000000002,0,42.06,0,43.368000000000002,0,48.595999999999997,48.595999999999997,48.595999999999997]
[null,null,null,"Ochagavia 110 kV - HT2 Transformador TR02 50 MVA  110/12.5 kV ",48.595999999999997,0,29.042000000000002,0,42.06,0,43.368000000000002,0,48.595999999999997,48.595999999999997,48.595999999999997]
[null,"Ovalle",110,"Ovalle 110 kV - H2 Línea 110 kV Ovalle -  La Ruca C2",4.9450000000000003,1.583,4.1959999999999997,1.155,4.242,1.3640000000000001,4.9909999999999997,1.496,4.9909999999999997,3.4949999999999997,3.4949999999999997]
[null,null,null,"Ovalle 110 kV - HT3 Transformador TR03 30 MVA 110/66/23 kV",4.9450000000000003,0.39,4.1959999999999997,0.38100000000000001,4.242,0.32800000000000001,4.9909999999999997,0.41099999999999998,4.9909999999999997,4.58,4.58]
[null,null,null,"Ovalle 110 kV - H1 Línea 110 kV Ovalle - Punitaqui 1",4.9450000000000003,1.1619999999999999,4.1959999999999997,0.878,4.242,0.99299999999999999,4.9909999999999997,1.1060000000000001,4.9909999999999997,3.8849999999999998,3.8849999999999998]
[null,null,null,"Ovalle 110 kV - HT4 Transformador TR 04 60 MVA 110/69/23 kV ",4.9450000000000003,0.253,4.1959999999999997,0.64400000000000002,4.242,0.21299999999999999,4.9909999999999997,0.54500000000000004,4.9909999999999997,4.6920000000000002,4.6920000000000002]
[null,null,null,"Ovalle 110 kV - H3 Línea 110 kV Ovalle -  La Ruca C1",4.9450000000000003,1.5720000000000001,4.1959999999999997,1.155,4.242,1.355,4.9909999999999997,1.4930000000000001,4.9909999999999997,3.4979999999999993,3.4979999999999993]
[null,"Oxy",154,"Oxy 154 kV - A Transformador 154/69/13.8 kV N°1 ; Transformador 154/69/13.8 kV N°2",13.648,13.648,14.577,14.551,11.715,11.715,14.26,14.249000000000001,14.577,2.5999999999999801E-2,14.551]
[null,"Pacífico",110,"Pacífico 110 kV - HT1 Transformador TRAFO 33/25 MVA 110/13.8 kV ",3.3340000000000001,0,3.1379999999999999,0,2.85,0,3.2839999999999998,0,3.3340000000000001,3.3340000000000001,3.3340000000000001]
[null,"Padre Hurtado",110,"Padre Hurtado 110 kV - HTX Transformador TR01 30 MVA 110/23 kV",17.077000000000002,0,8.3629999999999995,0,14.791,0,15.12,0,17.077000000000002,17.077000000000002,17.077000000000002]
[null,null,null,"Padre Hurtado 110 kV - HX Línea 110 kV Padre Hurtado - Santa Marta",17.077000000000002,17.077000000000002,8.3629999999999995,8.3629999999999995,14.791,14.791,15.12,15.12,17.077000000000002,0,17.077000000000002]
[null,"Paine",154,"Paine 154 kV - AT Transformador TR1 56MVA 154/66/13,2kV",12.507999999999999,11.858000000000001,9.9610000000000003,9.6170000000000009,10.863,10.3,11.622,11.073,12.507999999999999,0.64999999999999858,11.858000000000001]
[null,"Pajaritos",110,"Pajaritos 110 kV - H1 Línea 110 kV Pajaritos - Cerro Navia (Enel)/ Chena 1",34.713999999999999,17.356999999999999,16.937000000000001,8.468,30.062999999999999,15.032,30.722000000000001,15.361000000000001,34.713999999999999,17.356999999999999,17.356999999999999]
[null,null,null,"Pajaritos 110 kV - H2 Línea 110 kV Pajaritos - Cerro Navia (Enel)/Chena 2",34.713999999999999,17.356999999999999,16.937000000000001,8.468,30.062999999999999,15.032,30.722000000000001,15.361000000000001,34.713999999999999,17.356999999999999,17.356999999999999]
[null,null,null,"Pajaritos 110 kV - HT1 Transformador Pajaritos 110/12.5 kV N°1",34.713999999999999,0,16.937000000000001,0,30.062999999999999,0,30.722000000000001,0,34.713999999999999,34.713999999999999,34.713999999999999]
[null,null,null,"Pajaritos 110 kV - HT2 Transformador Pajaritos 110/12.5 kV N°2",34.713999999999999,0,16.937000000000001,0,30.062999999999999,0,30.722000000000001,0,34.713999999999999,34.713999999999999,34.713999999999999]
[null,null,null,"Pajaritos 110 kV - HT3 Transformador Pajaritos 110/23.5 kV N°3",34.713999999999999,0,16.937000000000001,0,30.062999999999999,0,30.722000000000001,0,34.713999999999999,34.713999999999999,34.713999999999999]
[null,null,null,"Pajaritos 110 kV - H4 Transformador Pajaritos 110/23.5 kV N°4",34.713999999999999,0,16.937000000000001,0,30.062999999999999,0,30.722000000000001,0,34.713999999999999,34.713999999999999,34.713999999999999]
[null,"Pajonales (Infotécnica interna)",110,"Pajonales (Infotécnica interna) 110 kV -  En Barra",2.6880000000000002,0,2.0579999999999998,0,2.323,0,2.645,0,2.6880000000000002,2.6880000000000002,2.6880000000000002]
[null,"Palafitos",110,"Palafitos 110 kV - HT1 Transformador Trafo1 25/33MVA 110/13,8 kV",3.0139999999999998,0,2.948,0,2.58,0,3.0009999999999999,0,3.0139999999999998,3.0139999999999998,3.0139999999999998]
[null,"Palmar",110,"Palmar 110 kV - HT1 Transformador 15MVA 110/13.2kV T1",2.7970000000000002,0.192,2.5329999999999999,0.114,2.4569999999999999,0.16800000000000001,2.8029999999999999,0.17,2.8029999999999999,2.633,2.633]
[null,null,null,"Palmar 110 kV - HT2 Transformador 15MVA 110/13.2kVT2",2.7970000000000002,0.192,2.5329999999999999,0.114,2.4569999999999999,0.16800000000000001,2.8029999999999999,0.17,2.8029999999999999,2.633,2.633]
[null,null,null,"Palmar 110 kV - H1 Línea 110kV PALMAR - COPIHUES",2.7970000000000002,2.423,2.5329999999999999,2.3109999999999999,2.4569999999999999,2.1320000000000001,2.8029999999999999,2.5070000000000001,2.8029999999999999,0.37400000000000011,2.5070000000000001]
[null,"Pan de Azúcar",110,"Pan de Azúcar 110 kV - HT4 Transformador 150 MVA 220/110/13,2kV ATR4  ",14.861000000000001,3.8170000000000002,19.399999999999999,4.3570000000000002,12.805,3.3079999999999998,19.456,4.2460000000000004,19.456,15.209999999999999,15.209999999999999]
[null,null,null,"Pan de Azúcar 110 kV - HT1 Transformador TR01 48MVA 110/110kV",14.861000000000001,0.62,19.399999999999999,3.9649999999999999,12.805,0.53400000000000003,19.456,5.5430000000000001,19.456,15.434999999999999,15.434999999999999]
[null,null,null,"Pan de Azúcar 110 kV - HT3 Transformador ATR3 75MVA 220/110/13,2kV y ATR9 90 MVA 220/110/13.2 kV",14.861000000000001,4.101,19.399999999999999,4.4189999999999996,12.805,3.5539999999999998,19.456,4.3730000000000002,19.456,15.082999999999998,15.082999999999998]
[null,null,null,"Pan de Azúcar 110 kV - H2 Línea 110 kV Pan de Azucar - Maitencillo - Las Compañias C1",14.861000000000001,0.62,19.399999999999999,0.53900000000000003,12.805,0.53400000000000003,19.456,0.57799999999999996,19.456,18.878,18.878]
[null,null,null,"Pan de Azúcar 110 kV - HT7 Transformador TR7 35MVA 110/110kV",14.861000000000001,0,19.399999999999999,2E-3,12.805,0,19.456,3.0000000000000001E-3,19.456,19.452999999999999,19.452999999999999]
[null,null,null,"Pan de Azúcar 110 kV - H1 Línea 110 kV Pan de Azucar - Ovalle (El Peñon)",14.861000000000001,1.2030000000000001,19.399999999999999,1.1000000000000001,12.805,1.006,19.456,1.161,19.456,18.299999999999997,18.299999999999997]
[null,null,null,"Pan de Azúcar 110 kV - H6 Línea 110 kV Pan de Azucar - San Joaquin",14.861000000000001,0,19.399999999999999,0,12.805,0,19.456,0,19.456,19.456,19.456]
[null,null,null,"Pan de Azúcar 110 kV - HT2 Transformador T10 60MVA 110/66/23kV TR2 60 MVA 110/66/23 kV",14.861000000000001,0,19.399999999999999,0.10100000000000001,12.805,0,19.456,0.14799999999999999,19.456,19.308,19.308]
[null,null,null,"Pan de Azúcar 110 kV - HT10 Transformador 220/110/13.2 kV N°10",14.861000000000001,4.0570000000000004,19.399999999999999,4.4130000000000003,12.805,3.516,19.456,4.3630000000000004,19.456,15.093,15.093]
[null,null,null,"Pan de Azúcar 110 kV - H8 Línea 110 kV Pan de Azucar - El Peñon C2",14.861000000000001,1.2030000000000001,19.399999999999999,1.1000000000000001,12.805,1.006,19.456,1.161,19.456,18.299999999999997,18.299999999999997]
[null,null,null,"Pan de Azúcar 110 kV - HT8/11 TR8 - TR11",14.861000000000001,0,19.399999999999999,0,12.805,0,19.456,0,19.456,19.456,19.456]
[null,null,null,"Pan de Azúcar 110 kV - HT11 Transformador TR11 24MVA 110/13,8kV",14.861000000000001,0,19.399999999999999,0,12.805,0,19.456,0,19.456,19.456,19.456]
[null,null,null,"Pan de Azúcar 110 kV - HT8 Transformador TR8 24MVA 110/13,8kV",14.861000000000001,0,19.399999999999999,0,12.805,0,19.456,0,19.456,19.456,19.456]
[null,"Panamericana",110,"Panamericana 110 kV - HT1 Transformador TR01 25MVA 110/13,2kV",51.774999999999999,0,40.804000000000002,0,44.845999999999997,0,48.097999999999999,0,51.774999999999999,51.774999999999999,51.774999999999999]
[null,null,null,"Panamericana 110 kV - HT2 Transformador TR02 22,4MVA 110/12,5kV",51.774999999999999,0,40.804000000000002,0,44.845999999999997,0,48.097999999999999,0,51.774999999999999,51.774999999999999,51.774999999999999]
[null,null,null,"Panamericana 110 kV - H4 Transformador TR04 22,4MVA 110/12,5kV",51.774999999999999,0,40.804000000000002,0,44.845999999999997,0,48.097999999999999,0,51.774999999999999,51.774999999999999,51.774999999999999]
[null,"Pargua",110,"Pargua 110 kV - HTX Transformador 60 MVA 230/115/13.8 kV",4.4580000000000002,1.778,5.048,2.673,3.823,1.5229999999999999,4.9660000000000002,2.484,5.048,2.68,2.68]
[null,null,null,"Pargua 110 kV - HX1 Línea 110 kV Colaco-Pargua",4.4580000000000002,1.972,5.048,1.754,3.823,1.7050000000000001,4.9660000000000002,1.869,5.048,3.294,3.294]
[null,null,null,"Pargua 110 kV - HX2 Línea 110kV Pargua - Ancud 110 kV",4.4580000000000002,0.72399999999999998,5.048,0.63500000000000001,3.823,0.60799999999999998,4.9660000000000002,0.68700000000000006,5.048,4.4130000000000003,4.4130000000000003]
[null,"Parral",154,"Parral 154 kV - A2 Línea 154kV Parral  - Monterrico",5.4269999999999996,1.9850000000000001,8.1210000000000004,1.978,4.6879999999999997,1.7130000000000001,9.4009999999999998,1.9850000000000001,9.4009999999999998,7.4159999999999995,7.4159999999999995]
[null,null,null,"Parral 154 kV - A1 Línea 154kV Parral  - Itahue/Linares",5.4269999999999996,2.36,8.1210000000000004,2.3559999999999999,4.6879999999999997,2.04,9.4009999999999998,2.36,9.4009999999999998,7.0410000000000004,7.0410000000000004]
[null,null,null,"Parral 154 kV - AT1 Transformador TR1 75MVA 154/66/13,2kV",5.4269999999999996,0.18,8.1210000000000004,2.8860000000000001,4.6879999999999997,0.155,9.4009999999999998,5.5270000000000001,9.4009999999999998,5.2469999999999999,5.5270000000000001]
[null,null,null,"Parral 154 kV - AT2 Transformador TR2 56/56/22,4MVA 154/66/13,2kV",5.4269999999999996,0.90500000000000003,8.1210000000000004,0.90300000000000002,4.6879999999999997,0.78200000000000003,9.4009999999999998,0.90500000000000003,9.4009999999999998,8.4960000000000004,8.4960000000000004]
[null,"Pellets",110,"Pellets 110 kV - H1 Línea 110 kV Pellets - Central Huasco C1",5.8710000000000004,2.9359999999999999,6.38,3.19,5.0380000000000003,2.5190000000000001,6.5270000000000001,3.2639999999999998,6.5270000000000001,3.2630000000000003,3.2639999999999998]
[null,null,null,"Pellets 110 kV - H2 Línea 110 kV Pellets - Central Huasco C2",5.8710000000000004,2.9359999999999999,6.38,3.19,5.0380000000000003,2.5190000000000001,6.5270000000000001,3.2639999999999998,6.5270000000000001,3.2630000000000003,3.2639999999999998]
[null,"Peñablanca",110,"Peñablanca 110 kV - H1 Línea 110 kV Peñablanca - San Pedro C2",11.484,5.2930000000000001,6.4059999999999997,2.8820000000000001,9.9469999999999992,4.5880000000000001,10.294,4.7510000000000003,11.484,6.1909999999999998,6.1909999999999998]
[null,null,null,"Peñablanca 110 kV - H2 Línea 110 kV Peñablanca - Miraflores C1",11.484,6.1959999999999997,6.4059999999999997,3.5259999999999998,9.9469999999999992,5.3630000000000004,10.294,5.5449999999999999,11.484,5.2880000000000003,6.1959999999999997]
[null,null,null,"Peñablanca 110 kV - HT2 Transformador TR2 25MVA110/12,5 kV ",11.484,0,6.4059999999999997,0,9.9469999999999992,0,10.294,0,11.484,11.484,11.484]
[null,"Petrodow",154,"Petrodow 154 kV - CT Transformador Petrodow 154/4.16 kV",13.263999999999999,0,13.787000000000001,0,11.388,0,13.680999999999999,0,13.787000000000001,13.787000000000001,13.787000000000001]
[null,"Pid Pid",110,"Pid Pid 110 kV - H1 Línea 110 kV Pid Pid - Gamboa",4.7190000000000003,3.0350000000000001,4.7060000000000004,3.2749999999999999,3.95,2.5830000000000002,4.7430000000000003,3.1429999999999998,4.7430000000000003,1.6840000000000002,3.2749999999999999]
[null,null,null,"Pid Pid 110 kV - HT1 Transformador TR1 16MVA115/69/24/13.8 kV",4.7190000000000003,0,4.7060000000000004,0,3.95,0,4.7430000000000003,0,4.7430000000000003,4.7430000000000003,4.7430000000000003]
[null,null,null,"Pid Pid 110 kV - H2 Línea 110 kV Pid Pid - Chiloe/ Dalcahue ",4.7190000000000003,1.7050000000000001,4.7060000000000004,1.4419999999999999,3.95,1.3779999999999999,4.7430000000000003,1.601,4.7430000000000003,3.2640000000000002,3.2640000000000002]
[null,"Pirque",110,"Pirque 110 kV - HX1 Línea 110 kV Pirque - CMPC Puente Alto",3.2410000000000001,1.1619999999999999,3.472,1.573,2.867,1.0609999999999999,3.3959999999999999,1.3959999999999999,3.472,2.0790000000000002,2.0790000000000002]
[null,null,null,"Pirque 110 kV - HX2 Línea 110 kV Pirque - Maipo",3.2410000000000001,2.081,3.472,1.9,2.867,1.8109999999999999,3.3959999999999999,2.02,3.472,1.5720000000000001,2.081]
[null,null,null,"Pirque 110 kV - HTX Transformador TR2 4/5MVA 110/13.2 kV ",3.2410000000000001,0,3.472,0,2.867,0,3.3959999999999999,0,3.472,3.472,3.472]
[null,null,null,"Pirque 110 kV - HT Transformador TR1 3.75/4.2/5.2MVA 110/13.2 kV ",3.2410000000000001,0,3.472,0,2.867,0,3.3959999999999999,0,3.472,3.472,3.472]
[null,"Placilla",110,"Placilla 110 kV - HX1 Línea 110 kV Placilla - Agua Santa",20.552,9.2439999999999998,16.937000000000001,7.52,17.82,8.0169999999999995,19.376000000000001,8.827,20.552,11.308,11.308]
[null,null,null,"Placilla 110 kV - HX2 Línea 110 kV Agua Santa - Placilla C2 ",20.552,11.162000000000001,16.937000000000001,9.3290000000000006,17.82,9.6790000000000003,19.376000000000001,10.419,20.552,9.3899999999999988,11.162000000000001]
[null,null,null,"Placilla 110 kV - HT2 Transformador TR2 30MVA 110/12kV ",20.552,0.19400000000000001,16.937000000000001,0.107,17.82,0.16600000000000001,19.376000000000001,0.16800000000000001,20.552,20.358000000000001,20.358000000000001]
[null,"Planta de Óxidos",110,"Planta de Óxidos 110 kV - HT1 Transformador ATR1 4MVA 110/33 kV N°1",1.4450000000000001,0,1.107,0,1.2509999999999999,0,1.405,0,1.4450000000000001,1.4450000000000001,1.4450000000000001]
[null,null,null,"Planta de Óxidos 110 kV - H2 Línea 110 kV Planta de Oxidos - Las Luces",1.4450000000000001,0,1.107,3.0000000000000001E-3,1.2509999999999999,0,1.405,2E-3,1.4450000000000001,1.4450000000000001,1.4450000000000001]
[null,"Planta Matta ",110,"Planta Matta  110 kV - HT TR - Cardones",4.4059999999999997,0,3.2850000000000001,0,3.8090000000000002,0,4.2080000000000002,0,4.4059999999999997,4.4059999999999997,4.4059999999999997]
[null,"Plantas",110,"Plantas 110 kV - HT1 Transformador T1 16-20-24MVA 110-24/13,8kV",7.5170000000000003,0,7.7629999999999999,0,6.4870000000000001,0,7.8369999999999997,0,7.8369999999999997,7.8369999999999997,7.8369999999999997]
[null,null,null,"Plantas 110 kV - HTX Transformador 150MVA 220/110/13,8 kV",7.5170000000000003,4.0830000000000002,7.7629999999999999,4.7469999999999999,6.4870000000000001,3.5219999999999998,7.8369999999999997,4.4260000000000002,7.8369999999999997,3.4340000000000002,4.7469999999999999]
[null,null,null,"Plantas 110 kV - HX Línea 110 kV Plantas - Tierra Amarilla",7.5170000000000003,3.5449999999999999,7.7629999999999999,3.097,6.4870000000000001,3.06,7.8369999999999997,3.4159999999999999,7.8369999999999997,4.6660000000000004,4.6660000000000004]
[null,"Playa Ancha",110,"Playa Ancha 110 kV - HT1 Transformador TR1 22,4MVA 110/12 kV N°1",14.333,0,11.83,0,12.425000000000001,0,13.756,0,14.333,14.333,14.333]
[null,null,null,"Playa Ancha 110 kV - HT2 Transformador TR2 22,4MVA 110/12 kV N°2",14.333,0,11.83,0,12.425000000000001,0,13.756,0,14.333,14.333,14.333]
[null,"Portezuelo",110,"Portezuelo 110 kV - H1 Línea 110kV Litueche - Portezuelo",4.7,2.5409999999999999,4.4660000000000002,2.056,4.07,2.2010000000000001,4.7380000000000004,2.3809999999999998,4.7380000000000004,2.41,2.5409999999999999]
[null,null,null,"Portezuelo 110 kV - HT2 Transformador TR2 15/18MVA 110/66/13.8 kV N°2",4.7,0.751,4.4660000000000002,0.85199999999999998,4.07,0.65,4.7380000000000004,0.84399999999999997,4.7380000000000004,3.9490000000000003,3.9490000000000003]
[null,null,null,"Portezuelo 110 kV - HT1 Transformador TR1 75 MVA 110/66/13.8 kV N°1",4.7,1.4279999999999999,4.4660000000000002,1.5760000000000001,4.07,1.2370000000000001,4.7380000000000004,1.52,4.7380000000000004,3.2720000000000002,3.2720000000000002]
[null,"Potrerillos",110,"Potrerillos 110 kV -  H3 Línea 110 kV Potrerillos - Llanta 1/ Diego de Almagro 1",3.3290000000000002,1.8320000000000001,3.1509999999999998,1.728,2.879,1.585,3.3889999999999998,1.859,3.3889999999999998,1.5299999999999998,1.859]
[null,null,null,"Potrerillos 110 kV - H2 Línea 110 kV Potrerillos - Llanta 2/ Diego de Almagro 2",3.3290000000000002,1.4970000000000001,3.1509999999999998,1.4219999999999999,2.879,1.2949999999999999,3.3889999999999998,1.53,3.3889999999999998,1.8589999999999998,1.8589999999999998]
[null,null,null,"Potrerillos 110 kV - HT1 Transformador TR01 110/12/2.1 kV N°1",3.3290000000000002,0,3.1509999999999998,0,2.879,0,3.3889999999999998,0,3.3889999999999998,3.3889999999999998,3.3889999999999998]
[null,null,null,"Potrerillos 110 kV - HT2 Transformador TR02 110/12/2.1 kV N°2",3.3290000000000002,0,3.1509999999999998,0,2.879,0,3.3889999999999998,0,3.3889999999999998,3.3889999999999998,3.3889999999999998]
[null,"Pozo Almonte",110,"Pozo Almonte 110 kV - H1 Línea 110 kV Pozo Almonte - Tap Off Cerro Balcón",4.9710000000000001,0.30199999999999999,5.8559999999999999,0.28000000000000003,4.1520000000000001,0.255,5.8310000000000004,0.30299999999999999,5.8559999999999999,5.5759999999999996,5.5759999999999996]
[null,null,null,"Pozo Almonte 110 kV - H2 Línea 110 kV Pozo Almonte - Cerro Colorado ",4.9710000000000001,0,5.8559999999999999,1E-3,4.1520000000000001,0,5.8310000000000004,2E-3,5.8559999999999999,5.8549999999999995,5.8549999999999995]
[null,null,null,"Pozo Almonte 110 kV - H3 Línea 110 kV Pozo Almonte - Cerro Colorado ",4.9710000000000001,0,5.8559999999999999,1E-3,4.1520000000000001,0,5.8310000000000004,2E-3,5.8559999999999999,5.8549999999999995,5.8549999999999995]
[null,null,null,"Pozo Almonte 110 kV - HT2 Transformador ATR 2 100/100/25MVA 220/115/13.8 kV",4.9710000000000001,2.2010000000000001,5.8559999999999999,2.5840000000000001,4.1520000000000001,1.84,5.8310000000000004,2.5489999999999999,5.8559999999999999,3.2820000000000005,3.2820000000000005]
[null,null,null,"Pozo Almonte 110 kV - HT1 Transformador ATR1 90MVA 110/66/13.8  kV ",4.9710000000000001,0.372,5.8559999999999999,0.46,4.1520000000000001,0.27200000000000002,5.8310000000000004,0.501,5.8559999999999999,5.3959999999999999,5.3959999999999999]
[null,null,null,"Pozo Almonte 110 kV - HTX Transformador 30MVA 110/23kV",4.9710000000000001,0,5.8559999999999999,0,4.1520000000000001,0,5.8310000000000004,0,5.8559999999999999,5.8559999999999999,5.8559999999999999]
[null,null,null,"Pozo Almonte 110 kV - HT5 Transformador ATR 5 100/100/25MVA 220/115/13.8 kV N°5",4.9710000000000001,2.12,5.8559999999999999,2.552,4.1520000000000001,1.8069999999999999,5.8310000000000004,2.4889999999999999,5.8559999999999999,3.3420000000000005,3.3420000000000005]
[null,"Pudahuel",110,"Pudahuel 110 kV - HT1 Transformador TR01 22,4MVA 110/12.5 kV N°1",61.2,0,63.709000000000003,0,52.945999999999998,0,63.073999999999998,0,63.709000000000003,63.709000000000003,63.709000000000003]
[null,null,null,"Pudahuel 110 kV - HT2 Transformador TR02 22,4MVA 110/12.5 kV N°2",61.2,0,63.709000000000003,0,52.945999999999998,0,63.073999999999998,0,63.709000000000003,63.709000000000003,63.709000000000003]
[null,null,null,"Pudahuel 110 kV - HT3 Transformador TR03 20MVA 110/12.5 kV N°3",61.2,0,63.709000000000003,0,52.945999999999998,0,63.073999999999998,0,63.709000000000003,63.709000000000003,63.709000000000003]
[null,"Puente Alto (CMPC)",110,"Puente Alto (CMPC) 110 kV - A-1 Línea 110 kV Puente Alto - Pirque C1",3.1219999999999999,1.911,3.5979999999999999,1.7390000000000001,2.7679999999999998,1.665,3.4950000000000001,1.8560000000000001,3.5979999999999999,1.8589999999999998,1.911]
[null,null,null,"Puente Alto (CMPC) 110 kV - H-T3 Transformador TR3 45/60MVA 110/11.5 kV",3.1219999999999999,1.2190000000000001,3.5979999999999999,1.867,2.7679999999999998,1.1160000000000001,3.4950000000000001,1.6719999999999999,3.5979999999999999,1.9029999999999998,1.9029999999999998]
[null,"Puente Alto (EEPA)",110,"Puente Alto (EEPA) 110 kV - H2 Línea 100 kV Puente Alto - Costanera",9.5760000000000005,0,6.9690000000000003,0,8.3070000000000004,0,9.3149999999999995,0,9.5760000000000005,9.5760000000000005,9.5760000000000005]
[null,null,null,"Puente Alto (EEPA) 110 kV - H3 Línea 110 kV Puente Alto - Central Puntilla",9.5760000000000005,0.34699999999999998,6.9690000000000003,0.90900000000000003,8.3070000000000004,0.32500000000000001,9.3149999999999995,0.66800000000000004,9.5760000000000005,9.229000000000001,9.229000000000001]
[null,null,null,"Puente Alto (EEPA) 110 kV - H1 Línea 110 kV Puente Alto - Las Vizcachas",9.5760000000000005,9.2609999999999992,6.9690000000000003,6.0910000000000002,8.3070000000000004,8.0210000000000008,9.3149999999999995,8.69,9.5760000000000005,0.87800000000000011,9.2609999999999992]
[null,"Punitaqui",110,"Punitaqui 110 kV - HT2 Transformador T2 20MVA 110/13,2kV",3.5739999999999998,0,2.637,0,3.0590000000000002,0,3.4260000000000002,0,3.5739999999999998,3.5739999999999998,3.5739999999999998]
[null,"Punta de Cortés",154,"Punta de Cortés 154 kV - A2 Línea 154 kV Punta de Cortés - Tinguiririca 1/Tap Tilcoco C1",17.733000000000001,2.391,20.459,2.1080000000000001,15.481,2.0960000000000001,19.791,2.258,20.459,18.350999999999999,18.350999999999999]
[null,null,null,"Punta de Cortés 154 kV - A3 Línea 154 kV Punta de Cortés - Tinguiririca 2/Tap Tilcoco C2",17.733000000000001,2.391,20.459,2.1080000000000001,15.481,2.0960000000000001,19.791,2.258,20.459,18.350999999999999,18.350999999999999]
[null,null,null,"Punta de Cortés 154 kV - AX3 Línea 154 kV Tap Punta de Cortés - Alto Jahuel / Rancagua C1",17.733000000000001,3.1579999999999999,20.459,2.8250000000000002,15.481,2.7429999999999999,19.791,2.97,20.459,17.634,17.634]
[null,null,null,"Punta de Cortés 154 kV - AX4 Línea 154 kV Tap Punta de Cortés - Alto Jahuel /Rancagua C2",17.733000000000001,3.1480000000000001,20.459,2.8180000000000001,15.481,2.734,19.791,2.9609999999999999,20.459,17.640999999999998,17.640999999999998]
[null,null,null,"Punta de Cortés 154 kV - AT Acoplador",17.733000000000001,0.71,20.459,0.56000000000000005,15.481,0.61,19.791,1.65,20.459,19.899000000000001,19.899000000000001]
[null,null,null,"Punta de Cortés 154 kV - AT1 Transformador TR1 56MVA 154/69/13,8kV",17.733000000000001,0.15,20.459,0.33300000000000002,15.481,0.13100000000000001,19.791,0.35,20.459,20.126000000000001,20.126000000000001]
[null,null,null,"Punta de Cortés 154 kV - AT2 Transformador TR2 36/48/60MVA 154/69/13,8kV",17.733000000000001,0.27100000000000002,20.459,0.59499999999999997,15.481,0.23599999999999999,19.791,0.63,20.459,19.864000000000001,19.864000000000001]
[null,null,null,"Punta de Cortés 154 kV - A1 Transformador TR3 60/75MVA 154/69/14,8kV",17.733000000000001,0.28399999999999997,20.459,0.63,15.481,0.247,19.791,0.66900000000000004,20.459,19.829000000000001,19.829000000000001]
[null,null,null,"Punta de Cortés 154 kV - ATX Transformador 300MVA 220/154kV",17.733000000000001,5.9880000000000004,20.459,9.0619999999999994,15.481,5.2380000000000004,19.791,8.3149999999999995,20.459,11.745000000000001,11.745000000000001]
[null,"Punta Padrones",110,"Punta Padrones 110 kV - H1 Línea 110kV Caldera - Punta Padrones",2.0489999999999999,2.0489999999999999,1.242,1.242,1.7729999999999999,1.7729999999999999,1.8720000000000001,1.8720000000000001,2.0489999999999999,0,2.0489999999999999]
[null,"Punta Peuco (Cemento Polpaico)",110,"Punta Peuco (Cemento Polpaico) 110 kV - HT1 Transformador TR1 15/22MVA110/44kV",14.397,0,11.196999999999999,0,12.452,0,13.34,0,14.397,14.397,14.397]
[null,null,null,"Punta Peuco (Cemento Polpaico) 110 kV - HT2 Transformador TR2 20MVA110/44kV",14.397,0,11.196999999999999,0,12.452,0,13.34,0,14.397,14.397,14.397]
[null,"Quelentaro",110,"Quelentaro 110 kV - H1 Línea 110 kV Quelentaro - Las Arañas",7.008,0,11.781000000000001,0.123,6.0670000000000002,0,19.931999999999999,0.38400000000000001,19.931999999999999,19.547999999999998,19.547999999999998]
[null,null,null,"Quelentaro 110 kV - H2 Línea 110kV Litueche - Quelentaro",7.008,1.2989999999999999,11.781000000000001,1.2969999999999999,6.0670000000000002,1.1240000000000001,19.931999999999999,1.349,19.931999999999999,18.582999999999998,18.582999999999998]
[null,null,null,"Quelentaro 110 kV - HT1 Transformador AT1 195MVA 220/110kV",7.008,5.7309999999999999,11.781000000000001,10.624000000000001,6.0670000000000002,4.9619999999999997,19.931999999999999,19.446000000000002,19.931999999999999,1.2770000000000001,19.446000000000002]
[null,null,null,"Quelentaro 110 kV - HT5 Transformador TR5 13MVA 110/23 kV",7.008,0,11.781000000000001,0,6.0670000000000002,0,19.931999999999999,0,19.931999999999999,19.931999999999999,19.931999999999999]
[null,"Quellon",110,"Quellon 110 kV -  H1 Línea 110 kV Quellón - Chonchi",1.9530000000000001,1.554,1.1759999999999999,1.0149999999999999,1.6759999999999999,1.3380000000000001,1.768,1.456,1.9530000000000001,0.39900000000000002,1.554]
[null,null,null,"Quellon 110 kV - HT1 Transformador TR1 16MVA 115/13,8 kV N°1",1.9530000000000001,0.222,1.1759999999999999,0.09,1.6759999999999999,0.191,1.768,0.193,1.9530000000000001,1.7310000000000001,1.7310000000000001]
[null,null,null,"Quellon 110 kV - HT2 Transformador TR2 16MVA  115/24 kV N°2",1.9530000000000001,0.20599999999999999,1.1759999999999999,8.4000000000000005E-2,1.6759999999999999,0.17699999999999999,1.768,0.17899999999999999,1.9530000000000001,1.7470000000000001,1.7470000000000001]
[null,"Quereo",110,"Quereo 110 kV -  En Barra",8.4090000000000007,0,9.2309999999999999,0,7.1130000000000004,0,9.2579999999999991,0,9.2579999999999991,9.2579999999999991,9.2579999999999991]
[null,"Quilicura",110,"Quilicura 110 kV -  H1 Línea 110 kV Qulicura - San Cristobal /Cerro Navia C1",40.255000000000003,20.126999999999999,20.611000000000001,10.305999999999999,34.845999999999997,17.422999999999998,35.841000000000001,17.920000000000002,40.255000000000003,20.128000000000004,20.128000000000004]
[null,null,null,"Quilicura 110 kV -  H2 Línea 110 kV Qulicura - San Cristobal /Cerro Navia C2",40.255000000000003,20.126999999999999,20.611000000000001,10.305999999999999,34.845999999999997,17.422999999999998,35.841000000000001,17.920000000000002,40.255000000000003,20.128000000000004,20.128000000000004]
[null,null,null,"Quilicura 110 kV - HT1 Transformador TR01 50MVA 110/23kV",40.255000000000003,0,20.611000000000001,0,34.845999999999997,0,35.841000000000001,0,40.255000000000003,40.255000000000003,40.255000000000003]
[null,null,null,"Quilicura 110 kV - HT2 Transformador TR02 25MVA 110/12kV",40.255000000000003,0,20.611000000000001,0,34.845999999999997,0,35.841000000000001,0,40.255000000000003,40.255000000000003,40.255000000000003]
[null,null,null,"Quilicura 110 kV - HT3 Transformador TR03 50MVA 110/12kV",40.255000000000003,0,20.611000000000001,0,34.845999999999997,0,35.841000000000001,0,40.255000000000003,40.255000000000003,40.255000000000003]
[null,null,null,"Quilicura 110 kV - AT4 Transformador TR04 22,4MVA 110/12kV",40.255000000000003,0,20.611000000000001,0,34.845999999999997,0,35.841000000000001,0,40.255000000000003,40.255000000000003,40.255000000000003]
[null,"Quillota",110,"Quillota 110 kV - H3 Línea 110 kV Quillota - Marbella/ Illapel",13.013,0.877,15.846,0.77100000000000002,11.262,0.75600000000000001,15.574999999999999,0.84499999999999997,15.846,15.074999999999999,15.074999999999999]
[null,null,null,"Quillota 110 kV - HT3 Transformador TR03 48MVA 110/110 kV N°3",27.087,0.80500000000000005,38.692999999999998,12.363,23.43,0.69299999999999995,41.634999999999998,21.11,41.634999999999998,26.33,26.33]
[null,null,null,"Quillota 110 kV - H2 Línea 110 kV Quillota - San Pedro",27.087,15.282,38.692999999999998,14.872,23.43,13.223000000000001,41.634999999999998,14.986000000000001,41.634999999999998,26.648999999999997,26.648999999999997]
[null,null,null,"Quillota 110 kV - HT1/2 Transformador ATR1 75 MVA 220/115/13.8 kV ATR2 75 MVA 220/115/13.8 kV",27.087,2.1680000000000001,38.692999999999998,2.2839999999999998,23.43,1.8759999999999999,41.634999999999998,2.258,41.634999999999998,39.376999999999995,39.376999999999995]
[null,null,null,"Quillota 110 kV - HT4 Transformador ATR4 150MVA 220/115/13.8 kV N°4",27.087,4.415,38.692999999999998,4.6020000000000003,23.43,3.82,41.634999999999998,4.5490000000000004,41.634999999999998,37.085999999999999,37.085999999999999]
[null,null,null,"Quillota 110 kV - HT5 Tranformador ATR5 150MVA  ",27.087,4.5730000000000004,38.692999999999998,4.6529999999999996,23.43,3.956,41.634999999999998,4.63,41.634999999999998,37.004999999999995,37.004999999999995]
[null,"Quilpue",110,"Quilpue 110 kV - HT1 Transformador TR1 25MVA 110/12 kV ",14.205,0,7.8789999999999996,0,12.316000000000001,0,12.766,0,14.205,14.205,14.205]
[null,null,null,"Quilpue 110 kV - HT2 Transformador TR2 110/12 kV ",14.205,0,7.8789999999999996,0,12.316000000000001,0,12.766,0,14.205,14.205,14.205]
[null,null,null,"Quilpue 110 kV - HT3 Transformador TR3 25MVA 110/12 kV",14.205,0,7.8789999999999996,0,12.316000000000001,0,12.766,0,14.205,14.205,14.205]
[null,"Quinquimo",110,"Quinquimo 110 kV - HT1 Transformador 20MVA 110/23 kV",3.4129999999999998,0,2.2269999999999999,0,2.9470000000000001,0,3.2189999999999999,0,3.4129999999999998,3.4129999999999998,3.4129999999999998]
[null,null,null,"Quinquimo 110 kV -  H1 Línea 110 kV Quinquimo - Choapa",3.4129999999999998,1.744,2.2269999999999999,1.149,2.9470000000000001,1.5009999999999999,3.2189999999999999,1.641,3.4129999999999998,1.6689999999999998,1.744]
[null,null,null,"Quinquimo 110 kV -  H2 Línea 110 kV Quinquimo - Casas Viejas",3.4129999999999998,1.67,2.2269999999999999,1.0780000000000001,2.9470000000000001,1.4470000000000001,3.2189999999999999,1.579,3.4129999999999998,1.7429999999999999,1.7429999999999999]
[null,null,null,"Quinquimo 110 kV -  H3 Línea 110 kV Quinquimo - Cabildo",3.4129999999999998,0,2.2269999999999999,0,2.9470000000000001,0,3.2189999999999999,0,3.4129999999999998,3.4129999999999998,3.4129999999999998]
[null,"Quintero (Chilquinta)",110,"Quintero (Chilquinta) 110 kV - H1 Transformador TR1 22,5MVA 110/12 kV ",25.51,0,29.718,0,22.102,0,28.49,0,29.718,29.718,29.718]
[null,null,null,"Quintero (Chilquinta) 110 kV - H2 Transformador TR2 20MVA 110/12 kV ",25.51,0,29.718,0,22.102,0,28.49,0,29.718,29.718,29.718]
[null,"Rancagua",154,"Rancagua 154 kV - A1 Línea 154kV Rancagua - Tinguiririca 2/Alto Jahuel 2",14.292,5.0330000000000004,12.962,4.1219999999999999,12.441000000000001,4.3860000000000001,14.006,4.6959999999999997,14.292,9.31,9.31]
[null,null,null,"Rancagua 154 kV - A2 Línea 154kV Rancagua - Tinguiririca 1/Alto Jahuel 1",14.292,5.0250000000000004,12.962,4.117,12.441000000000001,4.3789999999999996,14.006,4.6890000000000001,14.292,9.3170000000000002,9.3170000000000002]
[null,null,null,"Rancagua 154 kV - A3 Línea 154kV Rancagua - Sauzal/Minera del Valle Central",14.292,3.1139999999999999,12.962,2.593,12.441000000000001,2.7,14.006,3.3220000000000001,14.292,11.178000000000001,11.178000000000001]
[null,null,null,"Rancagua 154 kV - AT2/3 Transformador TR02 25MVA 154/66kV",14.292,0,12.962,0.39800000000000002,12.441000000000001,0,14.006,0.36,14.292,14.292,14.292]
[null,null,null,"Rancagua 154 kV - AT4 Transformador TR04 45/60/75MVA 154/69/14,8kV",14.292,0.60599999999999998,12.962,0.93100000000000005,12.441000000000001,0.52900000000000003,14.006,0.74299999999999999,14.292,13.686,13.686]
[null,null,null,"Rancagua 154 kV - AT2 Transformador TR01 35/45/56MVA 154/69/13,8kV",14.292,0.51600000000000001,12.962,0.84499999999999997,12.441000000000001,0.45,14.006,0.66100000000000003,14.292,13.776,13.776]
[null,"Recoleta",110,"Recoleta 110 kV - H1 Línea 110 kV Recoleta - San Cristobal/Cerro Navia C1",32.076999999999998,16.039000000000001,15.404,7.702,27.774999999999999,13.888,28.35,14.175000000000001,32.076999999999998,16.037999999999997,16.039000000000001]
[null,null,null,"Recoleta 110 kV - H2 Línea 110 kV Recoleta - San Cristobal/Cerro Navia C2",32.076999999999998,16.039000000000001,15.404,7.702,27.774999999999999,13.888,28.35,14.175000000000001,32.076999999999998,16.037999999999997,16.039000000000001]
[null,null,null,"Recoleta 110 kV - HT3 Transformador TR03 110/12,5kV",32.076999999999998,0,15.404,0,27.774999999999999,0,28.35,0,32.076999999999998,32.076999999999998,32.076999999999998]
[null,null,null,"Recoleta 110 kV - HT1 Transformador TR01 25MVA 110/13.2 kV",32.076999999999998,0,15.404,0,27.774999999999999,0,28.35,0,32.076999999999998,32.076999999999998,32.076999999999998]
[null,"Renca",110,"Renca 110 kV - H4 Línea 110 kV Renca - Brasil C2",54.667000000000002,0,50.243000000000002,0,47.226999999999997,0,53.567,0,54.667000000000002,54.667000000000002,54.667000000000002]
[null,null,null,"Renca 110 kV - H3 Línea 110 kV Renca - Brasil C1",54.667000000000002,0,50.243000000000002,0,47.226999999999997,0,53.567,0,54.667000000000002,54.667000000000002,54.667000000000002]
[null,null,null,"Renca 110 kV - H1 Línea 110 kV Renca - Cerro Navia C1",54.667000000000002,14.975,50.243000000000002,10.765000000000001,47.226999999999997,12.989000000000001,53.567,13.363,54.667000000000002,40.204000000000001,40.204000000000001]
[null,null,null,"Renca 110 kV - H2 Línea 110 kV Renca - Cerro Navia C2",54.667000000000002,14.975,50.243000000000002,10.765000000000001,47.226999999999997,12.989000000000001,53.567,13.363,54.667000000000002,40.204000000000001,40.204000000000001]
[null,null,null,"Renca 110 kV - H5 Línea 110 kV Renca - Metro C1",54.667000000000002,14.013999999999999,50.243000000000002,10.327,47.226999999999997,12.17,53.567,12.859,54.667000000000002,40.707999999999998,40.707999999999998]
[null,null,null,"Renca 110 kV - H7 Enlace unidad a Gas central nueva renca - Renca",54.667000000000002,4.117,50.243000000000002,5.73,47.226999999999997,3.4510000000000001,53.567,5.12,54.667000000000002,50.550000000000004,50.550000000000004]
[null,null,null,"Renca 110 kV - H8 Enlace unidad a Vapor central nueva renca - Renca",54.667000000000002,3.8090000000000002,50.243000000000002,5.7869999999999999,47.226999999999997,3.1920000000000002,53.567,5.0750000000000002,54.667000000000002,50.858000000000004,50.858000000000004]
[null,"Reñaca",110,"Reñaca 110 kV - HX Línea 110kV Reñaca - Bosquemar",14.821,4.4950000000000001,10.243,2.9220000000000002,12.881,3.911,13.768000000000001,4.0839999999999996,14.821,10.326000000000001,10.326000000000001]
[null,null,null,"Reñaca 110 kV - HT1 Transformador TR1 22,4MVA 110/12 kV N°1",14.821,0,10.243,0,12.881,0,13.768000000000001,0,14.821,14.821,14.821]
[null,null,null,"Reñaca 110 kV - HT2 Transformador TR2 30MVA 110/12 kV N°2",14.821,0,10.243,0,12.881,0,13.768000000000001,0,14.821,14.821,14.821]
[null,"Río Bonito",110,"Río Bonito 110 kV - HT1 Transformador T1 40MVA 110/66/23 kV",2.0169999999999999,5.5E-2,2.0550000000000002,0.51400000000000001,1.8160000000000001,0.122,2.1539999999999999,0.39400000000000002,2.1539999999999999,1.962,1.962]
[null,"Río Toltén",110,"Río Toltén 110 kV - H1 Línea 110 kV Rio Toltén - Cunco/Melipeuco",3.1739999999999999,0.313,3.133,0.32600000000000001,2.7349999999999999,0.25900000000000001,3.1779999999999999,0.32700000000000001,3.1779999999999999,2.8609999999999998,2.8609999999999998]
[null,"S/E ACONCAGUA TG [En_Revision]",110,"S/E ACONCAGUA TG [En_Revision] 110 kV -  En Barra",18.643000000000001,0,16.326000000000001,0,16.297000000000001,0,17.904,0,18.643000000000001,18.643000000000001,18.643000000000001]
[null,"S/E CENTRAL CUEL",154,"S/E CENTRAL CUEL 154 kV - AL Línea 154 kV Negrete Cuel - Tap Santa Luisa",4.4969999999999999,4.4969999999999999,4.2149999999999999,3.7989999999999999,3.867,3.867,4.5739999999999998,4.3380000000000001,4.5739999999999998,0.41599999999999993,4.4969999999999999]
[null,"S/E CENTRAL SAUZALITO",154,"S/E CENTRAL SAUZALITO 154 kV - A1 Línea 154 kV Sauzal - Minera Valle Central / Rancagua",10.622999999999999,6.8570000000000002,9.2349999999999994,4.8099999999999996,9.2249999999999996,5.9669999999999996,10.388,6.726,10.622999999999999,4.4249999999999998,6.8570000000000002]
[null,"S/E INTERCONEXION CHACAYES",110,"S/E INTERCONEXION CHACAYES 110 kV - J1 Línea 110 kV Interconexión Chacayes - Arranque a: Sauzal 1 / Central Chacayes 1",17.238,5.0359999999999996,17.292999999999999,5.2270000000000003,14.99,4.3769999999999998,17.440999999999999,5.1619999999999999,17.440999999999999,12.279,12.279]
[null,null,null,"S/E INTERCONEXION CHACAYES 110 kV - J2 Línea 110 kV Interconexión Chacayes - Arranque a: Sauzal 2 / Central Chacayes 2",17.238,5.0359999999999996,17.292999999999999,5.2270000000000003,14.99,4.3769999999999998,17.440999999999999,5.1619999999999999,17.440999999999999,12.279,12.279]
[null,null,null,"S/E INTERCONEXION CHACAYES 110 kV - JT  Transformador Interconexión Chacayes 110/110 kV",17.238,10.071999999999999,17.292999999999999,10.454000000000001,14.99,8.7539999999999996,17.440999999999999,10.324,17.440999999999999,7.1660000000000004,10.454000000000001]
[null,null,null,"S/E INTERCONEXION CHACAYES 110 kV - HT Transformador Interconexión Chacayes 110/110 kV",17.238,7.1680000000000001,17.292999999999999,6.8380000000000001,14.99,6.2380000000000004,17.440999999999999,7.1239999999999997,17.440999999999999,10.454999999999998,10.454999999999998]
[null,null,null,"S/E INTERCONEXION CHACAYES 110 kV - H1 Línea 110 kV Interconexión Chacayes - Minero 1",17.238,3.5840000000000001,17.292999999999999,3.419,14.99,3.1190000000000002,17.440999999999999,3.5619999999999998,17.440999999999999,13.879,13.879]
[null,null,null,"S/E INTERCONEXION CHACAYES 110 kV - H2 Línea 110 kV Interconexión Chacayes - Minero 2",17.238,3.5840000000000001,17.292999999999999,3.419,14.99,3.1190000000000002,17.440999999999999,3.5619999999999998,17.440999999999999,13.879,13.879]
[null,"S/E MALLOA NUEVA",154,"S/E MALLOA NUEVA 154 kV - AT1 Transformador TR01 60/75MVA 220-154/66/15kV",14.827999999999999,0.38,15.115,0.25800000000000001,12.964,0.33100000000000002,15.138999999999999,0.33900000000000002,15.138999999999999,14.856999999999999,14.856999999999999]
[null,null,null,"S/E MALLOA NUEVA 154 kV - A1 Línea 154 kV Nueva Malloa - Tap Malloa 2",14.827999999999999,7.0469999999999997,15.115,7.3090000000000002,12.964,6.1630000000000003,15.138999999999999,7.2320000000000002,15.138999999999999,7.9069999999999991,7.9069999999999991]
[null,null,null,"S/E MALLOA NUEVA 154 kV - A2 Línea 154 kV Nueva Malloa - Tap Malloa 1",14.827999999999999,7.0469999999999997,15.115,7.3090000000000002,12.964,6.1630000000000003,15.138999999999999,7.2320000000000002,15.138999999999999,7.9069999999999991,7.9069999999999991]
[null,null,null,"S/E MALLOA NUEVA 154 kV - AT2 Transformador TR02 ",14.827999999999999,0.38,15.115,0.25800000000000001,12.964,0.33100000000000002,15.138999999999999,0.33900000000000002,15.138999999999999,14.856999999999999,14.856999999999999]
[null,"S/E POLPAICO (ENEL DISTRIBUCIÓN)",110,"S/E POLPAICO (ENEL DISTRIBUCIÓN) 110 kV -  En Barra",14.353999999999999,0,11.145,0,12.414,0,13.298999999999999,0,14.353999999999999,14.353999999999999,14.353999999999999]
[null,"Salamanca ",110,"Salamanca  110 kV - HT1 Transformador TR1 ",2.391,0,1.5640000000000001,0,2.056,0,2.246,0,2.391,2.391,2.391]
[null,null,null,"Salamanca  110 kV - HT2 Transformador TR2",2.391,0,1.5640000000000001,0,2.056,0,2.246,0,2.391,2.391,2.391]
[null,"Salar ",110,"Salar  110 kV - H25 Línea 100 kV Salar - KM6 ",9.7929999999999993,3.0640000000000001,10.728999999999999,3.1509999999999998,8.3670000000000009,2.62,10.48,3.1240000000000001,10.728999999999999,7.5779999999999994,7.5779999999999994]
[null,null,null,"Salar  110 kV - HT3 Transformador  ATR1 120/120/30 MVA 220/110/13,8 kV ",9.7929999999999993,2.8860000000000001,10.728999999999999,3.794,8.3670000000000009,2.46,10.48,3.5409999999999999,10.728999999999999,6.9390000000000001,6.9390000000000001]
[null,null,null,"Salar  110 kV - H26 Línea 100 kV Salar - KM6 ",9.7929999999999993,3.0640000000000001,10.728999999999999,3.1509999999999998,8.3670000000000009,2.62,10.48,3.1240000000000001,10.728999999999999,7.5779999999999994,7.5779999999999994]
[null,null,null,"Salar  110 kV - H4 Línea 100 kV Salar - Central Tamaya ",9.7929999999999993,0.79200000000000004,10.728999999999999,0.64700000000000002,8.3670000000000009,0.67700000000000005,10.48,0.72799999999999998,10.728999999999999,10.081999999999999,10.081999999999999]
[null,null,null,"Salar  110 kV - HPT1 Transformador TR1 40/32/40 MVA 100/13,8/13,8 kV ",9.7929999999999993,0,10.728999999999999,0,8.3670000000000009,0,10.48,0,10.728999999999999,10.728999999999999,10.728999999999999]
[null,null,null,"Salar  110 kV - HPT2 Transformador TR2 40/32/40 MVA 100/13,8/13,8 kV ",9.7929999999999993,0,10.728999999999999,0,8.3670000000000009,0,10.48,0,10.728999999999999,10.728999999999999,10.728999999999999]
[null,null,null,"Salar  110 kV - HAB Acoplador ",9.7929999999999993,0,10.728999999999999,0,8.3670000000000009,0,10.48,0,10.728999999999999,10.728999999999999,10.728999999999999]
[null,"San Antonio ",110,"San Antonio  110 kV -  H1 Línea 110 kV San Antonio - Alto Melipilla ",5.3090000000000002,2.226,4.5369999999999999,1.764,4.5979999999999999,1.927,5.0979999999999999,2.0539999999999998,5.3090000000000002,3.0830000000000002,3.0830000000000002]
[null,null,null,"San Antonio  110 kV - HT2 Transformador TR2 25 MVA 110/12 kV  ",5.3090000000000002,0,4.5369999999999999,0,4.5979999999999999,0,5.0979999999999999,0,5.3090000000000002,5.3090000000000002,5.3090000000000002]
[null,null,null,"San Antonio  110 kV - HT3 Transformador 60MVA ATR 110/66 kV",5.3090000000000002,0.86799999999999999,4.5369999999999999,1.01,4.5979999999999999,0.752,5.0979999999999999,1.0429999999999999,5.3090000000000002,4.4409999999999998,4.4409999999999998]
[null,null,null,"San Antonio  110 kV -  H2 Línea 110 kV San Antonio - Leyda ",5.3090000000000002,2.2250000000000001,4.5369999999999999,1.764,4.5979999999999999,1.927,5.0979999999999999,2.0550000000000002,5.3090000000000002,3.0840000000000001,3.0840000000000001]
[null,null,null,"San Antonio  110 kV - HT4 Transformador TR4 25 MVA 110/23 kV ",5.3090000000000002,0,4.5369999999999999,0,4.5979999999999999,0,5.0979999999999999,0,5.3090000000000002,5.3090000000000002,5.3090000000000002]
[null,null,null,"San Antonio  110 kV - HT1 Transformador TR1 30 MVA 110/12 kV  ",5.3090000000000002,0,4.5369999999999999,0,4.5979999999999999,0,5.0979999999999999,0,5.3090000000000002,5.3090000000000002,5.3090000000000002]
[null,null,null,"San Antonio  110 kV - HT5 Transformador TR5 50 MVA 110/23 kV",5.3090000000000002,0,4.5369999999999999,0,4.5979999999999999,0,5.0979999999999999,0,5.3090000000000002,5.3090000000000002,5.3090000000000002]
[null,"San Bernardo ",110,"San Bernardo  110 kV -  H1 Línea 110 kV San Bernardo - Buin/Lo Espejo 1 ",36.941000000000003,18.47,15.817,7.9089999999999998,32.018000000000001,16.009,32.497,16.248000000000001,36.941000000000003,18.471000000000004,18.471000000000004]
[null,null,null,"San Bernardo  110 kV -  H2 Línea 110 kV San Bernardo - Buin/Lo Espejo 2",36.941000000000003,18.47,15.817,7.9089999999999998,32.018000000000001,16.009,32.497,16.248000000000001,36.941000000000003,18.471000000000004,18.471000000000004]
[null,null,null,"San Bernardo  110 kV -  H3 Línea 110 kV San Bernardo - Malloco ",36.941000000000003,0,15.817,1E-3,32.018000000000001,0,32.497,1E-3,36.941000000000003,36.941000000000003,36.941000000000003]
[null,"San Cristóbal ",110,"San Cristóbal  110 kV -  H1 Línea 110 kV San Cristóbal - El Salto/Cerro Navia 1 ",27.562000000000001,13.781000000000001,13.058999999999999,6.5289999999999999,23.869,11.933999999999999,24.26,12.13,27.562000000000001,13.781000000000001,13.781000000000001]
[null,null,null,"San Cristóbal  110 kV -  H2 Línea 110 kV San Cristóbal - El Salto/Cerro Navia 2",27.562000000000001,13.781000000000001,13.058999999999999,6.5289999999999999,23.869,11.933999999999999,24.26,12.13,27.562000000000001,13.781000000000001,13.781000000000001]
[null,null,null,"San Cristóbal  110 kV - HT1 Transformador TR01 40 MVA 110/12 kV ",27.562000000000001,0,13.058999999999999,0,23.869,0,24.26,0,27.562000000000001,27.562000000000001,27.562000000000001]
[null,null,null,"San Cristóbal  110 kV - HT2 Transformador TR02 40 MVA 110/12 kV ",27.562000000000001,0,13.058999999999999,0,23.869,0,24.26,0,27.562000000000001,27.562000000000001,27.562000000000001]
[null,null,null,"San Cristóbal  110 kV - HT3 TR03-TR04",27.562000000000001,0,13.058999999999999,0,23.869,0,24.26,0,27.562000000000001,27.562000000000001,27.562000000000001]
[null,null,null,"San Cristóbal  110 kV - HT4 Transformador TR04 50 MVA 110/12,5 kV ",27.562000000000001,0,13.058999999999999,0,23.869,0,24.26,0,27.562000000000001,27.562000000000001,27.562000000000001]
[null,null,null,"San Cristóbal  110 kV - HT5 Transformador TR05 50 MVA 110/12 kV ",27.562000000000001,0,13.058999999999999,0,23.869,0,24.26,0,27.562000000000001,27.562000000000001,27.562000000000001]
[null,"San Felipe ",110,"San Felipe  110 kV - H1 Línea 110 kV San Felipe - Tap San Felipe C1",9.702,4.851,5.3529999999999998,2.677,8.4979999999999993,4.2489999999999997,8.8360000000000003,4.4180000000000001,9.702,4.851,4.851]
[null,null,null,"San Felipe  110 kV - H2 Línea 110 kV San Felipe - Tap San Felipe C2",9.702,4.851,5.3529999999999998,2.677,8.4979999999999993,4.2489999999999997,8.8360000000000003,4.4180000000000001,9.702,4.851,4.851]
[null,"San Fernando",154,"San Fernando 154 kV - AT1 Transformador 220-154/69/14.8 kV N°1",14.916,0.35799999999999998,16.324999999999999,0.57699999999999996,13.064,0.31,15.933,0.57899999999999996,16.324999999999999,15.747999999999999,15.747999999999999]
[null,null,null,"San Fernando 154 kV - AT2 Transformador 154/69/13.8 kV N°2",14.916,0.52,16.324999999999999,0.876,13.064,0.45100000000000001,15.933,0.878,16.324999999999999,15.449,15.449]
[null,null,null,"San Fernando 154 kV - AT3 Transformador 154/69/13.2 kV N°3",14.916,0.26500000000000001,16.324999999999999,0.182,13.064,0.23,15.933,0.20100000000000001,16.324999999999999,16.143000000000001,16.143000000000001]
[null,"San Joaquín (Enel Distribución) ",110,"San Joaquín (Enel Distribución)  110 kV - H1 Línea 110 kV San Joaquín (Chilectra) - Ochagavía/Florida 1 ",38.133000000000003,19.065999999999999,17.719000000000001,8.86,33.017000000000003,16.509,33.543999999999997,16.771999999999998,38.133000000000003,19.067000000000004,19.067000000000004]
[null,null,null,"San Joaquín (Enel Distribución)  110 kV - H2 Línea 110 kV San Joaquín (Chilectra) - Ochagavía/Florida 2",38.133000000000003,19.065999999999999,17.719000000000001,8.86,33.017000000000003,16.509,33.543999999999997,16.771999999999998,38.133000000000003,19.067000000000004,19.067000000000004]
[null,"San Joaquín (Transnet)",110,"San Joaquín (Transnet) 110 kV - HT2 Transformador TR2 30/24/18 MVA 110/13,8 kV ",7.992,0,6.4669999999999996,0,6.9050000000000002,0,7.61,0,7.992,7.992,7.992]
[null,null,null,"San Joaquín (Transnet) 110 kV - HT1 Transformador TR1 30/24/18 MVA 110/13,8 kV ",7.992,0,6.4669999999999996,0,6.9050000000000002,0,7.61,0,7.992,7.992,7.992]
[null,"San José ",110,"San José  110 kV - H1 Línea 110 kV San José - Cerro Navia/Chena 1",36.71,18.355,18.416,9.2080000000000002,31.783000000000001,15.891,32.651000000000003,16.326000000000001,36.71,18.355,18.355]
[null,null,null,"San José  110 kV - H2 Línea 110 kV San José - Cerro Navia/Chena 2",36.71,18.355,18.416,9.2080000000000002,31.783000000000001,15.891,32.651000000000003,16.326000000000001,36.71,18.355,18.355]
[null,null,null,"San José  110 kV - HT3 Transformador TR03 22,4 MVA 110/12,5 kV ",36.71,0,18.416,0,31.783000000000001,0,32.651000000000003,0,36.71,36.71,36.71]
[null,null,null,"San José  110 kV - H4 Transformador TR04 50 MVA 110/12,5 kV ",36.71,0,18.416,0,31.783000000000001,0,32.651000000000003,0,36.71,36.71,36.71]
[null,"San Pablo ",110,"San Pablo  110 kV -  H1 Línea 110 kV San Pablo - Cerro Navia/Lo Aguirre 1",33.896000000000001,17.143999999999998,26.407,13.44,29.346,14.842000000000001,31.974,16.202999999999999,33.896000000000001,16.752000000000002,17.143999999999998]
[null,null,null,"San Pablo  110 kV -  H2 Línea 110 kV San Pablo - Cerro Navia/Lo Aguirre 2",33.896000000000001,16.753,26.407,12.968,29.346,14.504,31.974,15.772,33.896000000000001,17.143000000000001,17.143000000000001]
[null,null,null,"San Pablo  110 kV - HT1 Transformador TR01 37,5MVA 110/23,5kV",33.896000000000001,0,26.407,0,29.346,0,31.974,0,33.896000000000001,33.896000000000001,33.896000000000001]
[null,null,null,"San Pablo  110 kV - HT2 Transformador TR02 37,5MVA 110/23,5kV",33.896000000000001,0,26.407,0,29.346,0,31.974,0,33.896000000000001,33.896000000000001,33.896000000000001]
[null,"San Pedro (AES GENER)",110,"San Pedro (AES GENER) 110 kV - H6 Línea 110 kV San Pedro - TO Mayaca C1",27.959,3.4940000000000002,32.444000000000003,3.089,24.181999999999999,3.01,31.303999999999998,3.306,32.444000000000003,29.355000000000004,29.355000000000004]
[null,null,null,"San Pedro (AES GENER) 110 kV - H7 Línea 110 kV San Pedro - TO Mayaca C2",27.959,3.4940000000000002,32.444000000000003,3.089,24.181999999999999,3.01,31.303999999999998,3.306,32.444000000000003,29.355000000000004,29.355000000000004]
[null,null,null,"San Pedro (AES GENER) 110 kV - HT Transformador TR1 110/12 kV / TR2 110/12 kV",27.959,0,32.444000000000003,0,24.181999999999999,0,31.303999999999998,0,32.444000000000003,32.444000000000003,32.444000000000003]
[null,null,null,"San Pedro (AES GENER) 110 kV - H3 Línea 110 kV San Pedro - Quillota",27.959,10.776,32.444000000000003,17.295000000000002,24.181999999999999,9.3179999999999996,31.303999999999998,16.756,32.444000000000003,17.183,17.295000000000002]
[null,null,null,"San Pedro (AES GENER) 110 kV - H1 Línea 110 kV San Pedro - Ventanas /Codelco Div. Ventanas 1 ",27.959,2.7370000000000001,32.444000000000003,2.472,24.181999999999999,2.371,31.303999999999998,2.6579999999999999,32.444000000000003,29.972000000000001,29.972000000000001]
[null,null,null,"San Pedro (AES GENER) 110 kV - H2 Línea 110 kV San Pedro - Ventanas /Codelco Div. Ventanas 2",27.959,2.7370000000000001,32.444000000000003,2.472,24.181999999999999,2.371,31.303999999999998,2.6579999999999999,32.444000000000003,29.972000000000001,29.972000000000001]
[null,null,null,"San Pedro (AES GENER) 110 kV - H4 Línea 110 kV San Pedro - Miraflores 1 ",27.959,3.0859999999999999,32.444000000000003,2.5950000000000002,24.181999999999999,2.6789999999999998,31.303999999999998,2.8109999999999999,32.444000000000003,29.849000000000004,29.849000000000004]
[null,null,null,"San Pedro (AES GENER) 110 kV - H5 Línea 110 kV San Pedro - Miraflores 2",27.959,1.8260000000000001,32.444000000000003,1.5629999999999999,24.181999999999999,1.585,31.303999999999998,1.6919999999999999,32.444000000000003,30.881000000000004,30.881000000000004]
[null,null,null,"San Pedro (AES GENER) 110 kV - HR Acoplador ",27.959,0,32.444000000000003,0,24.181999999999999,0,31.303999999999998,0,32.444000000000003,32.444000000000003,32.444000000000003]
[null,"San Rafael (Chilquinta)",110,"San Rafael (Chilquinta) 110 kV - HT1 Transformador TR1 25MVA 110/12kV",9.2240000000000002,0,6.01,0,8.1630000000000003,0,8.6059999999999999,0,9.2240000000000002,9.2240000000000002,9.2240000000000002]
[null,null,null,"San Rafael (Chilquinta) 110 kV - HT2 Transformador TR2 22,5MVA 110/12kV",9.2240000000000002,0,6.01,0,8.1630000000000003,0,8.6059999999999999,0,9.2240000000000002,9.2240000000000002,9.2240000000000002]
[null,null,null,"San Rafael (Chilquinta) 110 kV - HT3 Transformador TR3 30MVA 110/23kV",9.2240000000000002,0,6.01,0,8.1630000000000003,0,8.6059999999999999,0,9.2240000000000002,9.2240000000000002,9.2240000000000002]
[null,"San Vicente",154,"San Vicente 154 kV - A1 Línea 154kV San Vicente - Hualpén 2",15.452999999999999,3.9319999999999999,18.248999999999999,4.6349999999999998,13.250999999999999,3.3679999999999999,17.552,4.5350000000000001,18.248999999999999,13.613999999999999,13.613999999999999]
[null,null,null,"San Vicente 154 kV - A2 Línea 154kV San Vicente - EKA Chile /Hualpén 1",15.452999999999999,3.9319999999999999,18.248999999999999,4.6420000000000003,13.250999999999999,3.3679999999999999,17.552,4.5410000000000004,18.248999999999999,13.606999999999999,13.606999999999999]
[null,null,null,"San Vicente 154 kV - A3 Línea 154kV San Vicente - Concepción 1",15.452999999999999,3.3260000000000001,18.248999999999999,3.7370000000000001,13.250999999999999,2.8580000000000001,17.552,3.6190000000000002,18.248999999999999,14.511999999999999,14.511999999999999]
[null,null,null,"San Vicente 154 kV - A10 Línea 154kV San Vicente - Concepción 2",15.452999999999999,3.3260000000000001,18.248999999999999,3.7370000000000001,13.250999999999999,2.8580000000000001,17.552,3.6190000000000002,18.248999999999999,14.511999999999999,14.511999999999999]
[null,null,null,"San Vicente 154 kV - A9 Línea 154kV San Vicente - Huachipato 2",15.452999999999999,0,18.248999999999999,0,13.250999999999999,0,17.552,0,18.248999999999999,18.248999999999999,18.248999999999999]
[null,null,null,"San Vicente 154 kV - ACE1 Condensador CCEE1",15.452999999999999,0,18.248999999999999,0,13.250999999999999,0,17.552,0,18.248999999999999,18.248999999999999,18.248999999999999]
[null,null,null,"San Vicente 154 kV - A6 Línea 154kV San Vicente - Huachipato 1",15.452999999999999,0,18.248999999999999,0,13.250999999999999,0,17.552,0,18.248999999999999,18.248999999999999,18.248999999999999]
[null,null,null,"San Vicente 154 kV - AT4 Transformador TR4",15.452999999999999,0,18.248999999999999,0,13.250999999999999,0,17.552,0,18.248999999999999,18.248999999999999,18.248999999999999]
[null,null,null,"San Vicente 154 kV - AT3 Transformador TR3 40/20/30MVA 154/69/13,8kV",15.452999999999999,0.223,18.248999999999999,0.16800000000000001,13.250999999999999,0.18099999999999999,17.552,0.19800000000000001,18.248999999999999,18.081,18.081]
[null,null,null,"San Vicente 154 kV - AT2 Transformador TR2 26MVA 154/13,8kV",15.452999999999999,0,18.248999999999999,0,13.250999999999999,0,17.552,0,18.248999999999999,18.248999999999999,18.248999999999999]
[null,null,null,"San Vicente 154 kV - A5 Línea 154kV San Vicente - Talcahuano",15.452999999999999,0.74299999999999999,18.248999999999999,1.3520000000000001,13.250999999999999,0.63800000000000001,17.552,1.21,18.248999999999999,16.896999999999998,16.896999999999998]
[null,"Santa Elena",110,"Santa Elena 110 kV - HT2 Transformador TR02 50MVA 110/12,5kV",31.51,0,12.958,0,27.285,0,27.611999999999998,0,31.51,31.51,31.51]
[null,null,null,"Santa Elena 110 kV - H3 Transformador TR03 50MVA 110/13,2kV",31.51,0,12.958,0,27.285,0,27.611999999999998,0,31.51,31.51,31.51]
[null,null,null,"Santa Elena 110 kV - H4 Transformador TR04 50MVA 110/12,5kV",31.51,0,12.958,0,27.285,0,27.611999999999998,0,31.51,31.51,31.51]
[null,null,null,"Santa Elena 110 kV - AT5 Transformador TR05 22,4MVA 110/12,5kV",31.51,0,12.958,0,27.285,0,27.611999999999998,0,31.51,31.51,31.51]
[null,null,null,"Santa Elena 110 kV - H1 Línea 110kV Santa Elena - Ochagavía/Florida1",31.51,15.755000000000001,12.958,6.48,27.285,13.643000000000001,27.611999999999998,13.804,31.51,15.755000000000001,15.755000000000001]
[null,null,null,"Santa Elena 110 kV - H2 Línea 110kV Santa Elena - Ochagavía/Florida2",31.51,15.755000000000001,12.958,6.4779999999999998,27.285,13.643000000000001,27.611999999999998,13.808,31.51,15.755000000000001,15.755000000000001]
[null,"Santa Fe",154,"Santa Fe 154 kV -  En Barra",4.8079999999999998,0,4.5090000000000003,0,4.133,0,4.883,0,4.883,4.883,4.883]
[null,"Santa Marta",110,"Santa Marta 110 kV - HT2 Transformador TR02 50MVA 110/12,5kV",34.115000000000002,0,16.779,0,29.547999999999998,0,30.244,0,34.115000000000002,34.115000000000002,34.115000000000002]
[null,null,null,"Santa Marta 110 kV - HT4 Transformador TR04 37,5MVA 110/23,5kV",34.115000000000002,0,16.779,0,29.547999999999998,0,30.244,0,34.115000000000002,34.115000000000002,34.115000000000002]
[null,null,null,"Santa Marta 110 kV - H1 Línea 110kV Santa Marta - Cerro Navia/Chena1",34.115000000000002,17.056999999999999,16.779,8.39,29.547999999999998,14.773999999999999,30.244,15.122,34.115000000000002,17.058000000000003,17.058000000000003]
[null,null,null,"Santa Marta 110 kV - H2 Línea 110kV Santa Marta - Cerro Navia/Chena2",34.115000000000002,17.056999999999999,16.779,8.39,29.547999999999998,14.773999999999999,30.244,15.122,34.115000000000002,17.058000000000003,17.058000000000003]
[null,null,null,"Santa Marta 110 kV - HX Línea 110kV Santa Marta  - Padre Hurtado",34.115000000000002,0,16.779,0,29.547999999999998,0,30.244,0,34.115000000000002,34.115000000000002,34.115000000000002]
[null,"Santa Raquel",110,"Santa Raquel 110 kV - HT1 Transformador TR01 50MVA 110/12,5kV",24.462,0,11.4,0,21.198,0,21.747,0,24.462,24.462,24.462]
[null,null,null,"Santa Raquel 110 kV - HT2 Transformador TR02 25MVA 110/12,5kV",24.462,0,11.4,0,21.198,0,21.747,0,24.462,24.462,24.462]
[null,null,null,"Santa Raquel 110 kV - H4 Transformador TR04 22,4MVA 110/12,5kV",24.462,0,11.4,0,21.198,0,21.747,0,24.462,24.462,24.462]
[null,null,null,"Santa Raquel 110 kV - H1 Línea 110kV Santa Raquel - Buin/Florida1",24.462,12.231,11.4,5.7,21.198,10.599,21.747,10.872999999999999,24.462,12.231,12.231]
[null,null,null,"Santa Raquel 110 kV - H2 Línea 110kV Santa Raquel - Buin/Florida2",24.462,12.231,11.4,5.7,21.198,10.599,21.747,10.872999999999999,24.462,12.231,12.231]
[null,null,null,"Santa Raquel 110 kV - H5 Transformador TR05 50MVA 110/20,4kV",24.462,0,11.4,0,21.198,0,21.747,0,24.462,24.462,24.462]
[null,null,null,"Santa Raquel 110 kV - HT6 Transformador N°6 12/16/20/22,4MVA 110/12,5kV",24.462,0,11.4,0,21.198,0,21.747,0,24.462,24.462,24.462]
[null,"Santa Rosa Sur",110,"Santa Rosa Sur 110 kV - H1 Línea 110kV Santa Rosa Sur - Buin/Florida1",32.063000000000002,16.030999999999999,16.754000000000001,8.3770000000000007,27.783999999999999,13.891999999999999,28.457999999999998,14.228999999999999,32.063000000000002,16.032000000000004,16.032000000000004]
[null,null,null,"Santa Rosa Sur 110 kV - H2 Línea 110kV Santa Rosa Sur - Buin/Florida2",32.063000000000002,16.030999999999999,16.754000000000001,8.3770000000000007,27.783999999999999,13.891999999999999,28.457999999999998,14.228999999999999,32.063000000000002,16.032000000000004,16.032000000000004]
[null,null,null,"Santa Rosa Sur 110 kV - HT3 Transformador TR03 25MVA 110/12,5kV",32.063000000000002,0,16.754000000000001,0,27.783999999999999,0,28.457999999999998,0,32.063000000000002,32.063000000000002,32.063000000000002]
[null,null,null,"Santa Rosa Sur 110 kV - H4 Transformador TR04 22,4MVA 110/12,5kV",32.063000000000002,0,16.754000000000001,0,27.783999999999999,0,28.457999999999998,0,32.063000000000002,32.063000000000002,32.063000000000002]
[null,"Sauzal (C.Sauzal)",110,"Sauzal (C.Sauzal) 110 kV - HT4 Transformador TR4 50 MVA 154/110/13.8 kV y TR7 70 MVA 154/110/13.8 kV",19.122,4.1390000000000002,20.541,5.3630000000000004,16.498000000000001,3.6080000000000001,20.096,4.8019999999999996,20.541,15.294,15.294]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - H4 Línea 110kV Sauzal - Minero 2/Interconexión Chacayes 2",19.122,2.8679999999999999,20.541,2.8359999999999999,16.498000000000001,2.5310000000000001,20.096,2.8,20.541,17.705000000000002,17.705000000000002]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - H3 Línea 110kV Sauzal - Minero 1/Interconexión Chacayes 1",19.122,2.8679999999999999,20.541,2.8359999999999999,16.498000000000001,2.5310000000000001,20.096,2.8,20.541,17.705000000000002,17.705000000000002]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - H1 Línea 110kV Codegua - Sauzal C1",19.122,2.2269999999999999,20.541,1.855,16.498000000000001,1.9359999999999999,20.096,2.093,20.541,18.686,18.686]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - H2 Línea 110kV Codegua - Sauzal C2",19.122,2.2269999999999999,20.541,1.855,16.498000000000001,1.9359999999999999,20.096,2.093,20.541,18.686,18.686]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - H5 Línea 110kV Sauzal - Minero 3 ",19.122,2.5,20.541,2.3889999999999998,16.498000000000001,2.1880000000000002,20.096,2.4060000000000001,20.541,18.152000000000001,18.152000000000001]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - HT6 Transformador TR6 30 MVA 110/66/6 kV",19.122,0.25700000000000001,20.541,0.43099999999999999,16.498000000000001,0.20300000000000001,20.096,0.40200000000000002,20.541,20.11,20.11]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - HT1 Transformador T1 29 MVA 110/13.2 kV",19.122,0.59299999999999997,20.541,0.93300000000000005,16.498000000000001,0.46700000000000003,20.096,0.874,20.541,19.608000000000001,19.608000000000001]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - HT2 Transformador T2 29 MVA 110/13.2 kV",19.122,0.59299999999999997,20.541,0.93300000000000005,16.498000000000001,0.46700000000000003,20.096,0.874,20.541,19.608000000000001,19.608000000000001]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - HT3 Transformador T3 29 MVA 110/13.2 kV",19.122,0.65600000000000003,20.541,1.0369999999999999,16.498000000000001,0.51700000000000002,20.096,0.97299999999999998,20.541,19.504000000000001,19.504000000000001]
[null,null,null,"Sauzal (C.Sauzal) 110 kV - T5 Transformador T5 10 MVA 110/13.8 kV",19.122,0.25700000000000001,20.541,0.13400000000000001,16.498000000000001,0.16300000000000001,20.096,0.19700000000000001,20.541,20.407,20.407]
[null,"Seat El Sol (El Sol)",110,"Seat El Sol (El Sol) 110 kV - 3 Transformador TR1 ",14.205,0,7.8789999999999996,0,12.316000000000001,0,12.766,0,14.205,14.205,14.205]
[null,null,null,"Seat El Sol (El Sol) 110 kV - 5 Transformador TR2",14.205,0,7.8789999999999996,0,12.316000000000001,0,12.766,0,14.205,14.205,14.205]
[null,null,null,"Seat El Sol (El Sol) 110 kV - 1 Línea",14.205,0,7.8789999999999996,0,12.316000000000001,0,12.766,0,14.205,14.205,14.205]
[null,null,null,"Seat El Sol (El Sol) 110 kV - 2 Línea",14.205,0,7.8789999999999996,0,12.316000000000001,0,12.766,0,14.205,14.205,14.205]
[null,"Sewell",110,"Sewell 110 kV - H1 Línea 100kV Sewell - Minero C1",12.554,6.2770000000000001,10.605,5.3029999999999999,10.906000000000001,5.4530000000000003,11.882999999999999,5.9420000000000002,12.554,6.2770000000000001,6.2770000000000001]
[null,null,null,"Sewell 110 kV - H2 Línea 100kV Sewell - Minero C2",12.554,6.2770000000000001,10.605,5.3029999999999999,10.906000000000001,5.4530000000000003,11.882999999999999,5.9420000000000002,12.554,6.2770000000000001,6.2770000000000001]
[null,null,null,"Sewell 110 kV - HR Acoplador",12.554,0,10.605,0,10.906000000000001,0,11.882999999999999,0,12.554,12.554,12.554]
[null,null,null,"Sewell 110 kV - HT1 Transformador TR1 110/34,5kV",12.554,0,10.605,0,10.906000000000001,0,11.882999999999999,0,12.554,12.554,12.554]
[null,null,null,"Sewell 110 kV - HT2 Transformador TR2 110/34,5kV",12.554,0,10.605,0,10.906000000000001,0,11.882999999999999,0,12.554,12.554,12.554]
[null,null,null,"Sewell 110 kV - HT3 Transformador TR3 110/34,5kV",12.554,0,10.605,0,10.906000000000001,0,11.882999999999999,0,12.554,12.554,12.554]
[null,"Sierra Miranda",110,"Sierra Miranda 110 kV -  En Barra",7.5220000000000002,0,7.5179999999999998,0,6.4509999999999996,0,7.6340000000000003,0,7.6340000000000003,7.6340000000000003,7.6340000000000003]
[null,"Sopladores",110,"Sopladores 110 kV - HT1 Transformador TR01 25/33MVA 100/13,8kV",8.4719999999999995,0,7.8550000000000004,0,7.2519999999999998,0,8.2119999999999997,0,8.4719999999999995,8.4719999999999995,8.4719999999999995]
[null,null,null,"Sopladores 110 kV - HT2 Transformador TR02 25/33MVA 100/13,8kV",8.4719999999999995,0,7.8550000000000004,0,7.2519999999999998,0,8.2119999999999997,0,8.4719999999999995,8.4719999999999995,8.4719999999999995]
[null,null,null,"Sopladores 110 kV - HACOP Acoplador",8.4719999999999995,0,7.8550000000000004,0,7.2519999999999998,0,8.2119999999999997,0,8.4719999999999995,8.4719999999999995,8.4719999999999995]
[null,null,null,"Sopladores 110 kV - H24 Línea 100kV Sopladores - KM6",8.4719999999999995,8.4719999999999995,7.8550000000000004,7.8550000000000004,7.2519999999999998,7.2519999999999998,8.2119999999999997,8.2119999999999997,8.4719999999999995,0,8.4719999999999995]
[null,"Sur",110,"Sur 110 kV - HT1 Transformador TR1 110/13,8kV",6.5090000000000003,0,5.6260000000000003,0,5.5730000000000004,0,6.1550000000000002,0,6.5090000000000003,6.5090000000000003,6.5090000000000003]
[null,"Tal Tal (ELECDA)",110,"Tal Tal (ELECDA) 110 kV -  En Barra",0.99,0,0.68200000000000005,0,0.85799999999999998,0,0.94799999999999995,0,0.99,0.99,0.99]
[null,"Talcahuano ",154,"Talcahuano  154 kV - AT3 Transformador TR03 18,7MVA 154/15kV",14.488,7.5999999999999998E-2,17.218,0.06,12.430999999999999,6.5000000000000002E-2,16.600000000000001,6.8000000000000005E-2,17.218,17.158000000000001,17.158000000000001]
[null,null,null,"Talcahuano  154 kV - AT1 Transformador TR01 75MVA 154/69/14,8kV",14.488,0.42299999999999999,17.218,0.68100000000000005,12.430999999999999,0.36399999999999999,16.600000000000001,0.69,17.218,16.536999999999999,16.536999999999999]
[null,null,null,"Talcahuano  154 kV - ATX Transformador TR04 56MVA 154/69/14,8kV",14.488,0.33,17.218,0.67300000000000004,12.430999999999999,0.28399999999999997,16.600000000000001,0.70299999999999996,17.218,16.545000000000002,16.545000000000002]
[null,null,null,"Talcahuano  154 kV - A Línea 154kV Talcahuano - San Vicente",14.488,13.659000000000001,17.218,15.811,12.430999999999999,11.718999999999999,16.600000000000001,15.19,17.218,1.4100000000000019,15.811]
[null,"Tap Off Achupallas",110,"Tap Off Achupallas 110 kV -  En Barra",24.164000000000001,0,17.337,0,20.992999999999999,0,22.059000000000001,0,24.164000000000001,24.164000000000001,24.164000000000001]
[null,"Tap Off Alto Melipilla",110,"Tap Off Alto Melipilla 110 kV - H1 Línea 110kV Tap Alto Melipilla - Melipilla",10.455,0.23,11.416,0.18,9.0530000000000008,0.19800000000000001,11.032,0.223,11.416,11.236000000000001,11.236000000000001]
[null,null,null,"Tap Off Alto Melipilla 110 kV - H2 Línea 110kV Tap Alto Melipilla - Bollenar",10.455,0,11.416,0,9.0530000000000008,0,11.032,1E-3,11.416,11.416,11.416]
[null,"Tap Off Antucoya",110,"Tap Off Antucoya 110 kV - HT Línea 110kV Tap Antucoya - Antucoya",1.7509999999999999,0.59,0.88500000000000001,0.19800000000000001,1.5149999999999999,0.51,1.593,0.51700000000000002,1.7509999999999999,1.161,1.161]
[null,"Tap Off Barriles ",110,"Tap Off Barriles  110 kV - HT1 Transformador TR1 220/110/13,2kV",1.37,1.37,0.57499999999999996,0.57499999999999996,1.1859999999999999,1.1859999999999999,1.1990000000000001,1.1990000000000001,1.37,0,1.37]
[null,"Tap Off Cerro Balcón ",110,"Tap Off Cerro Balcón  110 kV -  En Barra",1.7929999999999999,0,1.337,0,1.532,0,1.7070000000000001,0,1.7929999999999999,1.7929999999999999,1.7929999999999999]
[null,"Tap Off Chañares",110,"Tap Off Chañares 110 kV - H1 Línea 110kV Tap Chañares - Central Chañares",7.7610000000000001,0,8.282,0.54500000000000004,6.6959999999999997,0,8.1470000000000002,0.58899999999999997,8.282,7.7610000000000001,7.7610000000000001]
[null,"Tap Off Chiza",110,"Tap Off Chiza 110 kV -  En Barra",1.7929999999999999,0,1.337,0,1.532,0,1.7070000000000001,0,1.7929999999999999,1.7929999999999999,1.7929999999999999]
[null,"Tap Off Codelco Ventanas",110,"Tap Off Codelco Ventanas 110 kV - E Línea 110 kV Ventanas 1 - Tap Codelco Ventanas",23.838000000000001,0,26.074999999999999,1.071,20.651,0,25.495999999999999,1.181,26.074999999999999,25.003999999999998,25.003999999999998]
[null,"Tap Off Coyanco",154,"Tap Off Coyanco 154 kV -  En Barra",4.8079999999999998,0,4.5090000000000003,0,4.133,0,4.883,0,4.883,4.883,4.883]
[null,"Tap Off Cuya",110,"Tap Off Cuya 110 kV -  En Barra",1.518,0,1.794,0,1.294,0,1.8420000000000001,0,1.8420000000000001,1.8420000000000001,1.8420000000000001]
[null,"Tap Off Desalant",110,"Tap Off Desalant 110 kV -  En Barra",8.1639999999999997,0,6.3739999999999997,0,6.9720000000000004,0,7.5039999999999996,0,8.1639999999999997,8.1639999999999997,8.1639999999999997]
[null,"Dolores",110,"Dolores 110 kV - HTX Transformador 15MVA TR1 110/24kV",1.7929999999999999,0,1.337,8.0000000000000002E-3,1.532,0,1.7070000000000001,6.0000000000000001E-3,1.7929999999999999,1.7929999999999999,1.7929999999999999]
[null,null,null,"Dolores 110 kV - HX1 Línea 110 kV Dolores - Tap Chiza",1.7929999999999999,0.53600000000000003,1.337,0.46600000000000003,1.532,0.45600000000000002,1.7070000000000001,0.52700000000000002,1.7929999999999999,1.2569999999999999,1.2569999999999999]
[null,null,null,"Dolores 110 kV - HX2 Línea 110 kV Dolores - Tap Cerro Balcón",1.7929999999999999,1.2589999999999999,1.337,0.86599999999999999,1.532,1.0780000000000001,1.7070000000000001,1.1779999999999999,1.7929999999999999,0.53400000000000003,1.2589999999999999]
[null,"Tap Off Eden",110,"Tap Off Eden 110 kV - H1 Línea 110 kV Tap Off Eden - Central Río Huasco/Alto del Carmen",4.2309999999999999,0.125,3.7839999999999998,0.247,3.645,0.11600000000000001,4.415,0.19600000000000001,4.415,4.2190000000000003,4.2190000000000003]
[null,"Tap Off El Negro ",110,"Tap Off El Negro  110 kV - HT1 Transformador TR1 110/23kV",6.7060000000000004,0,5.0640000000000001,0,5.7590000000000003,0,6.1790000000000003,0,6.7060000000000004,6.7060000000000004,6.7060000000000004]
[null,"Tap Off El Romeral",110,"Tap Off El Romeral 110 kV -  En Barra",3.9969999999999999,0,2.8839999999999999,0,3.4569999999999999,0,3.7930000000000001,0,3.9969999999999999,3.9969999999999999,3.9969999999999999]
[null,"Tap Off Impulsión",110,"Tap Off Impulsión 110 kV - H Línea 110kV TO Impulsión - Impulsión ",4.3710000000000004,0,3.3090000000000002,0,3.778,0,4.0670000000000002,0,4.3710000000000004,4.3710000000000004,4.3710000000000004]
[null,"Tap Off La Laja",110,"Tap Off La Laja 110 kV - H2 Línea 110 kV Tap La Laja - Central Queltehues 1",21.856000000000002,0.47899999999999998,17.952000000000002,0.46899999999999997,18.748999999999999,0.378,20.594999999999999,0.45100000000000001,21.856000000000002,21.377000000000002,21.377000000000002]
[null,null,null,"Tap Off La Laja 110 kV - H3 Línea 110 kV Tap La Laja - Central Queltehues 2",21.856000000000002,0.47,17.952000000000002,0.45300000000000001,18.748999999999999,0.37,20.594999999999999,0.44,21.856000000000002,21.386000000000003,21.386000000000003]
[null,null,null,"Tap Off La Laja 110 kV - HX2 Línea 110 kV Alto Maipo - Tap La Laja C2",21.856000000000002,2.6850000000000001,17.952000000000002,2.5419999999999998,18.748999999999999,2.3250000000000002,20.594999999999999,2.4350000000000001,21.856000000000002,19.171000000000003,19.171000000000003]
[null,null,null,"Tap Off La Laja 110 kV - HX1 Línea 110 kV Alto Maipo - Tap La Laja C1",21.856000000000002,2.7160000000000002,17.952000000000002,2.573,18.748999999999999,2.3519999999999999,20.594999999999999,2.4609999999999999,21.856000000000002,19.14,19.14]
[null,"La Laja (Energía coyanco)",110,"La Laja (Energía coyanco) 110 kV - BTP Transformador 110/23 kV 15 MVA ",21.856999999999999,0.23599999999999999,17.96,0.77500000000000002,18.748999999999999,0.13700000000000001,20.597999999999999,0.68500000000000005,21.856999999999999,21.620999999999999,21.620999999999999]
[null,"Tap Off Licancabur (Licancabur)",110,"Tap Off Licancabur (Licancabur) 110 kV - HT1 Transformador TR01 37,5MVA 110/3,45kV",2.0880000000000001,0,1.2490000000000001,0,1.8069999999999999,0,1.929,0,2.0880000000000001,2.0880000000000001,2.0880000000000001]
[null,null,null,"Tap Off Licancabur (Licancabur) 110 kV - HT2 Transformador TR02 37,5MVA 110/3,45kV",2.0880000000000001,0,1.2490000000000001,0,1.8069999999999999,0,1.929,0,2.0880000000000001,2.0880000000000001,2.0880000000000001]
[null,"Tap Off Mal Paso",110,"Tap Off Mal Paso 110 kV -  En Barra",1.69,0,2.5049999999999999,0,1.446,0,2.9910000000000001,0,2.9910000000000001,2.9910000000000001,2.9910000000000001]
[null,"Tap Off Malloa",154,"Tap Off Malloa 154 kV -  En Barra",14.827999999999999,0,15.115,0,12.964,0,15.138999999999999,0,15.138999999999999,15.138999999999999,15.138999999999999]
[null,"Tap Off Mayaca",110,"Tap Off Mayaca 110 kV - HX1 Línea 110kV TO Mayaca - TO Pachacama C1",22.216999999999999,4.6779999999999999,21.568000000000001,3.7389999999999999,19.184000000000001,4.0179999999999998,22.35,4.3280000000000003,22.35,18.022000000000002,18.022000000000002]
[null,null,null,"Tap Off Mayaca 110 kV - HX2 Línea 110kV TO Mayaca - TO Pachacama C2",22.216999999999999,4.6790000000000003,21.568000000000001,3.7389999999999999,19.184000000000001,4.0179999999999998,22.35,4.3280000000000003,22.35,18.022000000000002,18.022000000000002]
[null,null,null,"Tap Off Mayaca 110 kV - HX3 Línea 110kV TO Mayaca - San Pedro C1",22.216999999999999,6.43,21.568000000000001,7.0449999999999999,19.184000000000001,5.5739999999999998,22.35,6.931,22.35,15.786999999999999,15.786999999999999]
[null,null,null,"Tap Off Mayaca 110 kV - HX4 Línea 110kV TO Mayaca - San Pedro C2",22.216999999999999,6.43,21.568000000000001,7.0449999999999999,19.184000000000001,5.5739999999999998,22.35,6.931,22.35,15.786999999999999,15.786999999999999]
[null,null,null,"Tap Off Mayaca 110 kV - HX5 Línea 110kV TO Mayaca - Mayaca C1",22.216999999999999,0,21.568000000000001,1E-3,19.184000000000001,0,22.35,1E-3,22.35,22.349,22.349]
[null,null,null,"Tap Off Mayaca 110 kV - HX6 Línea 110kV TO Mayaca - Mayaca C2",22.216999999999999,0,21.568000000000001,0,19.184000000000001,0,22.35,0,22.35,22.35,22.35]
[null,"Tap Off Oeste ",110,"Tap Off Oeste  110 kV - H1 Línea 110 kV Tap Off Oeste (Oeste) - Minsal ",1.903,0,1.996,1E-3,1.6459999999999999,0,1.9790000000000001,1E-3,1.996,1.9950000000000001,1.9950000000000001]
[null,"Petroquímicas",154,"Petroquímicas 154 kV -  En Barra",14.864000000000001,0,17.044,0,12.749000000000001,0,16.440000000000001,0,17.044,17.044,17.044]
[null,"Tap Off Punta Peuco",110,"Tap Off Punta Peuco 110 kV - HT3 Línea 110kV Tap Punta Peuco - Polpaico (Enel distribución)",14.448,0,11.25,0,12.496,0,13.385,0,14.448,14.448,14.448]
[null,null,null,"Tap Off Punta Peuco 110 kV - HL Línea 110kV Tap Punta Peuco - Central Loma los Colorados",14.448,0.44800000000000001,11.25,0.7,12.496,0.40400000000000003,13.385,0.56200000000000006,14.448,14,14]
[null,null,null,"Tap Off Punta Peuco 110 kV - HT Línea 110kV Tap Punta Peuco - Punta Peuco (Cementos Polpaico)",14.448,0,11.25,0,12.496,0,13.385,0,14.448,14.448,14.448]
[null,"Tap Off Punta Toro",110,"Tap Off Punta Toro 110 kV - L-1 Línea 110 kV Tap Punta Toro - Los Colorados ",4.7779999999999996,0,3.2669999999999999,0,4.1130000000000004,0,4.4669999999999996,0,4.7779999999999996,4.7779999999999996,4.7779999999999996]
[null,"Tap Off Quiñenco",154,"Tap Off Quiñenco 154 kV -  En Barra",12.282999999999999,0,14.759,0,10.544,0,14.278,0,14.759,14.759,14.759]
[null,"Central Río Melado",154,"Central Río Melado 154 kV - AT Línea 154 kV Tap Río Melado - Itahue2/Cipreses2",5.0179999999999998,0,3.57,0,4.2359999999999998,0,4.54,0,5.0179999999999998,5.0179999999999998,5.0179999999999998]
[null,"Tap Off Sairecabur (Sairecabur)",110,"Tap Off Sairecabur (Sairecabur) 110 kV - HT1 Transformador TR01 37,5MVA 110/3,45kV",2.1789999999999998,0,1.351,0,1.8859999999999999,0,2.0219999999999998,0,2.1789999999999998,2.1789999999999998,2.1789999999999998]
[null,null,null,"Tap Off Sairecabur (Sairecabur) 110 kV - HT2 Transformador TR02 37,5MVA 110/3,45kV",2.1789999999999998,0,1.351,0,1.8859999999999999,0,2.0219999999999998,0,2.1789999999999998,2.1789999999999998,2.1789999999999998]
[null,"Tap Off Santa Luisa",154,"Tap Off Santa Luisa 154 kV -  En Barra",4.8079999999999998,0,4.5090000000000003,0,4.133,0,4.883,0,4.883,4.883,4.883]
[null,"Tap Off Tilcoco",154,"Tap Off Tilcoco 154 kV -  En Barra",14.779,0,11.701000000000001,0,12.906000000000001,0,13.755000000000001,0,14.779,14.779,14.779]
[null,"Tuniche",154,"Tuniche 154 kV -  En Barra",14.667999999999999,0,13.057,0,12.775,0,14.13,0,14.667999999999999,14.667999999999999,14.667999999999999]
[null,"Tap Off Uribe",110,"Tap Off Uribe 110 kV - H1 Acoplador  (Une los arranques (Uribe - Esmeralda con Antofagasta - Capricornio) ",9.2010000000000005,5.8360000000000003,8.8699999999999992,4.9710000000000001,7.806,5.0309999999999997,9.1449999999999996,5.4450000000000003,9.2010000000000005,3.8989999999999991,5.8360000000000003]
[null,"Tap Off Vítor",110,"Tap Off Vítor 110 kV -  En Barra",1.518,0,1.794,0,1.294,0,1.8420000000000001,0,1.8420000000000001,1.8420000000000001,1.8420000000000001]
[null,"Tap Off Vítor N°2 Móvil (Movil Vítor)",110,"Tap Off Vítor N°2 Móvil (Movil Vítor) 110 kV - HTT Transformador  20/25/30MVA 110/23kV",1.518,3.1E-2,1.794,0.41099999999999998,1.294,1.4999999999999999E-2,1.8420000000000001,0.51400000000000001,1.8420000000000001,1.4870000000000001,1.4870000000000001]
[null,"Teno",154,"Teno 154 kV - AT1 Transformador TR1 154/13,2kV - 33,3 MVA",12.132999999999999,0.17399999999999999,7.1120000000000001,5.8999999999999997E-2,10.481999999999999,0.127,10.834,0.13200000000000001,12.132999999999999,11.959,11.959]
[null,null,null,"Teno 154 kV - AT2 Transformador TR2 154/13,2kV - 33,3 MVA",12.132999999999999,0.17399999999999999,7.1120000000000001,5.8999999999999997E-2,10.481999999999999,0.127,10.834,0.13200000000000001,12.132999999999999,11.959,11.959]
[null,null,null,"Teno 154 kV - AT Interruptor transformadores N°3 y N°5",12.132999999999999,0,7.1120000000000001,1E-3,10.481999999999999,0,10.834,0,12.132999999999999,12.132999999999999,12.132999999999999]
[null,null,null,"Teno 154 kV - A9 Línea 154kV Teno - Paneles MDP Teno",12.132999999999999,0,7.1120000000000001,1E-3,10.481999999999999,0,10.834,0,12.132999999999999,12.132999999999999,12.132999999999999]
[null,"Teno Empalme",154,"Teno Empalme 154 kV - A Línea 154 kV Teno Empalme - Teno",13.657999999999999,1.738,8.3819999999999997,0.68700000000000006,11.813000000000001,1.456,12.199,1.4710000000000001,13.657999999999999,11.92,11.92]
[null,"Tierra Amarilla",110,"Tierra Amarilla 110 kV - HT1 Transformador T1 10-12MVA 110/23kV",7.9139999999999997,0,7.36,0,6.8280000000000003,0,7.7069999999999999,0,7.9139999999999997,7.9139999999999997,7.9139999999999997]
[null,null,null,"Tierra Amarilla 110 kV - HT2 Transformador T2 25-30MVA 110/23kV",7.9139999999999997,0,7.36,0,6.8280000000000003,0,7.7069999999999999,0,7.9139999999999997,7.9139999999999997,7.9139999999999997]
[null,null,null,"Tierra Amarilla 110 kV - H3  Línea 110kV Tierra Amarilla - Atacama Kozán",7.9139999999999997,1.6919999999999999,7.36,1.587,6.8280000000000003,1.46,7.7069999999999999,1.6559999999999999,7.9139999999999997,6.2219999999999995,6.2219999999999995]
[null,null,null,"Tierra Amarilla 110 kV - H4 Línea 110kV Tierra Amarilla - Plantas",7.9139999999999997,3.1539999999999999,7.36,3.0489999999999999,6.8280000000000003,2.72,7.7069999999999999,3.0779999999999998,7.9139999999999997,4.76,4.76]
[null,"Tinguiririca",154,"Tinguiririca 154 kV - A3 Línea 154kV Tinguiririca - Convento Viejo/Itahue 2",16.654,2.2879999999999998,20.234000000000002,1.9830000000000001,14.609,1.9650000000000001,19.602,2.145,20.234000000000002,18.251000000000001,18.251000000000001]
[null,null,null,"Tinguiririca 154 kV - A4 Línea 154kV Tinguiririca - Itahue 1",16.654,2.2410000000000001,20.234000000000002,1.9079999999999999,14.609,1.925,19.602,2.085,20.234000000000002,18.326000000000001,18.326000000000001]
[null,null,null,"Tinguiririca 154 kV - A8 Línea 154kV Tinguiririca - San Fernando C1",16.654,0.496,20.234000000000002,0.63700000000000001,14.609,0.42799999999999999,19.602,0.68,20.234000000000002,19.597000000000001,19.597000000000001]
[null,null,null,"Tinguiririca 154 kV - AX Línea 154kV Tinguiririca - San Fernando C2",16.654,0.49099999999999999,20.234000000000002,0.64,14.609,0.42399999999999999,19.602,0.66800000000000004,20.234000000000002,19.594000000000001,19.594000000000001]
[null,null,null,"Tinguiririca 154 kV - A9 Línea 154kV Tinguiririca - Rancagua 1/Alto Jahuel 1",16.654,2.5419999999999998,20.234000000000002,2.2629999999999999,14.609,2.214,19.602,2.41,20.234000000000002,17.971000000000004,17.971000000000004]
[null,null,null,"Tinguiririca 154 kV - A10 Línea 154kV Tinguiririca - Rancagua 2/Alto Jahuel 2",16.654,2.5419999999999998,20.234000000000002,2.2639999999999998,14.609,2.214,19.602,2.41,20.234000000000002,17.970000000000002,17.970000000000002]
[null,null,null,"Tinguiririca 154 kV - AT1 Transformador AT1 300MVA 220/154/69kV",16.654,6.1180000000000003,20.234000000000002,10.577,14.609,5.4859999999999998,19.602,9.8650000000000002,20.234000000000002,10.536,10.577]
[null,"Torquemada",110,"Torquemada 110 kV - H1 Línea 110kV Loncura - Torquemada C1",22.344999999999999,4.0549999999999997,20.247,3.2690000000000001,19.48,3.508,21.724,3.6960000000000002,22.344999999999999,18.29,18.29]
[null,null,null,"Torquemada 110 kV - H2 Línea 110kV Loncura - Torquemada C2",22.344999999999999,4.0549999999999997,20.247,3.2690000000000001,19.48,3.508,21.724,3.6960000000000002,22.344999999999999,18.29,18.29]
[null,null,null,"Torquemada 110 kV - H11 Línea 110kV Torquemada - Miraflores 1",22.344999999999999,3.746,20.247,2.7429999999999999,19.48,3.2410000000000001,21.724,3.3690000000000002,22.344999999999999,18.599,18.599]
[null,null,null,"Torquemada 110 kV - H12 Línea 110kV Torquemada - Miraflores 2",22.344999999999999,3.746,20.247,2.7429999999999999,19.48,3.2410000000000001,21.724,3.3690000000000002,22.344999999999999,18.599,18.599]
[null,null,null,"Torquemada 110 kV - HR Acoplador",22.344999999999999,0,20.247,0,19.48,0,21.724,0,22.344999999999999,22.344999999999999,22.344999999999999]
[null,null,null,"Torquemada 110 kV - H3 Línea 110kV Torquemada - Con Con 1",22.344999999999999,1.881,20.247,1.397,19.48,1.6259999999999999,21.724,1.76,22.344999999999999,20.463999999999999,20.463999999999999]
[null,null,null,"Torquemada 110 kV - H4 Línea 110kV Torquemada - Con Con 2",22.344999999999999,1.881,20.247,1.397,19.48,1.6259999999999999,21.724,1.76,22.344999999999999,20.463999999999999,20.463999999999999]
[null,null,null,"Torquemada 110 kV - H5 Línea 110kV Torquemada - Central Colmito",22.344999999999999,1.448,20.247,2.7789999999999999,19.48,1.2110000000000001,21.724,2.3199999999999998,22.344999999999999,20.896999999999998,20.896999999999998]
[null,null,null,"Torquemada 110 kV - H7 Línea 110kV Torquemada - Mauco 1",22.344999999999999,0.86799999999999999,20.247,1.383,19.48,0.85099999999999998,21.724,1.1359999999999999,22.344999999999999,21.477,21.477]
[null,null,null,"Torquemada 110 kV - H8 Línea 110kV Torquemada - Mauco 2",22.344999999999999,0.86799999999999999,20.247,1.383,19.48,0.85099999999999998,21.724,1.1359999999999999,22.344999999999999,21.477,21.477]
[null,"Totoralillo",110,"Totoralillo 110 kV - HT Transformador TR 33MVA 115/66kV",8.5310000000000006,0.182,5.7670000000000003,0.23699999999999999,7.7130000000000001,0.50700000000000001,7.9770000000000003,0.44500000000000001,8.5310000000000006,8.3490000000000002,8.3490000000000002]
[null,null,null,"Totoralillo 110 kV - H2 Línea 110kV Totoralillo - Aconcagua/Los Maquis 2",8.5310000000000006,4.6589999999999998,5.7670000000000003,3.331,7.7130000000000001,4.077,7.9770000000000003,4.3079999999999998,8.5310000000000006,3.8720000000000008,4.6589999999999998]
[null,null,null,"Totoralillo 110 kV - H2A Línea 110kV Totoralillo - Nueva San Rafael",8.5310000000000006,3.6989999999999998,5.7670000000000003,2.2069999999999999,7.7130000000000001,3.2269999999999999,7.9770000000000003,3.3650000000000002,8.5310000000000006,4.8320000000000007,4.8320000000000007]
[null,"Travesía",110,"Travesía 110 kV - H3 Línea 110kV Travesía - Punta Padrones/ EB2",5.0149999999999997,0.54800000000000004,3.54,0.40500000000000003,4.3330000000000002,0.47299999999999998,4.59,0.51400000000000001,5.0149999999999997,4.4669999999999996,4.4669999999999996]
[null,null,null,"Travesía 110 kV - H2 Transformador TR1 110/23kV",5.0149999999999997,0,3.54,0,4.3330000000000002,0,4.59,0,5.0149999999999997,5.0149999999999997,5.0149999999999997]
[null,"Uribe",110,"Uribe 110 kV - H2 Línea 110kV Uribe - Esmeralda/Tap Uribe",6.899,6.6369999999999996,6.8949999999999996,5.5750000000000002,5.8330000000000002,5.7290000000000001,7.0220000000000002,6.1710000000000003,7.0220000000000002,1.3199999999999994,6.6369999999999996]
[null,null,null,"Uribe 110 kV - H3 Línea 110kV Uribe - Uribe Solar",6.899,0.26400000000000001,6.8949999999999996,1.321,5.8330000000000002,0.129,7.0220000000000002,1.4159999999999999,7.0220000000000002,6.6349999999999998,6.6349999999999998]
[null,null,null,"Uribe 110 kV - HT1 Transformador TR1 110/23kV",6.899,0,6.8949999999999996,0,5.8330000000000002,0,7.0220000000000002,0,7.0220000000000002,7.0220000000000002,7.0220000000000002]
[null,"Uribe Solar",110,"Uribe Solar 110 kV - H1 Línea 110kV Uribe Solar - Uribe",5.2080000000000002,4.9480000000000004,6.2839999999999998,4.4619999999999997,4.38,4.2869999999999999,6.5350000000000001,4.7450000000000001,6.5350000000000001,1.8220000000000001,4.9480000000000004]
[null,"Valle de los vientos",110,"Valle de los vientos 110 kV - HT1 Transformador TR01 50/65MVA 110/23kV",4.9560000000000004,0.21099999999999999,5.5439999999999996,0.63800000000000001,4.0759999999999996,0.1,5.492,0.81,5.5439999999999996,4.9059999999999997,4.9059999999999997]
[null,null,null,"Valle de los vientos 110 kV - HT2 Transformador TR02 50/65MVA 110/23kV",4.9560000000000004,0.21099999999999999,5.5439999999999996,0.63800000000000001,4.0759999999999996,0.1,5.492,0.81,5.5439999999999996,4.9059999999999997,4.9059999999999997]
[null,null,null,"Valle de los vientos 110 kV - HL1 Línea 110kV Valle de los vientos - Calama",4.9560000000000004,4.5330000000000004,5.5439999999999996,4.2709999999999999,4.0759999999999996,3.9020000000000001,5.492,4.2949999999999999,5.5439999999999996,1.2729999999999997,4.5330000000000004]
[null,"Vallenar",110,"Vallenar 110 kV - HT1 Transformador TR01 y TR02",4.2309999999999999,0,3.7839999999999998,0,3.645,0,4.415,0,4.415,4.415,4.415]
[null,"Valparaíso",110,"Valparaíso 110 kV - HT1 Transformador TR1 25MVA 110/12kV",16.837,0,15.073,0,14.597,0,16.509,0,16.837,16.837,16.837]
[null,null,null,"Valparaíso 110 kV - HT2 Transformador TR2 25MVA 110/12kV",16.837,0,15.073,0,14.597,0,16.509,0,16.837,16.837,16.837]
[null,null,null,"Valparaíso 110 kV - HT3 Transformador TR3 25MVA 110/12kV",16.837,0,15.073,0,14.597,0,16.509,0,16.837,16.837,16.837]
[null,null,110,"Ventanas 110 kV - HS1 Acoplador",25.887,0,31.651,0,22.428999999999998,0,30.466999999999999,0,31.651,31.651,31.651]
[null,null,null,"Ventanas 110 kV - HS2 Acoplador",25.887,0,31.651,0,22.428999999999998,0,30.466999999999999,0,31.651,31.651,31.651]
[null,null,null,"Ventanas 110 kV - HR Acoplador",25.887,0,31.651,0,22.428999999999998,0,30.466999999999999,0,31.651,31.651,31.651]
[null,"Ventanas",null,"Ventanas 110 kV - H1 Línea 110kV Ventanas - San Pedro/Codelco Div. Ventanas C2",25.887,2.91,31.651,2.9470000000000001,22.428999999999998,2.5179999999999998,30.466999999999999,2.9169999999999998,31.651,28.704000000000001,28.704000000000001]
[null,null,null,"Ventanas 110 kV - H2 Línea 110kV Ventanas - San Pedro/Codelco Div. Ventanas C1",25.887,2.91,31.651,2.9470000000000001,22.428999999999998,2.5179999999999998,30.466999999999999,2.9169999999999998,31.651,28.704000000000001,28.704000000000001]
[null,null,null,"Ventanas 110 kV - H3 Línea 110kV Loncura - Ventanas C1",25.887,3.323,31.651,3.0379999999999998,22.428999999999998,2.8969999999999998,30.466999999999999,3.1579999999999999,31.651,28.613,28.613]
[null,null,null,"Ventanas 110 kV - H4 Línea 110kV Loncura - Ventanas C2",25.887,3.323,31.651,3.0379999999999998,22.428999999999998,2.8969999999999998,30.466999999999999,3.1579999999999999,31.651,28.613,28.613]
[null,null,null,"Ventanas 110 kV - H5 Línea 110kV Ventanas - Quintero (Chilquinta)",25.887,0,31.651,0,22.428999999999998,0,30.466999999999999,0,31.651,31.651,31.651]
[null,null,null,"Ventanas 110 kV - HX Línea 110kV Ventanas - El Bato",25.887,0,31.651,0,22.428999999999998,0,30.466999999999999,0,31.651,31.651,31.651]
[null,null,null,"Ventanas 110 kV - H6 Línea 110kV Ventanas - GNL Quintero",25.887,4.9139999999999997,31.651,3.31,22.428999999999998,4.2359999999999998,30.466999999999999,3.9079999999999999,31.651,28.341000000000001,28.341000000000001]
[null,null,null,"Ventanas 110 kV - HT1 Transformador 3 devanado",25.887,8.5630000000000006,31.651,10.467000000000001,22.428999999999998,7.4080000000000004,30.466999999999999,10.012,31.651,21.183999999999997,21.183999999999997]
[null,null,null,"Ventanas 110 kV - HTP Transformador TRP 20MVA 110/4,16kV",25.887,0,31.651,0.19500000000000001,22.428999999999998,0,30.466999999999999,0.25,31.651,31.456,31.456]
[null,null,null,"Ventanas 110 kV - HT4 Transformador T4 20MVA 110/4,16kV",25.887,0,31.651,0.19500000000000001,22.428999999999998,0,30.466999999999999,0.25,31.651,31.456,31.456]
[null,null,null,"Ventanas 110 kV - HT Aguas abajo paño HTP y HT4",25.887,0,31.651,0.38900000000000001,22.428999999999998,0,30.466999999999999,0.5,31.651,31.262,31.262]
[null,null,null,"Ventanas 110 kV - HT1A Transformador TR1A 22,5MVA 110/13kV",25.887,0,31.651,0.81899999999999995,22.428999999999998,0,30.466999999999999,1.052,31.651,30.832000000000001,30.832000000000001]
[null,null,null,"Ventanas 110 kV - HT1B Transformador TR1B 22,5MVA 110/13kV",25.887,0,31.651,0.81899999999999995,22.428999999999998,0,30.466999999999999,1.052,31.651,30.832000000000001,30.832000000000001]
[null,null,null,"Ventanas 110 kV - HT2A Transformador TR2A 22,5MVA 110/18kV",25.887,0,31.651,1.9710000000000001,22.428999999999998,0,30.466999999999999,2.5329999999999999,31.651,29.68,29.68]
[null,null,null,"Ventanas 110 kV - HT2B Transformador TR2B 22,5MVA 110/18kV",25.887,0,31.651,1.9710000000000001,22.428999999999998,0,30.466999999999999,2.5329999999999999,31.651,29.68,29.68]
[null,"Vicuña",110,"Vicuña 110 kV - HT Transformador TR1 10/13MVA",2.097,0,1.3120000000000001,0,1.8149999999999999,0,1.9770000000000001,0,2.097,2.097,2.097]
[null,null,null,"Vicuña 110 kV - H2 Línea 110kV Vicuña - El Indio",2.097,0,1.3120000000000001,7.0000000000000001E-3,1.8149999999999999,0,1.9770000000000001,5.0000000000000001E-3,2.097,2.097,2.097]
[null,"Vitacura",110,"Vitacura 110 kV - HT1 Transformador TR1 50MVA 110/12,5kV",28.138999999999999,0,16.481000000000002,0,24.370999999999999,0,25.181000000000001,0,28.138999999999999,28.138999999999999,28.138999999999999]
[null,null,null,"Vitacura 110 kV - HT2 Transformador TR2 50MVA 110/12,5kV",28.138999999999999,0,16.481000000000002,0,24.370999999999999,0,25.181000000000001,0,28.138999999999999,28.138999999999999,28.138999999999999]
[null,null,null,"Vitacura 110 kV - HT3 Transformador TR3 50MVA 110/12,5kV",28.138999999999999,0,16.481000000000002,0,24.370999999999999,0,25.181000000000001,0,28.138999999999999,28.138999999999999,28.138999999999999]
[null,null,null,"Vitacura 110 kV - H4 Transformador TR4 50MVA 110/12,5kV",28.138999999999999,0,16.481000000000002,0,24.370999999999999,0,25.181000000000001,0,28.138999999999999,28.138999999999999,28.138999999999999]
[null,null,null,"Vitacura 110 kV - HS1 Acoplador",28.138999999999999,0,16.481000000000002,0,24.370999999999999,0,25.181000000000001,0,28.138999999999999,28.138999999999999,28.138999999999999]
[null,null,null,"Vitacura 110 kV - H1 Línea 110kV Vitacura - Los Almendros/El Salto1",28.138999999999999,14.07,16.481000000000002,8.24,24.370999999999999,12.186,25.181000000000001,12.590999999999999,28.138999999999999,14.068999999999999,14.07]
[null,null,null,"Vitacura 110 kV - H2 Línea 110kV Vitacura - Los Almendros/El Salto2",28.138999999999999,14.069000000000001,16.481000000000002,8.24,24.370999999999999,12.186,25.181000000000001,12.590999999999999,28.138999999999999,14.069999999999999,14.069999999999999]
[null,"Yerbas Buenas",154,"Yerbas Buenas 154 kV - A1 Transformador T1 20MVA 154/13,2kV",6.89,0,5.9359999999999999,0,5.9560000000000004,0,6.6289999999999996,0,6.89,6.89,6.89]
[null,"Yungay",110,"Yungay 110 kV -  En Barra",5.2759999999999998,0,6.2389999999999999,0,4.5460000000000003,0,6.0339999999999998,0,6.2389999999999999,6.2389999999999999,6.2389999999999999]
[null,"CD Combarbalá",110,"CD Combarbalá 110 kV - HTX Transformador Combarbalá 110/13,8 kV",4.4420000000000002,2.0539999999999998,4.7679999999999998,2.7389999999999999,3.7490000000000001,1.681,5.008,2.5920000000000001,5.008,2.4159999999999999,2.7389999999999999]
[null,"Alto Maipo",110,"Alto Maipo 110 kV - HTX1 Transformador U1 160 MVA 220/12 kV",19.815000000000001,2.8039999999999998,18.71,3.3879999999999999,17.03,2.4449999999999998,19.675000000000001,3.1280000000000001,19.815000000000001,17.011000000000003,17.011000000000003]
[null,null,null,"Alto Maipo 110 kV - HTX2 Transformador U2 160 MVA 220/12 kV",19.815000000000001,2.8039999999999998,18.71,3.3879999999999999,17.03,2.4449999999999998,19.675000000000001,3.1280000000000001,19.815000000000001,17.011000000000003,17.011000000000003]
[null,null,null,"Alto Maipo 110 kV - HX1 Línea 110 kV Alto Maipo - Maitenes",19.815000000000001,6.6349999999999998,18.71,5.8470000000000004,17.03,5.67,19.675000000000001,6.4080000000000004,19.815000000000001,13.266999999999999,13.266999999999999]
[null,null,null,"Alto Maipo 110 kV - HX2 Línea 110 kV Alto Maipo - Tap La Laja C2",19.815000000000001,3.8220000000000001,18.71,3.081,17.03,3.2690000000000001,19.675000000000001,3.5219999999999998,19.815000000000001,16.153000000000002,16.153000000000002]
[null,null,null,"Alto Maipo 110 kV - HX3 Línea 110 kV Alto Maipo - Tap La Laja C1",19.815000000000001,3.8220000000000001,18.71,3.081,17.03,3.2690000000000001,19.675000000000001,3.5219999999999998,19.815000000000001,16.153000000000002,16.153000000000002]
[null,"Pueblo Seco",154,"Pueblo Seco 154 kV - HX1 Línea 154 kV Charrua - Pueblo Seco",7.8929999999999998,5.7910000000000004,5.8230000000000004,4.0279999999999996,6.7789999999999999,4.9649999999999999,7.2290000000000001,5.2759999999999998,7.8929999999999998,2.1019999999999994,5.7910000000000004]
[null,null,null,"Pueblo Seco 154 kV - HX2 Línea 154 kV Pueblo Seco - Monterrico",7.8929999999999998,2.113,5.8230000000000004,1.7989999999999999,6.7789999999999999,1.823,7.2290000000000001,1.9530000000000001,7.8929999999999998,5.7799999999999994,5.7799999999999994]
[null,null,null,"Pueblo Seco 154 kV - HTX Transformador 20MVA 154/23kV",7.8929999999999998,0,5.8230000000000004,0,6.7789999999999999,0,7.2290000000000001,0,7.8929999999999998,7.8929999999999998,7.8929999999999998]
[null,"La Ruca",110,"La Ruca 110 kV - HX1 Línea El Peñón - La Ruca 110 kV C1",5.5190000000000001,1.944,4.3040000000000003,1.3859999999999999,4.7370000000000001,1.6739999999999999,5.37,1.833,5.5190000000000001,3.5750000000000002,3.5750000000000002]
[null,null,null,"La Ruca 110 kV - HX2 Línea El Peñón - La Ruca 110 kV C2",5.5190000000000001,1.9570000000000001,4.3040000000000003,1.385,4.7370000000000001,1.6850000000000001,5.37,1.8360000000000001,5.5190000000000001,3.5620000000000003,3.5620000000000003]
[null,null,null,"La Ruca 110 kV - HX3 Línea La Ruca - Ovalle 110 kV C1",5.5190000000000001,0.80800000000000005,4.3040000000000003,0.77100000000000002,4.7370000000000001,0.68799999999999994,5.37,0.85899999999999999,5.5190000000000001,4.7110000000000003,4.7110000000000003]
[null,null,null,"La Ruca 110 kV - HX4 Línea La Ruca - Ovalle 110 kV C2",5.5190000000000001,0.81299999999999994,4.3040000000000003,0.76600000000000001,4.7370000000000001,0.69299999999999995,5.37,0.85399999999999998,5.5190000000000001,4.7060000000000004,4.7060000000000004]
[null,"Nueva Panquehue",110,"Nueva Panquehue 110 kV - HX1 Línea 110kV Fundición Chagres - Nueva Panquehue",16.23,5.75,9.7970000000000006,3.4239999999999999,14.108000000000001,4.9560000000000004,14.676,5.1669999999999998,16.23,10.48,10.48]
[null,null,null,"Nueva Panquehue 110 kV - HX2 Línea 110kV Tap Chagres - Nueva Panquehue",16.23,7.4379999999999997,9.7970000000000006,4.4429999999999996,14.108000000000001,6.4109999999999996,14.676,6.69,16.23,8.7920000000000016,8.7920000000000016]
[null,null,null,"Nueva Panquehue 110 kV - HX3 Línea 110kV Nueva Panquehue - Tap San Felipe C1",16.23,1.5209999999999999,9.7970000000000006,0.96499999999999997,14.108000000000001,1.371,14.676,1.41,16.23,14.709,14.709]
[null,null,null,"Nueva Panquehue 110 kV - HX4 Línea 110kV Nueva Panquehue - Tap San Felipe C2",16.23,1.5209999999999999,9.7970000000000006,0.96499999999999997,14.108000000000001,1.371,14.676,1.41,16.23,14.709,14.709]
[null,null,null,"Nueva Panquehue 110 kV - HTX Transformador 30MVA 110/13,8kV",16.23,0,9.7970000000000006,0,14.108000000000001,0,14.676,0,16.23,16.23,16.23]
[null,"Río Aconcagua",110,"Río Aconcagua 110 kV - HX1 Línea 110 kV  Esperanza (HASA) - Río Aconcagua C1",26.728999999999999,5.6829999999999998,24.83,4.5579999999999998,23.052,4.8369999999999997,26.189,5.2469999999999999,26.728999999999999,21.045999999999999,21.045999999999999]
[null,null,null,"Río Aconcagua 110 kV - HX2 Línea 110 kV  Esperanza (HASA) - Río Aconcagua C2",26.728999999999999,5.6829999999999998,24.83,4.5579999999999998,23.052,4.8369999999999997,26.189,5.2469999999999999,26.728999999999999,21.045999999999999,21.045999999999999]
[null,null,null,"Río Aconcagua 110 kV - HX3 Línea 110 kV Fundición Chagres - Río Aconcagua C1",26.728999999999999,1.3149999999999999,24.83,1.0169999999999999,23.052,1.1839999999999999,26.189,1.228,26.728999999999999,25.413999999999998,25.413999999999998]
[null,null,null,"Río Aconcagua 110 kV - HX4 Línea 110 kV Fundición Chagres - Río Aconcagua C2",26.728999999999999,1.276,24.83,1.004,23.052,1.1479999999999999,26.189,1.196,26.728999999999999,25.452999999999999,25.452999999999999]
[null,null,null,"Río Aconcagua 110 kV - HTX Transformador 350MVA 220/110/13.2 kV",26.728999999999999,12.933999999999999,24.83,13.814,23.052,11.189,26.189,13.272,26.728999999999999,13.795,13.814]
[null,"Nueva San Rafael",110,"Nueva San Rafael 110 kV - HX1 Línea 110kV Nueva San Rafael - San Rafael C1",10.146000000000001,0,6.681,0,8.9960000000000004,0,9.3930000000000007,0,10.146000000000001,10.146000000000001,10.146000000000001]
[null,null,null,"Nueva San Rafael 110 kV - HX2 Línea 110kV Nueva San Rafael - San Rafael C2",10.146000000000001,0,6.681,0,8.9960000000000004,0,9.3930000000000007,0,10.146000000000001,10.146000000000001,10.146000000000001]
[null,null,null,"Nueva San Rafael 110 kV - HX3 Línea 110kV Nueva San Rafael - Tap San Felipe C1",10.146000000000001,2.8050000000000002,6.681,1.585,8.9960000000000004,2.4159999999999999,9.3930000000000007,2.536,10.146000000000001,7.3410000000000011,7.3410000000000011]
[null,null,null,"Nueva San Rafael 110 kV - HX4 Línea 110kV Nueva San Rafael - Tap San Felipe C2",10.146000000000001,2.8050000000000002,6.681,1.585,8.9960000000000004,2.4159999999999999,9.3930000000000007,2.536,10.146000000000001,7.3410000000000011,7.3410000000000011]
[null,null,null,"Nueva San Rafael 110 kV - HX5 Línea 110kV Nueva San Rafael - Tap Los Maquis",10.146000000000001,2.29,6.681,1.7430000000000001,8.9960000000000004,2.036,9.3930000000000007,2.1360000000000001,10.146000000000001,7.8560000000000008,7.8560000000000008]
[null,null,null,"Nueva San Rafael 110 kV - HX6 Línea 110kV Nueva San Rafael - Totoralillo",10.146000000000001,2.3090000000000002,6.681,1.7909999999999999,8.9960000000000004,2.17,9.3930000000000007,2.2050000000000001,10.146000000000001,7.8370000000000006,7.8370000000000006]
[null,"Guardiamarina",110,"Guardiamarina 110 kV - HX1 Línea 110kV Guardiamarina - Tap Off Desalant",8.2680000000000007,1.9690000000000001,6.5289999999999999,1.3839999999999999,7.0590000000000002,1.6879999999999999,7.6109999999999998,1.7869999999999999,8.2680000000000007,6.2990000000000004,6.2990000000000004]
[null,null,null,"Guardiamarina 110 kV - HX2 Línea 110kV Guardiamarina - Antofagasta",8.2680000000000007,3.4609999999999999,6.5289999999999999,2.6989999999999998,7.0590000000000002,2.948,7.6109999999999998,3.1869999999999998,8.2680000000000007,4.8070000000000004,4.8070000000000004]
[null,null,null,"Guardiamarina 110 kV - HX3 Línea 110kV Guardiamarina - Esmeralda",8.2680000000000007,2.82,6.5289999999999999,2.4369999999999998,7.0590000000000002,2.4079999999999999,7.6109999999999998,2.625,8.2680000000000007,5.4480000000000004,5.4480000000000004]
[null,null,null,"Guardiamarina 110 kV - HX4 Línea 110kV Guardiamarina - La Portada",8.2680000000000007,2.1000000000000001E-2,6.5289999999999999,1.0999999999999999E-2,7.0590000000000002,1.7000000000000001E-2,7.6109999999999998,1.7999999999999999E-2,8.2680000000000007,8.2469999999999999,8.2469999999999999]
[null,null,null,"Guardiamarina 110 kV - HTX1 Transformador 30MVA 110/23kV",8.2680000000000007,0,6.5289999999999999,0,7.0590000000000002,0,7.6109999999999998,0,8.2680000000000007,8.2680000000000007,8.2680000000000007]
[null,null,null,"Guardiamarina 110 kV - HTX2 Transformador 50MVA 110/13,8kV",8.2680000000000007,0,6.5289999999999999,0,7.0590000000000002,0,7.6109999999999998,0,8.2680000000000007,8.2680000000000007,8.2680000000000007]
[null,"La Pólvora",110,"La Pólvora 110 kV - HTX Transformador 150MVA 220/110/23kV",18.931000000000001,4.7119999999999997,18.14,6.5250000000000004,16.411999999999999,4.0839999999999996,19.056000000000001,5.7009999999999996,19.056000000000001,14.219000000000001,14.219000000000001]
[null,null,null,"La Pólvora 110 kV - HX1 Línea 110kV La Pólvora - Tap Placeres C1",18.931000000000001,6.0759999999999996,18.14,4.5250000000000004,16.411999999999999,5.2709999999999999,19.056000000000001,5.569,19.056000000000001,13.615,13.615]
[null,null,null,"La Pólvora 110 kV - HX2 Línea 110kV La Pólvora - Tap Placeres C2",18.931000000000001,6.0759999999999996,18.14,4.5250000000000004,16.411999999999999,5.2709999999999999,19.056000000000001,5.569,19.056000000000001,13.615,13.615]
[null,null,null,"La Pólvora 110 kV - HX3 Línea 110kV La Pólvora - Central Laguna verde C1",18.931000000000001,1.07,18.14,1.3049999999999999,16.411999999999999,0.92400000000000004,19.056000000000001,1.244,19.056000000000001,17.861000000000001,17.861000000000001]
[null,null,null,"La Pólvora 110 kV - HX4 Línea 110kV La Pólvora - Central Laguna Verde C2",18.931000000000001,1.07,18.14,1.3049999999999999,16.411999999999999,0.92400000000000004,19.056000000000001,1.244,19.056000000000001,17.861000000000001,17.861000000000001]
[null,null,null,"La Pólvora 110 kV - HX5 Línea 110kV La Pólvora - Playa Ancha C1",18.931000000000001,0,18.14,0,16.411999999999999,0,19.056000000000001,0,19.056000000000001,19.056000000000001,19.056000000000001]
[null,null,null,"La Pólvora 110 kV - HX6 Línea 110kV La Pólvora - Playa Ancha C2",18.931000000000001,0,18.14,0,16.411999999999999,0,19.056000000000001,0,19.056000000000001,19.056000000000001,19.056000000000001]
[null,null,null,"La Pólvora 110 kV - HX7 Línea 110kV La Pólvora - Valparaíso C1",18.931000000000001,0,18.14,0,16.411999999999999,0,19.056000000000001,0,19.056000000000001,19.056000000000001,19.056000000000001]
[null,null,null,"La Pólvora 110 kV - HX8 Línea 110kV La Pólvora - Valparaíso C2",18.931000000000001,0,18.14,0,16.411999999999999,0,19.056000000000001,0,19.056000000000001,19.056000000000001,19.056000000000001]
[null,"Nueva La Negra",110,"Nueva La Negra 110 kV - HTX Transformador 120MVA 220/110kV",9.2129999999999992,4.67,9.1769999999999996,5.4640000000000004,7.8840000000000003,4.0330000000000004,9.2880000000000003,5.07,9.2880000000000003,4.5429999999999993,5.4640000000000004]
[null,null,null,"Nueva La Negra 110 kV - HT1 Transformador TR1 110/23kV",9.2129999999999992,0.109,9.1769999999999996,6.3E-2,7.8840000000000003,0.08,9.2880000000000003,8.7999999999999995E-2,9.2880000000000003,9.2000000000000011,9.2000000000000011]
[null,null,null,"Nueva La Negra 110 kV - HT2 Transformador TR2 110/23kV",9.2129999999999992,8.4000000000000005E-2,9.1769999999999996,0.05,7.8840000000000003,6.4000000000000001E-2,9.2880000000000003,6.9000000000000006E-2,9.2880000000000003,9.2189999999999994,9.2189999999999994]
[null,null,null,"Nueva La Negra 110 kV - HX1 Línea 110kV Nueva La Negra - Antofagasta",9.2129999999999992,3.0150000000000001,9.1769999999999996,2.4750000000000001,7.8840000000000003,2.5649999999999999,9.2880000000000003,2.806,9.2880000000000003,6.702,6.702]
[null,null,null,"Nueva La Negra 110 kV - HX3 Línea 110kV Nueva La Negra - Alto Norte",9.2129999999999992,1.3779999999999999,9.1769999999999996,1.155,7.8840000000000003,1.18,9.2880000000000003,1.282,9.2880000000000003,8.0220000000000002,8.0220000000000002]
[null,"Loncura",110,"Loncura 110 kV - HTX Transformador 20MVA 110/12kV",22.138000000000002,0,19.783000000000001,0,19.207999999999998,0,21.469000000000001,0,22.138000000000002,22.138000000000002,22.138000000000002]
[null,null,null,"Loncura 110 kV - HX1 Línea 110kV Loncura - Ventanas C1",22.138000000000002,6.9809999999999999,19.783000000000001,6.5659999999999998,19.207999999999998,6.0359999999999996,21.469000000000001,6.9729999999999999,22.138000000000002,15.157000000000002,15.157000000000002]
[null,null,null,"Loncura 110 kV - HX2 Línea 110kV Loncura - Ventanas C2",22.138000000000002,6.9809999999999999,19.783000000000001,6.5659999999999998,19.207999999999998,6.0359999999999996,21.469000000000001,6.9729999999999999,22.138000000000002,15.157000000000002,15.157000000000002]
[null,null,null,"Loncura 110 kV - HX3 Línea 110kV Loncura - Torquemada C1",22.138000000000002,4.0999999999999996,19.783000000000001,3.331,19.207999999999998,3.5790000000000002,21.469000000000001,3.8119999999999998,22.138000000000002,18.038000000000004,18.038000000000004]
[null,null,null,"Loncura 110 kV - HX4 Línea 110kV Loncura - Torquemada C2",22.138000000000002,4.0999999999999996,19.783000000000001,3.331,19.207999999999998,3.5790000000000002,21.469000000000001,3.8119999999999998,22.138000000000002,18.038000000000004,18.038000000000004]
[null,"Ilque",110,"Ilque 110 kV - HX1 Línea 110kV Ilique - Calbuco",3.23,0,2.3959999999999999,0,2.7879999999999998,0,2.9950000000000001,0,3.23,3.23,3.23]
[null,null,null,"Ilque 110 kV - HX2 Línea 110kV Ilique - El Empalme",3.23,3.23,2.3959999999999999,2.3959999999999999,2.7879999999999998,2.7879999999999998,2.9950000000000001,2.9950000000000001,3.23,0,3.23]
[null,"Damascal",110,"Damascal 110 kV - HX1 Transformador 30MVA 110/23kV",3.694,0,2.4580000000000002,0,3.1960000000000002,0,3.4830000000000001,0,3.694,3.694,3.694]
[null,null,null,"Damascal 110 kV - HX2 Línea 110kV Damascal - Vicuña",3.694,0,2.4580000000000002,6.0000000000000001E-3,3.1960000000000002,0,3.4830000000000001,5.0000000000000001E-3,3.694,3.694,3.694]
[null,null,null,"Damascal 110 kV - HX3 Línea 110kV Damascal - Pan de Azúcar",3.694,3.694,2.4580000000000002,2.4670000000000001,3.1960000000000002,3.1960000000000002,3.4830000000000001,3.488,3.694,0,3.694]
[null,"Litueche",110,"Litueche 110 kV - HX1 Línea 110kV Litueche - Quelentaro",5.8380000000000001,4.3319999999999999,5.9269999999999996,4.59,5.0549999999999997,3.7509999999999999,5.9850000000000003,4.5949999999999998,5.9850000000000003,1.5060000000000002,4.5949999999999998]
[null,null,null,"Litueche 110 kV - HX2 Línea 110kV Litueche - Portezuelo",5.8380000000000001,1.5069999999999999,5.9269999999999996,1.337,5.0549999999999997,1.3049999999999999,5.9850000000000003,1.4079999999999999,5.9850000000000003,4.59,4.59]
[null,"Codegua",110,"Codegua 110 kV - HTX Transformador 100MVA 110/66kV",14.500999999999999,1.7030000000000001,10.454000000000001,1.603,12.563000000000001,1.4830000000000001,13.481999999999999,1.7290000000000001,14.500999999999999,12.798,12.798]
[null,null,null,"Codegua 110 kV - HX1 Línea 110kV Codegua - Alto Jahuel C1",14.500999999999999,3.1739999999999999,10.454000000000001,2.0910000000000002,12.563000000000001,2.7530000000000001,13.481999999999999,2.9039999999999999,14.500999999999999,11.327,11.327]
[null,null,null,"Codegua 110 kV - HX2 Línea 110kV Codegua - Alto Jahuel C2",14.500999999999999,3.1739999999999999,10.454000000000001,2.089,12.563000000000001,2.7530000000000001,13.481999999999999,2.9039999999999999,14.500999999999999,11.327,11.327]
[null,null,null,"Codegua 110 kV - HX3 Línea 110kV Codegua - Sauzal C1",14.500999999999999,3.23,10.454000000000001,2.34,12.563000000000001,2.7909999999999999,13.481999999999999,2.9769999999999999,14.500999999999999,11.270999999999999,11.270999999999999]
[null,null,null,"Codegua 110 kV - HX4 Línea 110kV Codegua - Sauzal C2",14.500999999999999,3.23,10.454000000000001,2.34,12.563000000000001,2.7909999999999999,13.481999999999999,2.9769999999999999,14.500999999999999,11.270999999999999,11.270999999999999]
[null,"Trupán",154,"Trupán 154 kV - HX1 Línea 154kV Trupán - Abanico",5.5060000000000002,2.2349999999999999,4.5529999999999999,1.728,3.9089999999999998,1.1739999999999999,5.157,2.0649999999999999,5.5060000000000002,3.2710000000000004,3.2710000000000004]
[null,null,null,"Trupán 154 kV - HX2 Línea 154kV Trupán - Charrúa",5.5060000000000002,3.016,4.5529999999999999,2.3679999999999999,3.9089999999999998,2.6389999999999998,5.157,2.7559999999999998,5.5060000000000002,2.4900000000000002,3.016]
[null,null,null,"Trupán 154 kV - HTX Transformador 20MVA 154/13.8kV",5.5060000000000002,0.27800000000000002,4.5529999999999999,0.47099999999999997,3.9089999999999998,0.21199999999999999,5.157,0.47,5.5060000000000002,5.2279999999999998,5.2279999999999998]
[null,"Alfalfal",110,"Alfalfal 110 kV - HX Línea 110kV Alfalfal - Central Maitenes",15.731,9.6349999999999998,15.553000000000001,7.9240000000000004,13.56,8.2759999999999998,15.925000000000001,8.9179999999999993,15.925000000000001,7.6290000000000004,9.6349999999999998]
[null,null,null,"Alfalfal 110 kV - HTX Transformador 200MVA 220/110715MkV",15.731,6.17,15.553000000000001,7.6950000000000003,13.56,5.35,15.925000000000001,7.0510000000000002,15.925000000000001,9.5609999999999999,9.5609999999999999]