{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["2024 con y sin plan descarb"],"not_rendered":{"charts":0,"images":1,"macros":0,"external_links":1,"defined_names":2,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"2024 con y sin plan descarb","index":0,"n_rows":1283,"n_cols":11,"rows_kept":1283,"cut":false,"hidden":false,"merged":[[1268,2,1270,2],[1271,2,1272,2],[1273,2,1277,2],[1278,2,1280,2],[1281,2,1282,2],[1235,2,1240,2],[1241,2,1246,2],[1247,2,1255,2],[1256,2,1260,2],[1261,2,1265,2],[1266,2,1267,2],[1203,2,1209,2],[1213,2,1217,2],[1218,2,1220,2],[1221,2,1224,2],[1225,2,1229,2],[1230,2,1234,2],[1170,2,1171,2],[1172,2,1174,2],[1176,2,1178,2],[1180,2,1182,2],[1183,2,1200,2],[1201,2,1202,2],[1133,2,1134,2],[1141,2,1144,2],[1146,2,1149,2],[1150,2,1156,2],[1157,2,1166,2],[1167,2,1169,2],[1092,2,1093,2],[1103,2,1105,2],[1110,2,1113,2],[1115,2,1116,2],[1119,2,1124,2],[1127,2,1129,2],[1055,2,1058,2],[1059,2,1069,2],[1070,2,1073,2],[1074,2,1079,2],[1081,2,1084,2],[1088,2,1090,2],[1013,2,1021,2],[1022,2,1024,2],[1025,2,1035,2],[1036,2,1041,2],[1043,2,1047,2],[1048,2,1054,2],[996,2,997,2],[998,2,1000,2],[1001,2,1002,2],[1003,2,1004,2],[1005,2,1008,2],[1009,2,1012,2],[965,2,968,2],[970,2,971,2],[972,2,978,2],[979,2,985,2],[986,2,988,2],[989,2,995,2],[932,2,933,2],[934,2,939,2],[940,2,943,2],[944,2,950,2],[951,2,953,2],[959,2,964,2],[905,2,908,2],[909,2,911,2],[913,2,918,2],[919,2,924,2],[925,2,927,2],[928,2,931,2],[877,2,883,2],[884,2,886,2],[887,2,888,2],[889,2,891,2],[893,2,901,2],[903,2,904,2],[859,2,861,2],[862,2,863,2],[865,2,867,2],[868,2,869,2],[870,2,872,2],[873,2,876,2],[839,2,841,2],[842,2,845,2],[846,2,847,2],[848,2,850,2],[852,2,854,2],[855,2,858,2],[802,2,806,2],[809,2,810,2],[812,2,817,2],[820,2,822,2],[823,2,835,2],[836,2,838,2],[769,2,770,2],[771,2,782,2],[784,2,786,2],[787,2,790,2],[791,2,793,2],[794,2,801,2],[735,2,740,2],[742,2,743,2],[744,2,746,2],[748,2,749,2],[751,2,753,2],[754,2,768,2],[712,2,714,2],[715,2,717,2],[718,2,722,2],[723,2,726,2],[727,2,730,2],[731,2,733,2],[684,2,687,2],[690,2,691,2],[692,2,699,2],[700,2,703,2],[704,2,705,2],[707,2,710,2],[667,2,670,2],[672,2,673,2],[674,2,675,2],[676,2,677,2],[678,2,681,2],[682,2,683,2],[628,2,639,2],[641,2,643,2],[648,2,650,2],[654,2,659,2],[660,2,661,2],[662,2,666,2],[610,2,611,2],[612,2,617,2],[618,2,619,2],[620,2,622,2],[623,2,625,2],[626,2,627,2],[584,2,592,2],[593,2,596,2],[597,2,599,2],[600,2,603,2],[604,2,606,2],[607,2,609,2],[546,2,549,2],[550,2,554,2],[555,2,561,2],[562,2,566,2],[569,2,577,2],[578,2,583,2],[523,2,525,2],[526,2,528,2],[529,2,533,2],[535,2,540,2],[541,2,542,2],[543,2,545,2],[489,2,493,2],[494,2,496,2],[497,2,499,2],[501,2,506,2],[507,2,515,2],[517,2,522,2],[449,2,457,2],[458,2,461,2],[462,2,463,2],[465,2,472,2],[475,2,481,2],[482,2,488,2],[405,2,415,2],[416,2,419,2],[422,2,424,2],[425,2,427,2],[430,2,442,2],[446,2,447,2],[381,2,384,2],[385,2,388,2],[389,2,391,2],[392,2,397,2],[398,2,401,2],[402,2,404,2],[357,2,359,2],[360,2,361,2],[362,2,364,2],[365,2,366,2],[367,2,372,2],[373,2,380,2],[315,2,321,2],[323,2,328,2],[330,2,335,2],[336,2,338,2],[339,2,348,2],[350,2,356,2],[279,2,281,2],[282,2,291,2],[292,2,298,2],[299,2,302,2],[303,2,305,2],[306,2,314,2],[248,2,250,2],[251,2,263,2],[264,2,267,2],[268,2,270,2],[271,2,273,2],[275,2,277,2],[209,2,211,2],[212,2,216,2],[223,2,227,2],[231,2,233,2],[236,2,241,2],[245,2,247,2],[168,2,171,2],[172,2,182,2],[183,2,184,2],[187,2,189,2],[197,2,204,2],[205,2,206,2],[144,2,145,2],[146,2,147,2],[148,2,153,2],[154,2,155,2],[156,2,161,2],[163,2,165,2],[117,2,118,2],[120,2,121,2],[122,2,127,2],[129,2,133,2],[134,2,137,2],[138,2,140,2],[90,2,95,2],[96,2,101,2],[102,2,103,2],[104,2,107,2],[108,2,111,2],[112,2,115,2],[66,2,71,2],[72,2,73,2],[74,2,75,2],[76,2,78,2],[81,2,83,2],[84,2,89,2],[1271,1,1272,1],[1273,1,1277,1],[1278,1,1280,1],[1281,1,1282,1],[20,2,28,2],[29,2,44,2],[45,2,48,2],[49,2,50,2],[51,2,55,2],[56,2,63,2],[1241,1,1246,1],[1247,1,1255,1],[1256,1,1260,1],[1261,1,1265,1],[1266,1,1267,1],[1268,1,1270,1],[1213,1,1217,1],[1218,1,1220,1],[1221,1,1224,1],[1225,1,1229,1],[1230,1,1234,1],[1235,1,1240,1],[1172,1,1174,1],[1176,1,1178,1],[1180,1,1182,1],[1183,1,1200,1],[1201,1,1202,1],[1203,1,1209,1],[1141,1,1144,1],[1146,1,1149,1],[1150,1,1156,1],[1157,1,1166,1],[1167,1,1169,1],[1170,1,1171,1],[1103,1,1105,1],[1110,1,1113,1],[1119,1,1124,1],[1115,1,1116,1],[1127,1,1129,1],[1133,1,1134,1],[1059,1,1069,1],[1070,1,1073,1],[1074,1,1079,1],[1081,1,1084,1],[1088,1,1090,1],[1092,1,1093,1],[1022,1,1024,1],[1025,1,1035,1],[1036,1,1041,1],[1043,1,1047,1],[1048,1,1054,1],[1055,1,1058,1],[998,1,1000,1],[1001,1,1002,1],[1003,1,1004,1],[1005,1,1008,1],[1009,1,1012,1],[1013,1,1021,1],[970,1,971,1],[972,1,978,1],[979,1,985,1],[986,1,988,1],[989,1,995,1],[996,1,997,1],[934,1,939,1],[940,1,943,1],[944,1,950,1],[951,1,953,1],[959,1,964,1],[965,1,968,1],[909,1,911,1],[913,1,918,1],[919,1,924,1],[925,1,927,1],[928,1,931,1],[932,1,933,1],[884,1,886,1],[887,1,888,1],[889,1,891,1],[893,1,901,1],[903,1,904,1],[905,1,908,1],[862,1,863,1],[865,1,867,1],[868,1,869,1],[870,1,872,1],[873,1,876,1],[877,1,883,1],[842,1,845,1],[846,1,847,1],[848,1,850,1],[852,1,854,1],[855,1,858,1],[859,1,861,1],[809,1,810,1],[812,1,817,1],[820,1,822,1],[823,1,835,1],[836,1,838,1],[839,1,841,1],[771,1,782,1],[784,1,786,1],[787,1,790,1],[791,1,793,1],[794,1,801,1],[802,1,806,1],[742,1,743,1],[744,1,746,1],[748,1,749,1],[751,1,753,1],[754,1,768,1],[769,1,770,1],[715,1,717,1],[718,1,722,1],[723,1,726,1],[727,1,730,1],[731,1,733,1],[735,1,740,1],[690,1,691,1],[692,1,699,1],[700,1,703,1],[704,1,705,1],[707,1,710,1],[712,1,714,1],[672,1,673,1],[674,1,675,1],[676,1,677,1],[678,1,681,1],[682,1,683,1],[684,1,687,1],[641,1,643,1],[648,1,650,1],[654,1,659,1],[660,1,661,1],[662,1,666,1],[667,1,670,1],[612,1,617,1],[618,1,619,1],[620,1,622,1],[623,1,625,1],[626,1,627,1],[628,1,639,1],[593,1,596,1],[597,1,599,1],[600,1,603,1],[604,1,606,1],[607,1,609,1],[610,1,611,1],[550,1,554,1],[555,1,561,1],[562,1,566,1],[569,1,577,1],[578,1,583,1],[584,1,592,1],[526,1,528,1],[529,1,533,1],[535,1,540,1],[541,1,542,1],[543,1,545,1],[546,1,549,1],[494,1,496,1],[497,1,499,1],[501,1,506,1],[507,1,515,1],[517,1,522,1],[523,1,525,1],[458,1,461,1],[462,1,463,1],[465,1,472,1],[475,1,481,1],[482,1,488,1],[489,1,493,1],[416,1,419,1],[422,1,424,1],[425,1,427,1],[430,1,442,1],[446,1,447,1],[449,1,457,1],[385,1,388,1],[389,1,391,1],[392,1,397,1],[398,1,401,1],[402,1,404,1],[405,1,415,1],[360,1,361,1],[362,1,364,1],[365,1,366,1],[367,1,372,1],[373,1,380,1],[381,1,384,1],[323,1,328,1],[330,1,335,1],[336,1,338,1],[339,1,348,1],[350,1,356,1],[357,1,359,1],[282,1,291,1],[292,1,298,1],[299,1,302,1],[303,1,305,1],[306,1,314,1],[315,1,321,1],[251,1,263,1],[264,1,267,1],[268,1,270,1],[271,1,273,1],[275,1,277,1],[279,1,281,1],[212,1,216,1],[223,1,227,1],[231,1,233,1],[236,1,241,1],[245,1,247,1],[248,1,250,1],[172,1,182,1],[183,1,184,1],[187,1,189,1],[197,1,204,1],[205,1,206,1],[209,1,211,1],[148,1,153,1],[154,1,155,1],[156,1,161,1],[163,1,165,1],[168,1,171,1],[122,1,127,1],[129,1,133,1],[134,1,137,1],[138,1,140,1],[144,1,145,1],[146,1,147,1],[102,1,103,1],[104,1,107,1],[108,1,111,1],[112,1,115,1],[117,1,118,1],[120,1,121,1],[81,1,83,1],[84,1,89,1],[90,1,95,1],[96,1,101,1],[45,1,48,1],[49,1,50,1],[51,1,55,1],[56,1,63,1],[66,1,71,1],[72,1,73,1],[1,1,1,8],[9,1,19,1],[20,1,28,1],[29,1,44,1],[7,6,7,7],[7,8,7,9],[9,2,19,2],[74,1,75,1],[76,1,78,1]]}
[]
[null,"VARIACIÓN DE CORTOCIRCUITOS DEBIDO A LA PRIMERA ETAPA DEL PLAN DE DESCARBONIZACIÓN"]
[]
[null,"Código de colores y Leyendas"]
[null,"N/A","No Aplica.","                           Interruptor de poder en estado normal."]
[null,"N/P","Nuevo Proyecto.","                           Interruptor de poder en estado alerta."]
[null,"F/I","Falta Información.","                           Interruptor de poder en estado crítico."]
[null,null,null,null,null,null,"Con descarbonización",null,"Sin Descarbonización",null,"Variación Sin Descarb - Con descarb"]
[null,"S/E o Central","Nivel Tensión [kV]","ID del Paño","Nomenclatura 52 (según  ANSI/IEEE)","Capacidad 52 [kA]","Imax [kA]\nI''kss circulante","Evaluación interruptores","Imax [kA]\nI''kss circulante","Evaluación interruptores","% Variación"]
[null,10,100,"10 100 kV - H21 Línea 100kV 10 - 10A","H21","S/I",6.032,"F/I",6.1840000000000002,"F/I",2.5198938992042463E-2]
[null,null,100,"10 100 kV - H23 Línea 100kV 10 - K1","H23","S/I",9.0299999999999994,"F/I",9.2620000000000005,"F/I",2.5692137320044418E-2]
[null,null,100,"10 100 kV - HT1 Transformador TR01 8/10MVA 100/13,8kV","HT1","S/I",11.273,"F/I",11.565,"F/I",2.5902599130666178E-2]
[null,null,100,"10 100 kV - HT2 Transformador TR02 8/10MVA 100/13,8kV","HT2","S/I",11.273,"F/I",11.565,"F/I",2.5902599130666178E-2]
[null,null,100,"10 100 kV - HT3 Transformador TR03 8/10MVA 100/13,8kV","HT3","S/I",11.273,"F/I",11.565,"F/I",2.5902599130666178E-2]
[null,null,100,"10 100 kV - HT4 Transformador TR04 8/10MVA 100/13,8kV","HT4","S/I",11.273,"F/I",11.565,"F/I",2.5902599130666178E-2]
[null,null,100,"10 100 kV - HT5 Transformador TR05 8/10MVA 100/13,8kV","HT5","S/I",11.273,"F/I",11.565,"F/I",2.5902599130666178E-2]
[null,null,100,"10 100 kV - HT6 Transformador TR06 8/10MVA 100/13,8kV","HT6","S/I",11.273,"F/I",11.565,"F/I",2.5902599130666178E-2]
[null,null,100,"10 100 kV - HT7 Transformador TR07 8/10MVA 100/13,8kV","HT7","S/I",11.273,"F/I",11.565,"F/I",2.5902599130666178E-2]
[null,null,100,"10 100 kV - H10 Línea 100kV 10 - Chuquicamata","H10","S/I",8.2710000000000008,"F/I",8.4830000000000005,"F/I",2.5631725305283487E-2]
[null,null,100,"10 100 kV - HAB Acoplador","HAB","S/I",11.273,"F/I",11.565,"F/I",2.5902599130666178E-2]
[null,"10A",100,"10A 100 kV - H11 Línea 100kV 10A - Chuquicamata","H11","S/I",8.4619999999999997,"F/I",8.6789999999999985,"F/I",2.5644055778775557E-2]
[null,null,100,"10A 100 kV - HT8 Transformador TR08 15/22,4MVA 100/13,8kV","HT8","S/I",11.273,"F/I",11.565,"F/I",2.5902599130666178E-2]
[null,null,100,"10A 100 kV - HT9 Transformador TR09 15/22,4MVA 100/13,8kV","HT9","S/I",11.273,"F/I",11.565,"F/I",2.5902599130666178E-2]
[null,null,100,"10A 100 kV - HT10 Transformador TR10 15/22,4MVA 100/13,8kV","HT10","S/I",11.273,"F/I",11.565,"F/I",2.5902599130666178E-2]
[null,null,100,"10A 100 kV - HT11 Transformador TR11 44,8/59,73MVA 100/13,8kV","HT11","S/I",11.273,"F/I",11.565,"F/I",2.5902599130666178E-2]
[null,null,100,"10A 100 kV - HT12 Transformador TR12 44,8/59,73MVA 100/13,8kV","HT12","S/I",11.273,"F/I",11.565,"F/I",2.5902599130666178E-2]
[null,null,100,"10A 100 kV - HT13 Transformador TR13 45/56MVA 100/13,8kV","HT13","S/I",11.273,"F/I",11.565,"F/I",2.5902599130666178E-2]
[null,null,100,"10A 100 kV - H22 Línea 100kV 10A - KM6","H22","S/I",8.0440000000000005,"F/I",8.2579999999999991,"F/I",2.6603679761312608E-2]
[null,null,100,"10A 100 kV - HAB Acoplador","HAB","S/I",11.273,"F/I",11.565,"F/I",2.5902599130666178E-2]
[null,"A",100,"A 100 kV -  H1 Línea 100 kV A - Central Tocopilla 1"," H1","S/I",11.811999999999999,"F/I",12.114000000000001,"F/I",2.5567219776498593E-2]
[null,null,100,"A 100 kV -  H2 Línea 100 kV A - Central Tocopilla 2"," H2","S/I",11.865,"F/I",12.169,"F/I",2.5621576064053964E-2]
[null,null,100,"A 100 kV -  H3 Línea 100 kV A - Central Diesel Tamaya 1"," H3","S/I",11.738,"F/I",12.041,"F/I",2.5813596864883357E-2]
[null,null,100,"A 100 kV - H14 Línea 100 kV A - Chuquicamata 1","H14",31.5,7.7569999999999997,0.24625396825396825,8.0340000000000007,0.25504761904761908,3.5709681577929746E-2]
[null,null,100,"A 100 kV - H15 Línea 100 kV A - Chuquicamata 2","H15",31.5,6.5179999999999998,0.20692063492063492,6.77,0.2149206349206349,3.8662166308683611E-2]
[null,null,100,"A 100 kV - HT3 Transformador TR03 10 MVA 100/5 kV ","HT3","S/I",12.407999999999999,"F/I",12.765000000000001,"F/I",2.8771760154738969E-2]
[null,null,100,"A 100 kV - HT4 Transformador TR04 10 MVA 100/5 kV ","HT4","S/I",12.407999999999999,"F/I",12.765000000000001,"F/I",2.8771760154738969E-2]
[null,null,100,"A 100 kV - HT13 Transformador TR13 20 MVA 100/13,8 kV ","HT13","S/I",12.407999999999999,"F/I",12.765000000000001,"F/I",2.8771760154738969E-2]
[null,null,100,"A 100 kV - HT14 Transformador TR14 20/25 MVA 100/13,8 kV ","HT14","S/I",12.407999999999999,"F/I",12.765000000000001,"F/I",2.8771760154738969E-2]
[null,null,100,"A 100 kV - HT15 Transformador TR15 25/33,3 MVA 100/13,8 kV","HT15","S/I",12.407999999999999,"F/I",12.765000000000001,"F/I",2.8771760154738969E-2]
[null,null,100,"A 100 kV - HT16 Transformador TR16 25/33,3 MVA 100/13,8 kV","HT16","S/I",12.407999999999999,"F/I",12.765000000000001,"F/I",2.8771760154738969E-2]
[null,null,100,"A 100 kV - HT17 Transformador TR17 40/56 MVA 100/13,8 kV","HT17","S/I",12.407999999999999,"F/I",12.765000000000001,"F/I",2.8771760154738969E-2]
[null,null,100,"A 100 kV - HT18 Transformador TR18 25/33,3 MVA 100/13,8 kV","HT18","S/I",12.407999999999999,"F/I",12.765000000000001,"F/I",2.8771760154738969E-2]
[null,null,100,"A 100 kV - HT19 Transformador TR19 40/56 MVA 100/13,8 kV","HT19","S/I",12.407999999999999,"F/I",12.765000000000001,"F/I",2.8771760154738969E-2]
[null,null,100,"A 100 kV - HC Banco de Condensadores 1","HC","S/I",12.407999999999999,"F/I",12.765000000000001,"F/I",2.8771760154738969E-2]
[null,null,100,"A 100 kV - HACOP Acoplador","HACOP","S/I",12.407999999999999,"F/I",12.765000000000001,"F/I",2.8771760154738969E-2]
[null,"Abanico",154,"Abanico 154 kV -  A2 Línea 154kV Trupán - Abanico"," A2",9,3.2160000000000002,0.35733333333333334,3.2160000000000002,0.35733333333333334,0]
[null,null,154,"Abanico 154 kV - AT1 Transformador Abanico N°1 y N°2","AT1",40,4.8120000000000003,0.1203,4.8130000000000006,0.12032500000000002,2.0781379883631212E-4]
[null,null,154,"Abanico 154 kV - AT3 Transformador Abanico N°3","AT3",13,4.8490000000000002,0.373,4.8500000000000005,0.37307692307692314,2.0622808826569063E-4]
[null,null,154,"Abanico 154 kV - AT4 Transformador Abanico N°4","AT4",13,4.2720000000000002,0.32861538461538464,4.2730000000000006,0.32869230769230773,2.3408239700382346E-4]
[null,"ACL",100,"ACL 100 kV - H1 Línea 100 kV ACL - KM6 1","H1",10,5.24,0.52400000000000002,5.3209999999999997,0.53210000000000002,1.545801526717548E-2]
[null,null,100,"ACL 100 kV - HT1 Transformador ACL 100/13.8 kV","HT1","S/I",5.24,"F/I",5.3209999999999997,"F/I",1.545801526717548E-2]
[null,"Aconcagua ",110,"Aconcagua  110 kV - H1 Transformador TR1 110/12 kV (Unidad 1 - Blanco)","H1",40,7.5380000000000003,0.18845000000000001,7.5489999999999995,0.18872499999999998,1.4592730167152072E-3]
[null,null,110,"Aconcagua  110 kV - H2 Transformador TR2 110/12 kV (Unidad 2 - Juncal)","H2",40,9.6790000000000003,0.241975,9.69,0.24224999999999999,1.1364810414298205E-3]
[null,null,110,"Aconcagua  110 kV - H3 Línea 110 kV Aconcagua - Los Maquis/San Rafael 1","H3",40,7.5969999999999995,0.18992499999999998,7.6050000000000004,0.19012500000000002,1.0530472554957082E-3]
[null,null,110,"Aconcagua  110 kV - H4 Línea 110 kV Aconcagua - Los Maquis/Totoralillo 2","H4",40,7.593,0.18982499999999999,7.6010000000000009,0.19002500000000003,1.0536020018439213E-3]
[null,null,110,"Aconcagua  110 kV - HT Transformador TR03 110/66/12 kV ","HT",31.5,9.9469999999999992,0.31577777777777777,9.9589999999999996,0.31615873015873014,1.2063938876043486E-3]
[null,"Agua Santa ",110,"Agua Santa  110 kV -  H7 Línea 110 kV Agua Santa - Miraflores 2"," H7",40,23.386000000000003,0.58465000000000011,23.855999999999998,0.59639999999999993,2.0097494227315285E-2]
[null,null,110,"Agua Santa  110 kV -  H8 Línea 110 kV Agua Santa - Miraflores 1"," H8",40,23.386000000000003,0.58465000000000011,23.855999999999998,0.59639999999999993,2.0097494227315285E-2]
[null,null,110,"Agua Santa  110 kV -  H9 Línea 110 kV Agua Santa - Tap Los Placeres 2"," H9",40,25.274000000000001,0.63185000000000002,26.085999999999999,0.65215000000000001,3.2127878452164187E-2]
[null,null,110,"Agua Santa  110 kV - H10 Línea 110 kV Agua Santa - Tap Los Placeres 1","H10",40,25.274000000000001,0.63185000000000002,26.085999999999999,0.65215000000000001,3.2127878452164187E-2]
[null,null,110,"Agua Santa  110 kV - HX Línea 110 kV Agua Santa - Placilla C2 ","HX","S/I",27.436999999999998,"N/P",28.312999999999999,"N/P",3.1927688887269066E-2]
[null,null,110,"Agua Santa  110 kV - H11 Línea 110 kV Agua Santa - Placilla ","H11",40,27.454999999999998,0.68637499999999996,28.331,0.70827499999999999,3.1906756510653847E-2]
[null,null,110,"Agua Santa  110 kV - HTX Transformador TR2 300 MVA 220/110/66 kV ","HTX","S/I",20.885000000000002,"N/P",21.591999999999999,"N/P",3.385204692362926E-2]
[null,null,110,"Agua Santa  110 kV - HT1 Transformador TR1 300 MVA 220/110/66 kV ","HT1",50,20.599,0.41198000000000001,21.393000000000001,0.42786000000000002,3.8545560464100223E-2]
[null,"Aihuapi ",110,"Aihuapi  110 kV - HT3 Transformador TR3 27/40 MVA 110/66 kV ","HT3",40,4.2460000000000004,0.10615000000000001,4.2460000000000004,0.10615000000000001,0]
[null,"Algarrobo ",110,"Algarrobo  110 kV - H1 TR 1 110/4,6 kV 6 MVA ","H1","S/I",3.9790000000000001,"F/I",3.9790000000000001,"F/I",0]
[null,"Alonso de Córdova ",110,"Alonso de Córdova  110 kV - H1 Línea 110 kV Alonso de Córdova - Los Almendros (Apoquindo)/El Salto (Vitacura) 1","H1",40,15.56,0.38900000000000001,15.603,0.39007500000000001,2.7634961439588213E-3]
[null,null,110,"Alonso de Córdova  110 kV - H2 Línea 110 kV Alonso de Córdova - Los Almendros (Apoquindo) /El Salto (Vitacura 2","H2",40,15.559999999999999,0.38899999999999996,15.602999999999998,0.39007499999999995,2.7634961439588217E-3]
[null,null,110,"Alonso de Córdova  110 kV - HT1 Transformador TR01 50 MVA 110/12,5 kV ","HT1",31.5,31.097999999999999,0.98723809523809525,31.184999999999999,0.99,2.797607563187335E-3]
[null,null,110,"Alonso de Córdova  110 kV - HT2 Transformador TR02 50 MVA 110/12,5 kV ","HT2",40,31.097999999999999,0.77744999999999997,31.184999999999999,0.77962500000000001,2.797607563187335E-3]
[null,null,110,"Alonso de Córdova  110 kV - HT3 Transformador TR03 50 MVA 110/12,5 kV ","HT3",40,31.097999999999999,0.77744999999999997,31.184999999999999,0.77962500000000001,2.797607563187335E-3]
[null,null,110,"Alonso de Córdova  110 kV - H4 Transformador TR04 50 MVA 110/12,5 kV ","H4",40,31.097999999999999,0.77744999999999997,31.184999999999999,0.77962500000000001,2.797607563187335E-3]
[null,"Alonso de Ribera",154,"Alonso de Ribera 154 kV - AT1 Transformador Alonso de Ribera TR1 75MVA 154/66/14,8kV","AT1",40,19.893999999999998,0.49734999999999996,20.354000000000003,0.50885000000000002,2.3122549512416025E-2]
[null,null,154,"Alonso de Ribera 154 kV - AT2 Transformador Alonso de Ribera TR2 75MVA 154/66/14,8kV","AT2",40,19.919999999999998,0.49799999999999994,20.382000000000001,0.50955000000000006,2.3192771084337517E-2]
[null,"Altamirano ",110,"Altamirano  110 kV -  H1 Línea 110 kV Altamirano - Cerro Navia/Renca 1 "," H1",31.5,24.274999999999999,0.77063492063492056,24.364000000000001,0.77346031746031751,3.6663233779609555E-3]
[null,null,110,"Altamirano  110 kV -  H2 Línea 110 kV Altamirano - Cerro Navia/Renca 2"," H2",31.5,24.274999999999999,0.77063492063492056,24.364000000000001,0.77346031746031751,3.6663233779609555E-3]
[null,"Alto Bonito ",110,"Alto Bonito  110 kV - H1 Línea 110 kV Alto Bonito - Melipulli ","H1",40,2.5669999999999997,6.4174999999999996E-2,2.5669999999999997,6.4174999999999996E-2,0]
[null,null,110,"Alto Bonito  110 kV -  H2 Línea 110 kV Alto Bonito - Molinos "," H2",40,2.569,6.4225000000000004E-2,2.569,6.4225000000000004E-2,0]
[null,null,110,"Alto Bonito  110 kV - HT1 Transformador TR1 30 MVA 115/24,5 kV ","HT1",40,4.6959999999999997,0.11739999999999999,4.6959999999999997,0.11739999999999999,0]
[null,"Alto del Carmen ",110,"Alto del Carmen  110 kV -  En Barra",null,null,1.8069999999999999,"N/A",1.8069999999999999,"N/A",0]
[null,"Alto Hospicio ",110,"Alto Hospicio  110 kV - HT1 Transformador T1 15/12,5/10 MVA 110/13,8 kV ","HT1","S/I",4.0869999999999997,"F/I",4.25,"F/I",3.9882554440910267E-2]
[null,"Alto Jahuel",154,"Alto Jahuel 154 kV - A1 Línea 154 kV Alto Jahuel - Fátima/ Rancagua 1/ Tingiuririca 1","A1",32,15.21,0.47531250000000003,15.223999999999998,0.47574999999999995,9.2044707429306835E-4]
[null,null,154,"Alto Jahuel 154 kV - A2 Línea 154 kV Alto Jahuel - Fátima/ Rancagua 2/ Tingiuririca 2","A2",32,15.21,0.47531250000000003,15.223999999999998,0.47574999999999995,9.2044707429306835E-4]
[null,null,154,"Alto Jahuel 154 kV - AT6 Transformador Alto Jahuel ATR6 220/154 kV ","AT6",40,12.67,0.31674999999999998,12.683,0.317075,1.0260457774269852E-3]
[null,"Alto Jahuel ",110,"Alto Jahuel  110 kV - HT1 Transformador ATR1 30 MVA 110/66/13,8 kV ","HT1",63,49.009,0.7779206349206349,49.122,0.77971428571428569,2.3056989532534745E-3]
[null,null,110,"Alto Jahuel  110 kV -  H2 Línea 110kV Codegua - Alto Jahuel C1"," H2",63,48.619,0.77173015873015871,48.731999999999999,0.7735238095238095,2.3241942450482229E-3]
[null,null,110,"Alto Jahuel  110 kV - HT2 Transformador ATR2 390 MVA 220/110/13,2 kV ","HT2",50,33.770000000000003,0.67540000000000011,33.864999999999995,0.6772999999999999,2.8131477642875853E-3]
[null,null,110,"Alto Jahuel  110 kV -  H1 Línea 110kV Codegua - Alto Jahuel C2"," H1",40,48.618000000000002,1.2154500000000001,48.730999999999995,1.2182749999999998,2.324242050269292E-3]
[null,null,110,"Alto Jahuel  110 kV -  H5 Línea 110 kV Alto Jahuel - Florida (Buin) 1"," H5",63,36.002000000000002,0.57146031746031745,36.083999999999996,0.57276190476190469,2.2776512415975119E-3]
[null,null,110,"Alto Jahuel  110 kV -  H6 Línea 110 kV Alto Jahuel - Florida (Buin) 2"," H6",25,36.002000000000002,1.44008,36.083999999999996,1.4433599999999998,2.2776512415975119E-3]
[null,"Alto Melipilla ",110,"Alto Melipilla  110 kV - HT1 Transformador TR1 150 MVA 220/110/13,2 kV ","HT1",40,6.1520000000000001,0.15379999999999999,6.1610000000000005,0.15402500000000002,1.4629388816645547E-3]
[null,null,110,"Alto Melipilla  110 kV - HTX Transformador TR2 150 MVA 220/110/13,2 kV ","HTX","S/I",6.1520000000000001,"N/P",6.1610000000000005,"N/P",1.4629388816645547E-3]
[null,null,110,"Alto Melipilla  110 kV -  H2 Línea 110 kV Alto Melipilla - San Antonio "," H2",40,11.135,0.27837499999999998,11.152000000000001,0.27880000000000005,1.5267175572520194E-3]
[null,null,110,"Alto Melipilla  110 kV -  H4 Línea 110 kV Alto Melipilla - Tap Off Alto Melipilla"," H4",40,11.48,0.28700000000000003,11.498000000000001,0.28745000000000004,1.5679442508711396E-3]
[null,null,110,"Alto Melipilla  110 kV - HX Línea 110kV Alto Melipilla - Bajo Melipilla","HX","S/I",11.478,"N/P",11.496,"N/P",1.5682174594877751E-3]
[null,null,110,"Alto Melipilla  110 kV -  H3 Línea 110 kV Alto Melipilla - Leyda"," H3",40,11.135999999999999,0.27839999999999998,11.153,0.27882499999999999,1.5265804597702261E-3]
[null,"Alto Norte ",110,"Alto Norte  110 kV -  H3 Línea 110 kV Alto Norte - Nueva La Negra"," H3",31.5,6.1429999999999998,0.195015873015873,6.149,0.19520634920634922,9.7672147159372094E-4]
[null,null,110,"Alto Norte  110 kV -  H4 Línea 110 kV Alto Norte - Capricornio/Tap Off El Negro "," H4",31.5,6.1429999999999998,0.195015873015873,6.1479999999999997,0.19517460317460317,8.1393455966138591E-4]
[null,null,110,"Alto Norte  110 kV - HT1 Transformador TR1 110/13,8 kV ","HT1","S/I",7.81,"F/I",7.8170000000000002,"F/I",8.9628681177984142E-4]
[null,null,110,"Alto Norte  110 kV - HT2 Transformador TR2 110/13,8 kV ","HT2","S/I",7.81,"F/I",7.8170000000000002,"F/I",8.9628681177984142E-4]
[null,null,110,"Alto Norte  110 kV - HT3 Transformador TR3 110/13,8 kV ","HT3","S/I",7.81,"F/I",7.8170000000000002,"F/I",8.9628681177984142E-4]
[null,null,110,"Alto Norte  110 kV - HT4 Transformador TR4 110/13,8 kV ","HT4","S/I",7.81,"F/I",7.8170000000000002,"F/I",8.9628681177984142E-4]
[null,"Ancud ",110,"Ancud  110 kV - HT1 Transformador TR1 110/23 kV ","HT1",25,2.9609999999999999,0.11843999999999999,2.9609999999999999,0.11843999999999999,0]
[null,null,110,"Ancud  110 kV - HT2 Transformador TR2 110/110 kV (Línea 110 kV Ancud - Chiloé)","HT2",25,2.1739999999999999,8.6959999999999996E-2,2.1739999999999999,8.6959999999999996E-2,0]
[null,"Andes ",110,"Andes  110 kV - H1 Línea 110 kV Andes - Los Almendros/Florida 1","H1",40,15.244999999999999,0.38112499999999999,15.280000000000001,0.38200000000000001,2.295834699901733E-3]
[null,null,110,"Andes  110 kV - H2 Línea 110 kV Andes - Los Almendros/Florida 2","H2",40,15.244999999999999,0.38112499999999999,15.280000000000001,0.38200000000000001,2.295834699901733E-3]
[null,null,110,"Andes  110 kV - HT1 Transformador TR01 50 MVA 110/12,5 kV ","HT1",40,30.489000000000001,0.76222500000000004,30.559000000000001,0.76397500000000007,2.2959100003279963E-3]
[null,null,110,"Andes  110 kV - HT4 Transformador TR04 22,4 MVA 110/12,5 kV ","HT4",40,30.489000000000001,0.76222500000000004,30.559000000000001,0.76397500000000007,2.2959100003279963E-3]
[null,"Antillanca ",110,"Antillanca  110 kV - HT1 Transformador T1 220/110/23 kV ","HT1",40,4.399,0.109975,4.399,0.109975,0]
[null,null,110,"Antillanca  110 kV - H1 Línea 110 kV Antillanca - Central Licán/Mantilhue ","H1",40,5.36,0.13400000000000001,5.36,0.13400000000000001,0]
[null,null,110,"Antillanca  110 kV - H2 Línea 110 kV Antillanca - Aihuapi ","H2",40,5.4750000000000005,0.13687500000000002,5.4750000000000005,0.13687500000000002,0]
[null,null,110,"Antillanca  110 kV - H3 Línea 110 kV Antillanca - Río Bonito ","H3",40,5.9950000000000001,0.14987500000000001,5.9950000000000001,0.14987500000000001,0]
[null,"Antofagasta ",110,"Antofagasta  110 kV - HT1 Transformador TR1 110/13,8 kV ","HT1",40,9.1829999999999998,0.229575,9.1920000000000002,0.2298,9.8007187193731261E-4]
[null,null,110,"Antofagasta  110 kV -  H1 Línea 110 kV Antofagasta -Tap Off Uribe/Capricornio"," H1",40,5.4039999999999999,0.1351,5.4090000000000007,0.13522500000000001,9.2524056254640673E-4]
[null,null,110,"Antofagasta  110 kV -  H3 Línea 110kV Guardiamarina - Antofagasta"," H3",31.5,6.8729999999999993,0.21819047619047616,6.8789999999999996,0.21838095238095237,8.7298123090356872E-4]
[null,null,110,"Antofagasta  110 kV -  H2 Línea 110 kV Antofagasta - Nueva La Negra"," H2",40,6.0839999999999996,0.15209999999999999,6.09,0.15225,9.8619329388563892E-4]
[null,"Antucoya ",110,"Antucoya  110 kV -  HT Transformador TR01 10/12,5 MVA 110/23 kV "," HT","S/I",1.0569999999999999,"F/I",1.0569999999999999,"F/I",0]
[null,"Apoquindo ",110,"Apoquindo  110 kV -  H1 Línea 110 kV Apoquindo - Los Almendros (Los Dominicos) / El Salto  (Alonso de Córdova) 1 "," H1",40,16.143000000000001,0.40357500000000002,16.186,0.40465000000000001,2.6636932416526826E-3]
[null,null,110,"Apoquindo  110 kV -  H2 Línea 110 kV Apoquindo - Los Almendros  (Los Dominicos) /El Salto (Alonso de Córdova) 2"," H2",40,16.143000000000001,0.40357500000000002,16.185000000000002,0.40462500000000007,2.6017468871957872E-3]
[null,"Arica ",110,"Arica  110 kV - HT3 Autotransformador 110/66/13,8 kV ","HT3",31.5,2.649,8.4095238095238098E-2,2.6859999999999999,8.5269841269841273E-2,1.3967534918837267E-2]
[null,"Atacama Kozán ",110,"Atacama Kozán  110 kV -  En Barra",null,null,7.1550000000000002,"N/A",7.1580000000000004,"N/A",4.1928721174005779E-4]
[null,null,110,"Atacama Kozán  110 kV - HX Línea 110 kV Cerrillos - Atacama Kozán","HX","S/I",4.9459999999999997,"N/P",4.9489999999999998,"N/P",6.0655074807927894E-4]
[null,"Bajo Melipilla ",110,"Bajo Melipilla  110 kV - HT1 Transformador TR01 25/20/15 MVA 110/13,2 kV ","HT1",25,9.2590000000000003,0.37036000000000002,9.2769999999999992,0.37107999999999997,1.9440544335240205E-3]
[null,null,110,"Bajo Melipilla  110 kV - HT2 Transformador TR02 40/50 MVA 110/66 kV ","HT2",40,9.1720000000000006,0.2293,9.19,0.22974999999999998,1.9624945486261345E-3]
[null,null,110,"Bajo Melipilla  110 kV - H3 Línea 110 kV Bajo Melipilla - Tap Alto Melipilla ","H3",40,4.7960000000000003,0.11990000000000001,4.8059999999999992,0.12014999999999998,2.085070892410112E-3]
[null,null,110,"Bajo Melipilla  110 kV - H4 Línea 110 kV Bajo Melipilla - Carga Móvil ","H4","S/I",9.2590000000000003,"F/I",9.2769999999999992,"F/I",1.9440544335240205E-3]
[null,null,110,"Bajo Melipilla  110 kV - HX Línea 110kV Alto Melipilla - Bajo Melipilla","HX","S/I",4.7480000000000002,"N/P",4.7569999999999997,"N/P",1.8955349620891854E-3]
[null,null,110,"Bajo Melipilla  110 kV - HT3 Transformador TR03 25/20/15 MVA 110/13,2 kV ","HT3",31.5,9.2590000000000003,0.29393650793650794,9.2769999999999992,0.2945079365079365,1.9440544335240205E-3]
[null,"Baños del Toro ",110,"Baños del Toro  110 kV - H1 Transformador Baños del Toro (El Indio) 110/13.2 kV","H1","S/I",0.86099999999999999,"F/I",0.86099999999999999,"F/I",0]
[null,"Batuco ",110,"Batuco  110 kV -  H1 Línea 110 kV Batuco - Tap Off Punta Peuco/Cerro Navia 1"," H1",40,8.98,0.22450000000000001,9.0070000000000014,0.22517500000000004,3.0066815144767283E-3]
[null,null,110,"Batuco  110 kV -  H2 Línea 110 kV Batuco - Tap Off Punta Peuco/Cerro Navia 2"," H2",40,8.98,0.22450000000000001,9.0070000000000014,0.22517500000000004,3.0066815144767283E-3]
[null,null,110,"Batuco  110 kV - HT1 Transformador TR01 37,5 MVA 110/23,5 kV ","HT1",31.5,17.959,0.57012698412698415,18.013000000000002,0.57184126984126993,3.0068489336823904E-3]
[null,null,110,"Batuco  110 kV - HT2 Transformador TR02 37,5 MVA 110/23,5 kV ","HT2",40,17.959,0.44897500000000001,18.013000000000002,0.45032500000000003,3.0068489336823904E-3]
[null,null,110,"Batuco  110 kV - HT3 Transformador TR03 50 MVA 110/23,5 kV ","HT3",31.5,17.959,0.57012698412698415,18.013000000000002,0.57184126984126993,3.0068489336823904E-3]
[null,"Bicentenario ",110,"Bicentenario  110 kV -  H1 Línea 110 kV Bicentenario - Cerro Navia (Santa Marta) /Chena 1"," H1",40,20.664999999999999,0.516625,20.733000000000001,0.51832500000000004,3.2905879506412482E-3]
[null,null,110,"Bicentenario  110 kV -  H2 Línea 110 kV Bicentenario - Cerro Navia (Santa Marta) /Chena 2"," H2",40,20.664999999999999,0.516625,20.733000000000001,0.51832500000000004,3.2905879506412482E-3]
[null,null,110,"Bicentenario  110 kV - HT1 Transformador TR01 25 MVA 110/12,5 kV ","HT1",40,41.33,1.03325,41.466000000000001,1.0366500000000001,3.2905879506412482E-3]
[null,null,110,"Bicentenario  110 kV - HT2 Transformador TR02 25 MVA 110/13,2 kV ","HT2",25,41.33,1.6532,41.466000000000001,1.6586400000000001,3.2905879506412482E-3]
[null,"Bocamina",154,"Bocamina 154 kV - A1 Línea 154 kV Bocamina - Lagunillas","A1",40,10.901,0.27252500000000002,10.938000000000001,0.27345000000000003,3.3941840198147702E-3]
[null,null,154,"Bocamina 154 kV - AT1 Transformador Bocamina TR01 147MVA 161/13.8 kV N°1","AT1","S/I",10.888,"F/I",10.911000000000001,"F/I",2.1124173401911705E-3]
[null,null,154,"Bocamina 154 kV - AT2 Transformador Bocamina 161/13.8 kV SSAA","AT2","S/I",12.18,"F/I",14.053000000000001,"F/I",0.15377668308702802]
[null,"Bollenar ",110,"Bollenar  110 kV - HT Transformador TR1 20/16 MVA 110/23-13,8 kV ","HT",40,4.7110000000000003,0.117775,4.7160000000000002,0.1179,1.0613457864572051E-3]
[null,"Bombeo 2 ",110,"Bombeo 2  110 kV - H1 Transformador TR1 110/4.16 kV 10 MVA ","H1",40,2.069,5.1725E-2,2.069,5.1725E-2,0]
[null,"Bombeo 1 y Desaladora",110,"Bombeo 1 y Desaladora 110 kV - H2 Transformador N°1 110/4.16 kV Planta Desaladora y Bombeo 1","H2",40,1.625,4.0625000000000001E-2,1.625,4.0625000000000001E-2,0]
[null,"Bosquemar ",110,"Bosquemar  110 kV - HX Línea 110kV Reñaca - Bosquemar","HX","S/I",11.213000000000001,"N/P",11.831999999999999,"N/P",5.5203781325247295E-2]
[null,null,110,"Bosquemar  110 kV - H1 Línea 110 kV Bosquemar - Concon","H1","S/I",11.215,"F/I",11.834,"F/I",5.5193936691930429E-2]
[null,"Brasil ",110,"Brasil  110 kV -  H1 Línea 110 kV Brasil - Renca (Carrascal) 1 "," H1",40,20.812999999999999,0.52032499999999993,20.879000000000001,0.52197500000000008,3.1710949887091004E-3]
[null,null,110,"Brasil  110 kV -  H2 Línea 110 kV Brasil - Renca (Carrascal)  2"," H2",40,20.812999999999999,0.52032499999999993,20.879000000000001,0.52197500000000008,3.1710949887091004E-3]
[null,"Buin ",110,"Buin  110 kV -  H1 Línea 110 kV Buin - Lo Espejo (San Bernardo) 2 "," H1",31.5,44.888999999999996,1.4250476190476189,44.988,1.4281904761904762,2.2054400855444265E-3]
[null,null,110,"Buin  110 kV -  H2 Línea 110 kV Buin - Lo Espejo (San Bernardo)  1 "," H2",31.5,44.888999999999996,1.4250476190476189,44.988,1.4281904761904762,2.2054400855444265E-3]
[null,null,110,"Buin  110 kV -  H3 Línea 110 kV Buin - Florida (La Pintana)  2"," H3",31.5,37.940999999999995,1.2044761904761903,38.027999999999999,1.2072380952380952,2.2930339210880924E-3]
[null,null,110,"Buin  110 kV -  H4 Línea 110 kV Buin - Florida  (La Pintana) 1"," H4",31.5,37.940999999999995,1.2044761904761903,38.027999999999999,1.2072380952380952,2.2930339210880924E-3]
[null,null,110,"Buin  110 kV - HT1 Transformador TR01 400 MVA 220/110/13,8 kV ","HT1",31.5,32.379000000000005,1.0279047619047621,32.475000000000001,1.0309523809523811,2.9648846474565772E-3]
[null,null,110,"Buin  110 kV - CCE1A Banco de Condensadores 1","CCE1A",40,49.23,1.23075,49.341000000000001,1.233525,2.2547227300427426E-3]
[null,"Cabildo ",110,"Cabildo  110 kV - HT2 Transformador TR2 13/10 MVA 110/24-14,4 kV ","HT2",40,2.0139999999999998,5.0349999999999992E-2,2.016,5.04E-2,9.9304865938442104E-4]
[null,null,110,"Cabildo  110 kV - HT1 Transformador TR1 30/24/18 MVA 110/25 kV","HT1",40,2.0139999999999998,5.0349999999999992E-2,2.016,5.04E-2,9.9304865938442104E-4]
[null,"Calama ",110,"Calama  110 kV - HT1 Transformador TR01 33/25 MVA 110/23 kV ","HT1",40,8.6679999999999993,0.21669999999999998,8.7579999999999991,0.21894999999999998,1.0383017997231179E-2]
[null,null,110,"Calama  110 kV - HT4 Transformador TR04 33/25 MVA 110/23 kV ","HT4",40,8.6679999999999993,0.21669999999999998,8.7579999999999991,0.21894999999999998,1.0383017997231179E-2]
[null,null,110,"Calama  110 kV - H3 Línea 110 kV Calama - Valle de los Vientos ","H3",31.5,8.1579999999999995,0.25898412698412698,8.2439999999999998,0.26171428571428573,1.0541799460652158E-2]
[null,null,110,"Calama  110 kV - HT5 Transformador TR1P 55/45/5 MVA 210/110/12,2 kV ","HT5",31.5,4.6759999999999993,0.14844444444444443,4.7130000000000001,0.14961904761904762,7.9127459366982074E-3]
[null,null,110,"Calama  110 kV - HTX Transformador 150MVA 210/110/23 kV","HTX","S/I",4.6759999999999993,"N/P",4.7130000000000001,"N/P",7.9127459366982074E-3]
[null,null,110,"Calama  110 kV - H2 Línea 110 kV Calama - San Pedro ","H2","S/I",8.7119999999999997,"F/I",8.8019999999999996,"F/I",1.0330578512396679E-2]
[null,"Calbuco ",110,"Calbuco  110 kV - HT1 Transformador TR1 16 MVA 115/69/24 kV ","HT1",40,2.625,6.5625000000000003E-2,2.625,6.5625000000000003E-2,0]
[null,"Caldera",110,"Caldera 110 kV - HX1 Línea 110kV Caldera - Punta Padrones","HX1","S/I",2.7669999999999999,"N/P",2.7669999999999999,"N/P",0]
[null,null,110,"Caldera 110 kV - HX2 Línea 110kV Caldera - EB2","HX2","S/I",1.4510000000000001,"N/P",1.452,"N/P",6.8917987594754643E-4]
[null,null,110,"Caldera  110 kV - HT1 Transformador T1 12/10 MVA 110/23-13.2 kV ","HT1",40,2.7669999999999999,6.9175E-2,2.7669999999999999,6.9175E-2,0]
[null,"Canal Melado ",110,"Canal Melado  110 kV - HT Transformador TR 220/110/13.8 kV 70 MVA ","HT",40,4.0670000000000002,0.101675,4.0670000000000002,0.101675,0]
[null,"CAP Rengo",154,"CAP Rengo 154 kV -  En Barra",null,null,11.798,"N/A",11.804,"N/A",5.0856077301239424E-4]
[null,"Capricornio ",110,"Capricornio  110 kV - HT1 Transformador TR01 80/80/20 MVA 220/110/13,8 kV ","HT1",31.5,4.7040000000000006,0.14933333333333335,4.7080000000000002,0.14946031746031746,8.5034013605432795E-4]
[null,null,110,"Capricornio  110 kV - H2 Línea 110 kV Capricornio - Alto Norte/Tap Off El Negro ","H2",31.5,6.1180000000000003,0.19422222222222224,6.1230000000000002,0.19438095238095238,8.1726054266098287E-4]
[null,null,110,"Capricornio  110 kV - H1 Línea 110 kV Capricornio - Tap Off Uribe/Antofagasta","H1",31.5,5.05,0.1603174603174603,5.0540000000000003,0.16044444444444445,7.9207920792088071E-4]
[null,null,110,"Capricornio  110 kV - H3 Línea 110 kV Capricornio - Sierra Miranda ","H3",31.5,7.6340000000000003,0.24234920634920637,7.641,0.24257142857142858,9.1695048467378476E-4]
[null,"Cardones ",110,"Cardones  110 kV - H8 Línea 110 kV Cardones - Central Cenizas ","H8",40,11.111000000000001,0.27777499999999999,11.117000000000001,0.27792500000000003,5.4000540005402092E-4]
[null,null,110,"Cardones  110 kV - H3 Línea 110 kV Copayapu - Cardones C2","H3",40,11.134,0.27834999999999999,11.14,0.27850000000000003,5.3888988683314422E-4]
[null,null,110,"Cardones  110 kV - H2 Línea 110 kV Cardones - Maintencillo ","H2",40,11.079000000000001,0.27697500000000003,11.085000000000001,0.27712500000000001,5.41565123206086E-4]
[null,null,110,"Cardones  110 kV - HT1 AutoTransformador ATR1 75 MVA 220/115/13,8 kV ","HT1",40,9.1370000000000005,0.22842500000000002,9.141,0.22852500000000001,4.3778045310272073E-4]
[null,null,110,"Cardones  110 kV - H4 Línea 110 kV Cardones - Copayapu/Cerrillos/Tierra Amarilla ","H4",31.5,10.531000000000001,0.33431746031746035,10.536000000000001,0.33447619047619054,4.7478871902011029E-4]
[null,null,110,"Cardones  110 kV - HT2 AutoTransformador ATR2 75 MVA 220/115/13,8 kV ","HT2",31.5,9.2460000000000004,0.29352380952380952,9.2510000000000012,0.29368253968253971,5.4077438892502505E-4]
[null,null,110,"Cardones  110 kV - H6 Línea 110 kV Cardones - Fundición Paipote ","H6",31.5,11.926,0.37860317460317461,11.932,0.37879365079365079,5.0310246520209859E-4]
[null,null,110,"Cardones  110 kV - HT3 AutoTransformador ATR3 79 MVA 220/115/13,8 kV ","HT3",50,9.2029999999999994,0.18406,9.2080000000000002,0.18415999999999999,5.4330109746830182E-4]
[null,null,110,"Cardones  110 kV - H9 Línea 110 kV Cardones - Travesía ","H9",40,11.920999999999999,0.29802499999999998,11.927,0.29817499999999997,5.033134804127362E-4]
[null,null,110,"Cardones  110 kV - H7 Línea 110 kV Cardones - Magnetita ","H7","S/I",11.926,"F/I",11.932,"F/I",5.0310246520209859E-4]
[null,null,110,"Cardones  110 kV - H1 Línea 110 kV Cardones - Refugio ","H1","S/I",11.923,"F/I",11.929,"F/I",5.032290530906842E-4]
[null,"Carrascal ",110,"Carrascal  110 kV - H1 Línea 110 kV Carrascal - Renca/Brasil 1 ","H1",40,25.071999999999999,0.62680000000000002,25.167000000000002,0.62917500000000004,3.789087428206861E-3]
[null,null,110,"Carrascal  110 kV - H2 Línea 110 kV Carrascal - Renca/Brasil 2","H2",40,25.071999999999999,0.62680000000000002,25.167000000000002,0.62917500000000004,3.789087428206861E-3]
[null,"Casas Viejas ",110,"Casas Viejas  110 kV -  En Barra",null,null,3.6419999999999999,"N/A",3.6520000000000001,"N/A",2.7457440966502556E-3]
[null,"Castilla ",110,"Castilla  110 kV -  En Barra",null,null,4.3040000000000003,"N/A",4.3049999999999997,"N/A",2.3234200743481545E-4]
[null,"Castro ",110,"Castro  110 kV - H1 Línea 110 kV Castro - Gamboa","H1",40,5.391,0.13477500000000001,5.391,0.13477500000000001,0]
[null,null,110,"Castro  110 kV - H2 Línea 110 kV Castro - Chonchi ","H2",40,5.3879999999999999,0.13469999999999999,5.3879999999999999,0.13469999999999999,0]
[null,null,110,"Castro  110 kV - HT1 Transformador TR1 110/23 kV ","HT1",40,5.6529999999999996,0.14132499999999998,5.6529999999999996,0.14132499999999998,0]
[null,"Central Andes Generación ",110,"Central Andes Generación  110 kV - HT Transformador TR1 63 MVA 110/10,5 kV ","HT",31.5,10.809999999999999,0.34317460317460313,10.814,0.34330158730158733,3.7002775208152974E-4]
[null,"Central Cenizas ",110,"Central Cenizas  110 kV - HT Transformador TR01 35/30 MVA 110/11 kV ","HT",40,10.531000000000001,0.26327500000000004,10.535,0.26337500000000003,3.7983097521598701E-4]
[null,"Central Chacayes",110,"Central Chacayes 110 kV -  En Barra",null,null,11.196,"N/A",11.199,"N/A",2.6795284030011732E-4]
[null,"Central Chañares ",110,"Central Chañares  110 kV - HT1 Transformador TR1 72/50 MVA 110/33 kV ","HT1",31.5,6.4480000000000004,0.20469841269841271,6.4489999999999998,0.20473015873015873,1.5508684863514978E-4]
[null,"Central Colmito ",110,"Central Colmito  110 kV - H1 Línea 110 kV Colmito - Torquemada","H1",40,19.294,0.48235,20.876999999999999,0.52192499999999997,8.2046231989219356E-2]
[null,"Central Curillinque",154,"Central Curillinque 154 kV - AT Transformador Central Curillinque 154/13.8 kV","AT",40,4.9130000000000003,0.122825,4.9130000000000003,0.122825,0]
[null,"Central Diesel Enaex ",110,"Central Diesel Enaex  110 kV -  En Barra",null,null,7.5039999999999996,"N/A",7.5090000000000003,"N/A",6.6631130063976303E-4]
[null,"Central Diesel Tamaya ",110,"Central Diesel Tamaya  110 kV - H4 Línea 110 kV Central Diesel Tamaya - Central Tocopilla ","H4",40,11.044,0.27610000000000001,12.228,0.30569999999999997,0.10720753350235415]
[null,null,110,"Central Diesel Tamaya  110 kV - H2 Línea 110 kV Central Diesel Tamaya - Central Tocopilla ","H2",40,10.685,0.267125,11.827999999999999,0.29569999999999996,0.10697239120262039]
[null,null,110,"Central Diesel Tamaya  110 kV - H1 Línea 110 kV Central Diesel Tamaya - Salar","H1",40,13.358000000000001,0.33395000000000002,15.17,0.37924999999999998,0.13564904925887103]
[null,null,110,"Central Diesel Tamaya  110 kV - H3 Línea 110 kV Central Diesel Tamaya - A","H3",40,13.295999999999999,0.33239999999999997,15.092000000000001,0.37730000000000002,0.13507821901323716]
[null,null,110,"Central Diesel Tamaya  110 kV - HT1 Transformador TR1 50/33,3 MVA 110/11 kV ","HT1",40,11.994999999999999,0.299875,13.808999999999999,0.345225,0.15122967903293041]
[null,null,110,"Central Diesel Tamaya  110 kV - HT2 Transformador TR2 50/33,3 MVA 110/11 kV ","HT2",40,11.994999999999999,0.299875,13.808999999999999,0.345225,0.15122967903293041]
[null,null,110,"Central Diesel Tamaya  110 kV - HT3 Transformador TR3 50/33,3 MVA 110/11 kV ","HT3",40,11.994999999999999,0.299875,13.808999999999999,0.345225,0.15122967903293041]
[null,null,110,"Central Diesel Tamaya  110 kV - HT4 Transformador TR04 10,5/9,38/7,5 MVA 110/23 kV ","HT4",40,14.179,0.35447499999999998,15.962,0.39905000000000002,0.12574934762677195]
[null,"Central Emelda ",110,"Central Emelda  110 kV - H1 Transformador TR01 110/10.5 kV","H1",40,9.0779999999999994,0.22694999999999999,9.08,0.22700000000000001,2.203128442388927E-4]
[null,null,110,"Central Emelda  110 kV - H2 Transformador TR02 110/11.5 kV","H2",40,9.0779999999999994,0.22694999999999999,9.08,0.22700000000000001,2.203128442388927E-4]
[null,"Central Isla B1",154,"Central Isla B1 154 kV -  En Barra",null,null,5.88,"N/A",5.8810000000000002,"N/A",1.7006802721094115E-4]
[null,"Central Isla B2",154,"Central Isla B2 154 kV -  En Barra",null,null,5.88,"N/A",5.8810000000000002,"N/A",1.7006802721094115E-4]
[null,"Central Javiera",110,"Central Javiera 110 kV - H1 Línea 110 kV Central Javiera - Planta de Óxidos","H1",40,4.7240000000000002,0.11810000000000001,4.7240000000000002,0.11810000000000001,0]
[null,null,110,"Central Javiera 110 kV - H2 Línea 110 kV Central Javiera - Diego de Almagro","H2",40,3.8660000000000001,9.665E-2,3.867,9.6674999999999997E-2,2.5866528711844023E-4]
[null,null,110,"Central Javiera 110 kV - HT1 Transformador TR1 110/22 kV","HT1",40,3.8660000000000001,9.665E-2,3.867,9.6674999999999997E-2,2.5866528711844023E-4]
[null,"Central Laguna Verde ",110,"Central Laguna Verde  110 kV - H1 Línea 110kV La Pólvora - Central Laguna verde C1","H1",40,8.8190000000000008,0.22047500000000003,8.9030000000000005,0.22257500000000002,9.5248894432474907E-3]
[null,null,110,"Central Laguna Verde  110 kV - H2 Línea 110kV La Pólvora - Central Laguna Verde C2","H2",40,8.8190000000000008,0.22047500000000003,8.9030000000000005,0.22257500000000002,9.5248894432474907E-3]
[null,null,110,"Central Laguna Verde  110 kV - HT3 AutoTransformador ATR 60 MVA 110/66 kV","HT3",31.5,13.671000000000001,0.43400000000000005,13.825000000000001,0.43888888888888894,1.126472094214029E-2]
[null,null,110,"Central Laguna Verde  110 kV - HT4 Transformador TRTG 28,8 MVA 110/11.5 kV ","HT4","S/I",14.329000000000001,"F/I",14.493,"F/I",1.1445320678344594E-2]
[null,null,110,"Central Laguna Verde  110 kV - H5 Transformador TR1 30 MVA 110/12 kV  ","H5","S/I",13.877000000000001,"F/I",14.041,"F/I",1.1818116307559249E-2]
[null,"Central Las Piedras",110,"Central Las Piedras 110 kV -  En Barra",null,null,9.2940000000000005,"N/A",9.2959999999999994,"N/A",2.1519259737453104E-4]
[null,"Central Licán",110,"Central Licán 110 kV - H1 Línea 110 kV Central Lican - Mantilhue/Antillanca","H1",31.5,3.1469999999999998,9.9904761904761899E-2,3.1469999999999998,9.9904761904761899E-2,0]
[null,"Central Lomas Los Colorados ",110,"Central Lomas Los Colorados  110 kV - HT1 Transformador TR1 110/23 kV","HT1",25,4.5659999999999998,0.18264,4.5709999999999997,0.18284,1.0950503723171033E-3]
[null,"Central Los Hierros ",110,"Central Los Hierros  110 kV - H Línea 110 kV Central Los Hierros - Canal Melado ","H",40,2.581,6.4524999999999999E-2,2.5819999999999999,6.4549999999999996E-2,3.8744672607512201E-4]
[null,"Central Los Hierros II ",110,"Central Los Hierros II  110 kV - H Línea 110 kV Central Los Hierros II - Canal Melado ","H",40,3.7240000000000002,9.3100000000000002E-2,3.7240000000000002,9.3100000000000002E-2,0]
[null,"Central Los Quilos ",110,"Central Los Quilos  110 kV -  En Barra",null,null,11.33,"N/A",11.345000000000001,"N/A",1.3239187996470052E-3]
[null,"Central Maitenes ",110,"Central Maitenes  110 kV - T4 Transformador TR GE 110/12 kV ","T4","S/I",19.015000000000001,"F/I",19.024000000000001,"F/I",4.7331054430714385E-4]
[null,null,110,"Central Maitenes  110 kV - H1 Línea 110 kV Central Maitenes - Tap Off La Laja 1","H1",65,16.388000000000002,0.25212307692307695,16.395,0.2522307692307692,4.2714181108115062E-4]
[null,null,110,"Central Maitenes  110 kV - H2 Línea 110 kV Central Maitenes - Tap Off La Laja 2","H2",65,16.388000000000002,0.25212307692307695,16.395,0.2522307692307692,4.2714181108115062E-4]
[null,null,110,"Central Maitenes  110 kV - HX1 Línea 110 kV Alto Maipo - Maitenes","HX1","S/I",10.597,"N/P",10.604000000000001,"N/P",6.6056431065409553E-4]
[null,null,110,"Central Maitenes  110 kV - HX2 Línea 110kV Alfalfal - Central Maitenes","HX2","S/I",13.997,"N/P",14.003,"N/P",4.286632849896569E-4]
[null,"Central Mejillones ",110,"Central Mejillones  110 kV -  En Barra",null,null,7.5709999999999997,"N/A",7.5750000000000002,"N/A",5.2833179236566477E-4]
[null,"Central Nueva Renca",110,"Central Nueva Renca 110 kV - 52GV Transformador TR01 205MVA 110/15,75kV (UG Vapor)","52GV","S/I",50.858000000000004,"F/I",51.085000000000001,"F/I",4.4634079200911708E-3]
[null,"Central Olivos ",110,"Central Olivos  110 kV -  En Barra",null,null,9.3919999999999995,"N/A",9.4009999999999998,"N/A",9.5826235093700405E-4]
[null,"Central Parque Solar Los Loros",110,"Central Parque Solar Los Loros 110 kV - H1 Línea 110 kV Central PV Los Loros - Los Loros 1","H1",31.5,2.2850000000000001,7.2539682539682543E-2,2.2850000000000001,7.2539682539682543E-2,0]
[null,null,110,"Central Parque Solar Los Loros 110 kV - HT1 Transformador TR1 24/30 MVA 110/23 kV N°1","HT1",31.5,2.4359999999999999,7.7333333333333337E-2,2.4359999999999999,7.7333333333333337E-2,0]
[null,null,110,"Central Parque Solar Los Loros 110 kV - HT2 Transformador TR2 24/30 MVA 110/23 kV N°2","HT2",31.5,2.4359999999999999,7.7333333333333337E-2,2.4359999999999999,7.7333333333333337E-2,0]
[null,"Central Puntilla ",110,"Central Puntilla  110 kV -  En Barra",null,null,9.4589999999999996,"N/A",9.4629999999999992,"N/A",4.2287768263025261E-4]
[null,"Central PV El Salvador",110,"Central PV El Salvador 110 kV - H1 Línea 110kV Central PV El Salvador - Diego de Almagro/El Salvador","H1",40,5.3520000000000003,0.1338,5.3529999999999998,0.133825,1.8684603886387252E-4]
[null,"Central Queltehues ",110,"Central Queltehues  110 kV - H1 Línea 110 kV Central Queltehues - Tap Off La Laja 1","H1",31.5,4.0920000000000005,0.12990476190476191,4.093,0.12993650793650793,2.4437927663720568E-4]
[null,null,110,"Central Queltehues  110 kV - H2 Línea 110 kV Central Queltehues - Tap Off La Laja 2","H2",31.5,4.0920000000000005,0.12990476190476191,4.093,0.12993650793650793,2.4437927663720568E-4]
[null,null,110,"Central Queltehues  110 kV - HT1 Transformador TR1 28 MVA 110/12 kV ","HT1",31.5,6.6499999999999995,0.21111111111111108,6.6509999999999998,0.21114285714285713,1.5037593984967428E-4]
[null,null,110,"Central Queltehues  110 kV - HT2 Transformador TR2 28 MVA 110/12 kV ","HT2",40,6.6549999999999994,0.166375,6.6559999999999997,0.16639999999999999,1.5026296018036574E-4]
[null,null,110,"Central Queltehues  110 kV - HT3 Transformador TR3 28 MVA 110/12 kV ","HT3",31.5,6.665,0.2115873015873016,6.6660000000000004,0.21161904761904762,1.5003750937739443E-4]
[null,null,110,"Central Queltehues  110 kV - HT5 Transformador TR Aux 5 MVA 110/12 kV ","HT5",40,6.7519999999999998,0.16880000000000001,6.7530000000000001,0.168825,1.4810426540289308E-4]
[null,"Central Quintero",110,"Central Quintero 110 kV -  En Barra",null,null,21.134,"N/A",25.515999999999998,"N/A",0.20734361692060177]
[null,"Central Renca",110,"Central Renca 110 kV - H6 Acoplador de Barras BP1 - BP3","H6",40,51.777000000000001,1.2944249999999999,52.003999999999998,1.3001,4.3841860285454308E-3]
[null,"Central Río Huasco ",110,"Central Río Huasco  110 kV - HT1 Transformador T1 7 MVA 110/6.6 kV","HT1",40,2.6130000000000004,6.5325000000000008E-2,2.6130000000000004,6.5325000000000008E-2,0]
[null,"Central San Pedro Dalcahue \n",110,"Central San Pedro Dalcahue \n 110 kV - HT-1 Transformador N°2 75 MVA 110/30 kV ","HT-1","S/I",3.7590000000000003,"F/I",3.7590000000000003,"F/I",0]
[null,null,110,"Central San Pedro Dalcahue \n 110 kV - HT-2 Transformador N°2 40 MVA 110/30 kV ","HT-2",40,3.6360000000000001,9.0900000000000009E-2,3.6360000000000001,9.0900000000000009E-2,0]
[null,null,110,"Central San Pedro Dalcahue \n 110 kV - H1 Línea 110 kV Central San Pedro Dalcahue - Chiloé","H1","S/I",2.859,"F/I",2.859,"F/I",0]
[null,"Central Santiago Solar ",110,"Central Santiago Solar  110 kV -  H1 Línea 110 kV Central Santiago Solar - Las Vegas "," H1",40,8.3420000000000005,0.20855000000000001,8.3610000000000007,0.20902500000000002,2.27763126348599E-3]
[null,null,110,"Central Santiago Solar  110 kV -  H2 Línea 110 kV Central Santiago Solar - Tap Off Punta Peuco/Cerro Navia "," H2",40,8.2360000000000007,0.20590000000000003,8.2590000000000003,0.20647500000000002,2.7926177756191946E-3]
[null,null,110,"Central Santiago Solar  110 kV - HT1 Transformador TR1 110/30 kV 110 MVA ","HT1",40,12.163,0.30407499999999998,12.207000000000001,0.30517500000000003,3.6175285702540888E-3]
[null,"Central Tocopilla ",110,"Central Tocopilla  110 kV - HR Acoplador ","HR",25,12.674999999999999,0.50700000000000001,16.052,0.64207999999999998,0.26642998027613418]
[null,null,110,"Central Tocopilla  110 kV - HT1 Transformador TR1 28/23 MVA 110/11,5 kV ","HT1",14.6,12.456,0.85315068493150681,15.766,1.0798630136986302,0.26573538856775858]
[null,null,110,"Central Tocopilla  110 kV - HT2 Transformador TR2 28/23 MVA 110/11,5 kV ","HT2",14.6,12.456,0.85315068493150681,15.766,1.0798630136986302,0.26573538856775858]
[null,null,110,"Central Tocopilla  110 kV - H1 Línea 110 kV Central Tocopilla - A 1","H1",40,12.166,0.30415000000000003,15.417999999999999,0.38544999999999996,0.26730231793522924]
[null,null,110,"Central Tocopilla  110 kV - H2 Línea 110 kV Central Tocopilla - A 2","H2",40,12.148999999999999,0.30372499999999997,15.427,0.38567499999999999,0.26981644579800812]
[null,null,110,"Central Tocopilla  110 kV - H3 Línea 110 kV Central Tocopilla - Central Diesel Tamaya ","H3",40,11.067,0.276675,14.641,0.36602499999999999,0.32294208005782954]
[null,null,110,"Central Tocopilla  110 kV - H4 Línea 110 kV Central Tocopilla - Central Diesel Tamaya ","H4",40,10.979000000000001,0.27447500000000002,14.465,0.36162499999999997,0.31751525639857897]
[null,null,110,"Central Tocopilla  110 kV - HAT1 Autotransformador ATR1 100/100/30 MVA 220/110/13,8 kV ","HAT1",23,10.062999999999999,0.43752173913043474,13.281000000000001,0.57743478260869563,0.31978535228063221]
[null,null,110,"Central Tocopilla  110 kV - HAT2 Autotransformador ATR2 100/100/30 MVA 220/110/13,8 kV ","HAT2",25,10.062999999999999,0.40251999999999993,13.281000000000001,0.53124000000000005,0.31978535228063221]
[null,null,110,"Central Tocopilla  110 kV - HG12 Transformador TR12 92/75 MVA 110/13,8 kV ","HG12",40,12.444000000000001,0.31110000000000004,14.414999999999999,0.360375,0.15838958534233352]
[null,null,110,"Central Tocopilla  110 kV - HG13 Transformador TR13 92/75 MVA 110/13,8 kV ","HG13",40,12.444000000000001,0.31110000000000004,14.423,0.36057499999999998,0.15903246544519439]
[null,null,110,"Central Tocopilla  110 kV - HT105 Transformador TR105 15 MVA 115/5 kV ","HT105",20,12.674999999999999,0.63374999999999992,16.047999999999998,0.80239999999999989,0.26611439842209073]
[null,null,110,"Central Tocopilla  110 kV - HT141 Transformador TR141 30 MVA 115/5 kV ","HT141",25,12.669,0.50675999999999999,16.047999999999998,0.64191999999999994,0.26671402636356439]
[null,"S/E Yungay 154kV",154,"S/E Yungay 154kV 154 kV - ATG1 Transformador TR01 70MVA 154/11,5kV","ATG1",40,18.544999999999998,0.46362499999999995,18.587,0.464675,2.2647613912106551E-3]
[null,null,154,"S/E Yungay 154kV 154 kV - ATG2 Transformador TR02 70MVA 154/11,5kV","ATG2",40,18.544999999999998,0.46362499999999995,18.587,0.464675,2.2647613912106551E-3]
[null,null,154,"S/E Yungay 154kV 154 kV - ATG3 Transformador TR03 70MVA 154/11,5kV","ATG3",40,18.544999999999998,0.46362499999999995,18.587,0.464675,2.2647613912106551E-3]
[null,null,154,"S/E Yungay 154kV 154 kV - ATG4 Transformador TR04 70MVA 154/11,5kV","ATG4",40,18.998999999999999,0.47497499999999998,19.041,0.47602500000000003,2.2106426654035262E-3]
[null,"Centro ",110,"Centro  110 kV - H1 Línea 110 kV Centro - Esmeralda ","H1","S/I",8.7370000000000001,"F/I",8.7460000000000004,"F/I",1.0301018656289735E-3]
[null,null,110,"Centro  110 kV - HT1 Transformador TR1 110/13,8 kV ","HT1","S/I",8.7370000000000001,"F/I",8.7460000000000004,"F/I",1.0301018656289735E-3]
[null,null,110,"Centro  110 kV - HT1 Transformador TR2 110/23 kV ","HT1","S/I",8.7370000000000001,"F/I",8.7460000000000004,"F/I",1.0301018656289735E-3]
[null,"Cerrillos ",110,"Cerrillos  110 kV - H2 Línea 110 kV Cerrillos - Los Loros 1","H2",40,6.625,0.16562499999999999,6.6269999999999998,0.16567499999999999,3.0188679245279692E-4]
[null,null,110,"Cerrillos  110 kV - HX Línea 110 kV Cerrillos - Atacama Kozán","HX","S/I",3.5009999999999999,"N/P",3.5019999999999998,"N/P",2.8563267637814622E-4]
[null,null,110,"Cerrillos  110 kV - HT1 Transformador T1 30/25/20 MVA 110/24-13,8 kV ","HT1",31.5,6.625,0.21031746031746032,6.6269999999999998,0.21038095238095236,3.0188679245279692E-4]
[null,"Cerro Calera ",110,"Cerro Calera  110 kV - HT Transformador TR 30 MVA 110/60/12 kV ","HT",31.5,14.273,0.45311111111111108,14.495999999999999,0.46019047619047615,1.5623905275695297E-2]
[null,"Cerro Colorado ",110,"Cerro Colorado  110 kV - HL Línea 110 kV Cerro Colorado - Pozo Almonte ","HL","S/I",1.788,"F/I",1.82,"F/I",1.7897091722595095E-2]
[null,null,110,"Cerro Colorado  110 kV - HT1 Transformador TR1 46/30 MVA 110/12 kV ","HT1","S/I",1.788,"F/I",1.82,"F/I",1.7897091722595095E-2]
[null,null,110,"Cerro Colorado  110 kV - HT2 Transformador TR2 46/30 MVA 110/12 kV ","HT2","S/I",1.788,"F/I",1.82,"F/I",1.7897091722595095E-2]
[null,"Cerro Dragón ",110,"Cerro Dragón  110 kV - HT1 Transformador Trafo1 110/13.8 kV 33/25 MVA ","HT1","S/I",3.6,"F/I",3.73,"F/I",3.611111111111108E-2]
[null,"Cerro Navia",110,"Cerro Navia 110 kV - HT3 AutoTransformador ATR03 399 MVA 220/110/13,8 kV ","HT3",40,53.652999999999999,1.3413249999999999,53.911000000000008,1.3477750000000002,4.8086779863196795E-3]
[null,null,110,"Cerro Navia 110 kV - AT2 AutoTransformador ATR02 400 MVA 220/110/13,2 kV ","AT2",40,53.652999999999999,1.3413249999999999,53.911000000000008,1.3477750000000002,4.8086779863196795E-3]
[null,null,110,"Cerro Navia 110 kV - HT5 AutoTransformador ATR5 400 MVA 220/110/13,2 kV ","HT5",63,55.528000000000006,0.88139682539682551,55.752999999999993,0.88496825396825385,4.0520097968590116E-3]
[null,"Cerro Navia (Enel)",110,"Cerro Navia (Enel) 110 kV - H2 Línea 110 kV Cerro Navia - Renca 2","H2",40,59.665000000000006,1.4916250000000002,59.935999999999993,1.4983999999999997,4.5420263135839533E-3]
[null,null,110,"Cerro Navia (Enel) 110 kV - H11 Línea 110 kV Cerro Navia - Lo Aguirre 1","H11",50,66.50800000000001,1.3301600000000002,66.786000000000001,1.33572,4.1799482768988929E-3]
[null,null,110,"Cerro Navia (Enel) 110 kV - H10 Línea 110 kV Cerro Navia - San Pablo","H10",50,66.510000000000005,1.3302,66.787999999999997,1.3357599999999998,4.1798225830700884E-3]
[null,null,110,"Cerro Navia (Enel) 110 kV - H3 Línea 110 kV Cerro Navia - TO Los Libertadores C1","H3",40,65.245000000000005,1.6311250000000002,65.503999999999991,1.6375999999999997,3.9696528469612405E-3]
[null,null,110,"Cerro Navia (Enel) 110 kV - H4 Línea 110 kV Cerro Navia - TO Los Libertadores C2","H4",40,65.245000000000005,1.6311250000000002,65.503999999999991,1.6375999999999997,3.9696528469612405E-3]
[null,null,110,"Cerro Navia (Enel) 110 kV - H5 Línea 110 kV Cerro Navia - San Cristóbal 1","H5",50,63.878,1.27756,64.140999999999991,1.2828199999999998,4.117223457215176E-3]
[null,null,110,"Cerro Navia (Enel) 110 kV - H6 Línea 110 kV Cerro Navia - San Cristóbal 2","H6",50,63.878,1.27756,64.140999999999991,1.2828199999999998,4.117223457215176E-3]
[null,null,110,"Cerro Navia (Enel) 110 kV - H7 Línea 110 kV Cerro Navia - Chena 1 ","H7",40,62.782000000000004,1.56955,63.048999999999992,1.5762249999999998,4.2528113153449841E-3]
[null,null,110,"Cerro Navia (Enel) 110 kV - H8 Línea 110 kV Cerro Navia - Chena 2 ","H8",40,62.782000000000004,1.56955,63.048999999999992,1.5762249999999998,4.2528113153449841E-3]
[null,null,110,"Cerro Navia (Enel) 110 kV - H1 Línea 110 kV Cerro Navia - Renca 1","H1",40,59.665000000000006,1.4916250000000002,59.935999999999993,1.4983999999999997,4.5420263135839533E-3]
[null,"Chacabuco ",110,"Chacabuco  110 kV -  H1 Línea 110 kV Chacabuco - San Cristóbal/Cerro Navia 1 "," H1",40,13.904999999999999,0.34762499999999996,13.943,0.34857499999999997,2.7328299172959553E-3]
[null,null,110,"Chacabuco  110 kV -  H2 Línea 110 kV Chacabuco - San Cristóbal/Cerro Navia 2"," H2",40,13.904999999999999,0.34762499999999996,13.943,0.34857499999999997,2.7328299172959553E-3]
[null,null,110,"Chacabuco  110 kV - HT6 Transformador TR06 25 MVA 110/23,5 kV ","HT6",40,27.81,0.69524999999999992,27.885000000000002,0.69712499999999999,2.696871628910566E-3]
[null,null,110,"Chacabuco  110 kV - AT2 Transformador TR02 37,5 MVA 110/23,5 kV ","AT2",40,27.81,0.69524999999999992,27.885000000000002,0.69712499999999999,2.696871628910566E-3]
[null,null,110,"Chacabuco  110 kV - AT4 Transformador TR04 22,4 MVA 110/12,5 kV ","AT4",40,27.81,0.69524999999999992,27.885000000000002,0.69712499999999999,2.696871628910566E-3]
[null,null,110,"Chacabuco  110 kV - HT8 Transformador TR08 50 MVA 110/23,5 kV ","HT8",25,27.81,1.1124000000000001,27.885000000000002,1.1154000000000002,2.696871628910566E-3]
[null,null,110,"Chacabuco  110 kV - HT7 Transformador TR07110/23,5 kV ","HT7",25,27.81,1.1124000000000001,27.885000000000002,1.1154000000000002,2.696871628910566E-3]
[null,"Chacaya ",110,"Chacaya  110 kV - HT4 Transformador TR4 10 MVA 110/33 kV ","HT4","S/I",4.6639999999999997,"F/I",4.6669999999999998,"F/I",6.4322469982849785E-4]
[null,null,110,"Chacaya  110 kV - HT3 Transformador TR3 220/110/13,8 kV 80/100 MVA ","HT3",31.5,4.3289999999999997,0.13742857142857143,4.3310000000000004,0.1374920634920635,4.6200046200061632E-4]
[null,null,110,"Chacaya  110 kV - H3 Línea 110 kV Chacaya - GNL Mejillones ","H3",31.5,4.6639999999999997,0.14806349206349206,4.6669999999999998,0.14815873015873016,6.4322469982849785E-4]
[null,null,110,"Chacaya  110 kV - H2 Línea 110 kV Chacaya - Muelle ","H2",40,4.327,0.10817499999999999,4.33,0.10825,6.9332100762655737E-4]
[null,"Chamy ",110,"Chamy  110 kV - H16 Línea 110 kV Chamy - Chuquicamata ","H16","S/I",5.95,"F/I",6.0549999999999997,"F/I",1.7647058823529335E-2]
[null,null,110,"Chamy  110 kV - HT1 Transformador TR01 37/33/25 MVA 100/13,8 kV ","HT1","S/I",5.95,"F/I",6.0549999999999997,"F/I",1.7647058823529335E-2]
[null,null,110,"Chamy  110 kV - Acoplador Barras Acoplador ","Acoplador Barras","S/I",5.95,"F/I",6.0549999999999997,"F/I",1.7647058823529335E-2]
[null,"Charrua",154,"Charrua 154 kV - AT1 Transformador ATR Charrúa 220/154 kV N°1","AT1",40,12.36,0.309,12.388,0.30969999999999998,2.2653721682848278E-3]
[null,null,154,"Charrua 154 kV - A2 Línea 154 kV Charrua - Pueblo Seco","A2",31.5,23.035,0.73126984126984129,23.094999999999999,0.73317460317460315,2.6047319296721824E-3]
[null,null,154,"Charrua 154 kV - ACE1 Banco Condensador Charrua 154 kV 1","ACE1",40,24.149000000000001,0.60372500000000007,24.210999999999999,0.60527500000000001,2.5673940949934825E-3]
[null,null,154,"Charrua 154 kV - A4 Línea 154 kV Charrúa - Yungay (Ex Campanario)","A4",40,19.396000000000001,0.4849,19.454999999999998,0.48637499999999995,3.041864301917792E-3]
[null,null,154,"Charrua 154 kV - A6 Línea 154 kV Charrúa - Chillán","A6",40,23.611000000000001,0.59027499999999999,23.672999999999998,0.59182499999999993,2.6258947100926524E-3]
[null,null,154,"Charrua 154 kV - A7 Transformador Charrúa 154/69/13.8 kV N°2","A7",31.5,22.752000000000002,0.72228571428571431,22.811999999999998,0.72419047619047616,2.6371308016875511E-3]
[null,null,154,"Charrua 154 kV - A8 Línea 154kV Trupán - Charrúa","A8",31.5,23.144000000000002,0.73473015873015879,23.206,0.73669841269841263,2.6788800553058075E-3]
[null,null,154,"Charrua 154 kV - A9 Línea 154 kV Charrúa - Los Angeles","A9",40,22.941000000000003,0.57352500000000006,23.000999999999998,0.5750249999999999,2.6154047338823572E-3]
[null,null,154,"Charrua 154 kV - A10 Línea 154 kV Charrúa - Concepción 1","A10",40,22.28,0.55700000000000005,22.315999999999999,0.55789999999999995,1.6157989228006199E-3]
[null,"Chena ",110,"Chena  110 kV - A6 Línea 110 kV Chena - Ochagavía 1 ","A6",40,46.396999999999998,1.1599249999999999,46.542000000000002,1.1635500000000001,3.1252020604781157E-3]
[null,null,110,"Chena  110 kV - A5 Línea 110 kV Chena - Ochagavía 2","A5",40,46.396999999999998,1.1599249999999999,46.542000000000002,1.1635500000000001,3.1252020604781157E-3]
[null,null,110,"Chena  110 kV -  H3 Línea 110 kV Chena - Cerro Navia 1"," H3",40,49.483999999999995,1.2370999999999999,49.628999999999998,1.2407249999999999,2.9302400776009042E-3]
[null,null,110,"Chena  110 kV -  H4 Línea 110 kV Chena - Cerro Navia 2"," H4",40,49.483999999999995,1.2370999999999999,49.628999999999998,1.2407249999999999,2.9302400776009042E-3]
[null,null,110,"Chena  110 kV - HT1 Transformador TR01 400 MVA 220/110/13,8 kV ","HT1",50,43.579000000000001,0.87158000000000002,43.760000000000005,0.87520000000000009,4.1533766263568347E-3]
[null,null,110,"Chena  110 kV - CCE1A Banco de Condensadores 1","CCE1A",50,54.664000000000001,1.09328,54.865000000000002,1.0972999999999999,3.677008634567549E-3]
[null,null,110,"Chena  110 kV - AT2 Transformador TR02 400 MVA 220/110/13,8 kV ","AT2",50,43.578000000000003,0.87156000000000011,43.759,0.87517999999999996,4.1534719353801776E-3]
[null,"Chillán",154,"Chillán 154 kV - AT3 Transformador Chillán TR3 75MVA 154/66 kV ","AT3",40,3.0619999999999998,7.6549999999999993E-2,3.0629999999999997,7.657499999999999E-2,3.265839320705062E-4]
[null,"Chiloé",110,"Chiloé 110 kV - HT1 Transformador Chiloe 90 MVA 220/110/23 kV","HT1",45,3.1619999999999999,7.0266666666666672E-2,3.1619999999999999,7.0266666666666672E-2,0]
[null,null,110,"Chiloé 110 kV - H1 Línea 110 kV Chiloe - Ancud 1","H1",45,5.5010000000000003,0.12224444444444445,5.5010000000000003,0.12224444444444445,0]
[null,null,110,"Chiloé 110 kV - H2 Línea 110 kV Chiloe - Pid Pid/Dalcahue 1","H2",45,4.8260000000000005,0.10724444444444446,4.8260000000000005,0.10724444444444446,0]
[null,null,110,"Chiloé 110 kV - H3 Línea 110 kV Chiloe - Degañ 1","H3",45,5.6559999999999997,0.12568888888888888,5.6559999999999997,0.12568888888888888,0]
[null,null,110,"Chiloé 110 kV - H4 Línea 110 kV Chiloe - San Pedro 1","H4",40,5.2680000000000007,0.13170000000000001,5.2680000000000007,0.13170000000000001,0]
[null,null,110,"Chiloé 110 kV - HR1 Acoplador ","HR1",45,6.0880000000000001,0.1352888888888889,6.0880000000000001,0.1352888888888889,0]
[null,"Chirre",110,"Chirre 110 kV -  En Barra",null,null,4.702,"N/A",4.702,"N/A",0]
[null,"Choapa ",110,"Choapa  110 kV - H4 Línea 110 kV Choapa - Illapel ","H4",40,8.4689999999999994,0.211725,8.4779999999999998,0.21195,1.062699256110561E-3]
[null,null,110,"Choapa  110 kV - H5 Línea 110 kV Choapa - Central Olivos ","H5",40,7.17,0.17924999999999999,7.1789999999999994,0.179475,1.2552301255229362E-3]
[null,null,110,"Choapa  110 kV - H1 Línea 110 kV Choapa - Quereo","H1",40,9.4529999999999994,0.23632499999999998,9.4629999999999992,0.23657499999999998,1.0578652279699342E-3]
[null,null,110,"Choapa  110 kV - HT AutoTransformador ATR1 75/60 MVA 220/115/23 kV ","HT",40,6.8469999999999995,0.17117499999999999,6.8539999999999992,0.17134999999999997,1.0223455527967977E-3]
[null,null,110,"Choapa  110 kV - HTX AutoTransformador ATR2 75/60 MVA 220/115/23 kV ","HTX","S/I",6.8469999999999995,"N/P",6.8539999999999992,"N/P",1.0223455527967977E-3]
[null,null,110,"Choapa  110 kV - H3 Línea 110 kV Choapa - Quinquimo ","H3",40,8.64,0.21600000000000003,8.6460000000000008,0.21615000000000001,6.9444444444447071E-4]
[null,"Chonchi",110,"Chonchi 110 kV - HT1 Transformador TR1 30-24 MVA 115.69/24 kV ","HT1",40,4.4690000000000003,0.111725,4.4690000000000003,0.111725,0]
[null,null,110,"Chonchi 110 kV - HX Línea 220kV (energizada en 110kV) Gamboa - Chonchi","HX","S/I",3.2519999999999998,"N/P",3.2519999999999998,"N/P",0]
[null,null,110,"Chonchi 110 kV - H2 Línea 110 kV Chonchi - Quellon","H2",40,4.2039999999999997,0.1051,4.2039999999999997,0.1051,0]
[null,"Chuquicamata",100,"Chuquicamata 100 kV - HATR1 Transformador ATR1 220/110/13.8","HATR1",25,8.6739999999999995,0.34695999999999999,8.9720000000000013,0.35888000000000003,3.4355545307816676E-2]
[null,null,100,"Chuquicamata 100 kV - HT2 Transformador ATR2 220/110/13.8","HT2",25,8.6739999999999995,0.34695999999999999,8.9720000000000013,0.35888000000000003,3.4355545307816676E-2]
[null,null,100,"Chuquicamata 100 kV - HR Acoplador","HR","S/I",12.411,"F/I",12.768000000000001,"F/I",2.8764805414551696E-2]
[null,null,100,"Chuquicamata 100 kV - H16 Línea 110 kV Chuquicamata - Chamy 1","H16",25,12.411,0.49643999999999999,12.768000000000001,0.51072000000000006,2.8764805414551696E-2]
[null,null,100,"Chuquicamata 100 kV - H12  Línea 110 kV Chuquicamata - K1 1","H12 ",25,11.879999999999999,0.47519999999999996,12.224,0.48896000000000001,2.8956228956229058E-2]
[null,null,100,"Chuquicamata 100 kV - H10 Línea 110 kV Chuquicamata - 10 1","H10",25,11.721,0.46883999999999998,12.06,0.4824,2.8922446890197118E-2]
[null,null,100,"Chuquicamata 100 kV - H11 Línea 110 kV Chuquicamata - 10A 1","H11",25,11.783999999999999,0.47135999999999995,12.125,0.48499999999999999,2.8937542430414215E-2]
[null,null,100,"Chuquicamata 100 kV - H13 Línea 110 kV Chuquicamata - KM6 1","H13",25,11.112,0.44447999999999999,11.436,0.45744000000000001,2.9157667386609055E-2]
[null,null,100,"Chuquicamata 100 kV - H14 Línea 110 kV Chuquicamata - A 1","H14",25,11.526999999999999,0.46107999999999999,11.804,0.47216000000000002,2.4030537000086845E-2]
[null,null,100,"Chuquicamata 100 kV - H15 Línea 110 kV Chuquicamata - A 2","H15",25,11.488999999999999,0.45955999999999997,11.765000000000001,0.47060000000000002,2.4022978501175175E-2]
[null,"Chuschampis ",110,"Chuschampis  110 kV -  En Barra",null,null,3.7879999999999998,"N/A",3.7879999999999998,"N/A",0]
[null,"Cipreses",154,"Cipreses 154 kV - A1 Línea 154 kV Cipreses - Itahue1/Curillinque","A1",40,3.9510000000000005,9.8775000000000016E-2,3.95,9.8750000000000004E-2,-2.5310048089099816E-4]
[null,null,154,"Cipreses 154 kV - A2 Línea 154 kV Cipreses - Itahue 2","A2",40,4.8770000000000007,0.12192500000000002,4.8760000000000003,0.12190000000000001,-2.0504408447823125E-4]
[null,null,154,"Cipreses 154 kV - A3 Línea 154 kV Cipreses - Central Isla 1","A3",40,5.8930000000000007,0.14732500000000001,5.8930000000000007,0.14732500000000001,0]
[null,null,154,"Cipreses 154 kV - A4 Línea 154 kV Cipreses - Central Isla 2","A4",40,5.8930000000000007,0.14732500000000001,5.8930000000000007,0.14732500000000001,0]
[null,null,154,"Cipreses 154 kV - AT1 Transformador Cipreses TR01 32MVA 154/13,8 kV U1","AT1",10,5.8559999999999999,0.58560000000000001,5.8569999999999993,0.58569999999999989,1.7076502732230972E-4]
[null,null,154,"Cipreses 154 kV - AT2 Transformador Cipreses TR02 32MVA154/13.8 kV U2","AT2",40,5.915,0.14787500000000001,5.9159999999999995,0.14789999999999998,1.6906170752315229E-4]
[null,null,154,"Cipreses 154 kV - AT3 Transformador Cipreses TR03 161/13.8/6.9 kV U3","AT3",40,5.915,0.14787500000000001,5.9159999999999995,0.14789999999999998,1.6906170752315229E-4]
[null,"Club Hípico ",110,"Club Hípico  110 kV - H1 Línea 110 kV Club Hípico - Ochagavia/Florida 1 ","H1",31.5,21.959000000000003,0.69711111111111124,22.029,0.69933333333333336,3.1877590054190412E-3]
[null,null,110,"Club Hípico  110 kV - H2 Línea 110 kV Club Hípico - Ochagavia/Florida 2","H2",31.5,21.959000000000003,0.69711111111111124,22.029,0.69933333333333336,3.1877590054190412E-3]
[null,null,110,"Club Hípico  110 kV - HT3 Transformador TR3 25 MVA 110/12,5 kV ","HT3",31.5,43.917000000000002,1.3941904761904762,44.057000000000002,1.3986349206349207,3.1878315914110836E-3]
[null,"Codelco Ventanas 1 ",110,"Codelco Ventanas 1  110 kV - A12 Transformador TR1 ","A12","S/I",19.71,"F/I",22.469000000000001,"F/I",0.1399797057331304]
[null,null,110,"Codelco Ventanas 1  110 kV - A22 Transformador TR2 ","A22","S/I",19.62,"F/I",22.367000000000001,"F/I",0.14001019367991843]
[null,"Codelco Ventanas 2 ",110,"Codelco Ventanas 2  110 kV - HT3 Transformador TR3","HT3",31.5,17.617999999999999,0.5593015873015873,19.786999999999999,0.62815873015873014,0.12311272562152348]
[null,null,110,"Codelco Ventanas 2  110 kV - HT4 Transformador TR4","HT4",31.5,17.542999999999999,0.55692063492063493,19.704000000000001,0.62552380952380959,0.12318303596876255]
[null,null,110,"Codelco Ventanas 2  110 kV - HT5 Transformador TR5","HT5",31.5,17.483999999999998,0.55504761904761901,19.637,0.62339682539682539,0.12314115762983313]
[null,"Colaco ",110,"Colaco  110 kV - HT1 Transformador TR1 110/24 kV 16 MVA ","HT1",40,4.4249999999999998,0.110625,4.4249999999999998,0.110625,0]
[null,null,110,"Colaco  110 kV - H1 Línea 110 kV Colaco - Pargua ","H1",25,2.335,9.3399999999999997E-2,2.335,9.3399999999999997E-2,0]
[null,"Colón ",110,"Colón  110 kV -  H1 Línea 110 kV Colón - Minero 1 "," H1",31.5,10.153999999999998,0.32234920634920627,10.159000000000001,0.32250793650793652,4.9241678156416774E-4]
[null,null,110,"Colón  110 kV -  H2 Línea 110 kV Colón - Minero 2"," H2",22,10.153999999999998,0.46154545454545448,10.159000000000001,0.46177272727272728,4.9241678156416774E-4]
[null,null,110,"Colón  110 kV - HT1 Transformador TR1 20 MVA 110/13,8/4,16 kV ","HT1",24.2,20.306999999999999,0.83913223140495863,20.317,0.83954545454545459,4.9244103018671211E-4]
[null,null,110,"Colón  110 kV - HT2 Transformador TR2 20 MVA 110/13,8/4,16 kV ","HT2",24.2,20.306999999999999,0.83913223140495863,20.317,0.83954545454545459,4.9244103018671211E-4]
[null,null,110,"Colón  110 kV - HT3 Transformador TR3 20 MVA 110/13,8/4,16 kV ","HT3",24.2,20.306999999999999,0.83913223140495863,20.317,0.83954545454545459,4.9244103018671211E-4]
[null,null,110,"Colón  110 kV - HT4 Transformador TR4 20 MVA 110/13,8/4,16 kV ","HT4",52.73,20.306999999999999,0.38511283899108667,20.317,0.38530248435425757,4.9244103018671211E-4]
[null,"Concepción",154,"Concepción 154 kV - AT1 Transformador Concepción TR1 30MVA 154/66 kV N°1","AT1",11,20.59,1.8718181818181818,21.082999999999998,1.9166363636363635,2.3943661971830916E-2]
[null,null,154,"Concepción 154 kV - AT2 Transformador Concepción TR2 56MVA 154/66 kV N°2","AT2",40,20.942,0.52354999999999996,21.439,0.53597499999999998,2.3732212778149169E-2]
[null,null,154,"Concepción 154 kV - AT3 Transformador Concepción TR3 56MVA154/66 kV N°3","AT3",40,20.810000000000002,0.5202500000000001,21.305,0.53262500000000002,2.3786641037962391E-2]
[null,null,154,"Concepción 154 kV - AT7 Transformador Concepción ATR7 261MVA 225/161/13.2 kV N°7","AT7",40,12.213000000000001,0.30532500000000001,12.681000000000001,0.317025,3.8319823139277814E-2]
[null,null,154,"Concepción 154 kV - A3 Línea 154 kV Concepción - San Vicente 1","A3",40,18.206000000000003,0.45515000000000005,18.555999999999997,0.46389999999999992,1.9224431506096575E-2]
[null,null,154,"Concepción 154 kV - A4 Línea 154 kV Concepción - Charrúa","A4",40,19.087000000000003,0.47717500000000007,19.597999999999999,0.48995,2.6772148582804821E-2]
[null,null,154,"Concepción 154 kV - A6 Línea 154 kV Concepción - San Vicente 2","A6",40,18.206000000000003,0.45515000000000005,18.555999999999997,0.46389999999999992,1.9224431506096575E-2]
[null,null,154,"Concepción 154 kV - A7 Línea 154 kV Concepción - Alonso de Ribera","A7",40,20.203000000000003,0.50507500000000005,20.681999999999999,0.51705000000000001,2.3709350096520102E-2]
[null,"Concon ",110,"Concon  110 kV - H3 Línea 110 kV Concon - Tap Off Achupallas/Reñaca ","H3",40,19.400000000000002,0.48500000000000004,21.146999999999998,0.52867500000000001,9.0051546391752377E-2]
[null,null,110,"Concon  110 kV - HT1 Transformador TR1 25 MVA 110/12 kV ","HT1",31.5,22.057000000000002,0.7002222222222223,23.876999999999999,0.75800000000000001,8.2513487781656458E-2]
[null,null,110,"Concon  110 kV - HT2 Transformador TR2 25 MVA 110/12 kV  ","HT2",31.5,22.057000000000002,0.7002222222222223,23.876999999999999,0.75800000000000001,8.2513487781656458E-2]
[null,null,110,"Concon  110 kV - H4 Línea 110 kV Concon - Bosquemar ","H4",40,21.019000000000002,0.52547500000000003,22.81,0.57024999999999992,8.5208620771682606E-2]
[null,"Cóndores ",110,"Cóndores  110 kV - HT1 Transformador TR01 195/195/39 MVA 220/115/13,8 kV ","HT1","S/I",4.827,"F/I",5.0629999999999997,"F/I",4.8891651129065627E-2]
[null,null,110,"Cóndores  110 kV - H1 Línea 110 kV Cóndores - Cerro Dragón/Alto Hospicio ","H1","S/I",4.8259999999999996,"F/I",5.0629999999999997,"F/I",4.910899295482804E-2]
[null,null,110,"Cóndores  110 kV - H3 Línea 110 kV Cóndores - Pacífico ","H3","S/I",4.8959999999999999,"F/I",5.1319999999999997,"F/I",4.8202614379084921E-2]
[null,null,110,"Cóndores  110 kV - H2 Línea 110 kV Cóndores - Palafitos ","H2","S/I",4.8959999999999999,"F/I",5.1319999999999997,"F/I",4.8202614379084921E-2]
[null,"Convento Viejo",154,"Convento Viejo 154 kV - A3 Transformador Convento Viejo TR01 20MVA 154/66 kV ","A3",40,11.164999999999999,0.27912499999999996,11.17,0.27925,4.4782803403500062E-4]
[null,null,154,"Convento Viejo 154 kV - A1 Línea 154 kV Convento Viejo - Itahue","A1",40,6.3150000000000004,0.15787500000000002,6.3179999999999996,0.15794999999999998,4.7505938242268017E-4]
[null,null,154,"Convento Viejo 154 kV - A2 Línea 154 kV Convento Viejo - Tinguiririca","A2",40,6.5019999999999989,0.16254999999999997,6.5049999999999999,0.16262499999999999,4.6139649338680443E-4]
[null,"Copayapu ",110,"Copayapu  110 kV - H1 Línea 110 kV Copayapu - Galleguillos ","H1",40,11.436,0.28589999999999999,11.441000000000001,0.28602500000000003,4.3721580972374798E-4]
[null,null,110,"Copayapu  110 kV - HX1 Línea 110 kV Copayapu - Copiapó","HX1","S/I",11.436999999999999,"N/P",11.442,"N/P",4.3717758153368733E-4]
[null,null,110,"Copayapu  110 kV - HX2 Línea 110 kV Copayapu - Cardones C2","HX2","S/I",7.9819999999999993,"N/P",7.9849999999999994,"N/P",3.7584565271863118E-4]
[null,null,110,"Copayapu  110 kV - H2 Línea 110 kV Copayapu - Cardones ","H2",40,5.7640000000000002,0.14410000000000001,5.766,0.14415,3.4698126301175913E-4]
[null,null,110,"Copayapu  110 kV - H3 Línea 110 kV Copayapu - Tierra Amarilla ","H3",40,10.039999999999999,0.251,10.044,0.25109999999999999,3.9840637450212513E-4]
[null,null,110,"Copayapu  110 kV - H4 Línea 110 kV Copayapu - Cerrillos ","H4",40,10.628,0.26569999999999999,10.632,0.26579999999999998,3.7636432066235975E-4]
[null,"Copiapó ",110,"Copiapó  110 kV - H1 Línea 110 kV Copayapu - Copiapó","H1",31.5,4.3159999999999998,0.13701587301587301,4.3170000000000002,0.13704761904761906,2.3169601482862234E-4]
[null,null,110,"Copiapó  110 kV - H2 Línea 110 kV Copiapó - Hernán Fuentes ","H2",28.2,4.298,0.1524113475177305,4.3000000000000007,0.15248226950354613,4.6533271288987153E-4]
[null,null,110,"Copiapó  110 kV - HT3 Transformador T3 24/20/16 MVA 110/24-13,8 kV ","HT3",28.2,5.8019999999999996,0.20574468085106382,5.8040000000000003,0.20581560283687944,3.4470872113075976E-4]
[null,null,110,"Copiapó  110 kV - HT4 Transformador T4 25/20/16 MVA 110/24-13,8 kV ","HT4",31.5,5.8019999999999996,0.18419047619047618,5.8040000000000003,0.18425396825396825,3.4470872113075976E-4]
[null,"Copihues ",110,"Copihues  110 kV - H1 Línea 110 kV Copihues - Aihuapi ","H1",40,2.254,5.6349999999999997E-2,2.254,5.6349999999999997E-2,0]
[null,null,110,"Copihues  110 kV - HT1 Transformador TR1 30 MVA 115/69/13,8 kV ","HT1",40,2.609,6.5225000000000005E-2,2.609,6.5225000000000005E-2,0]
[null,null,110,"Copihues  110 kV - H2 Línea 110 kV Copihues - Central Correntoso","H2","S/I",2.8879999999999999,"F/I",2.8879999999999999,"F/I",0]
[null,"Cordillera ",110,"Cordillera  110 kV - H1 Línea 110 kV Cordillera - Minero 1 ","H1",32.954545454545503,9.0379999999999985,0.27425655172413749,9.0419999999999998,0.27437793103448233,4.4257579110437446E-4]
[null,null,110,"Cordillera  110 kV - H2 Línea 110 kV Cordillera - Minero 2","H2",32.954545454545503,9.0379999999999985,0.27425655172413749,9.0419999999999998,0.27437793103448233,4.4257579110437446E-4]
[null,null,110,"Cordillera  110 kV - HT39 Transformador TR39 110/33 kV","HT39",32.954545454544999,18.074999999999999,0.54848275862069718,18.082999999999998,0.54872551724138685,4.4260027662512414E-4]
[null,null,110,"Cordillera  110 kV - HT40 Transformador TR40 110/33 kV","HT40",32.954545454545503,18.074999999999999,0.54848275862068885,18.082999999999998,0.54872551724137841,4.4260027662512414E-4]
[null,null,110,"Cordillera  110 kV - HT41 Transformador TR41 110/33 kV","HT41",32.954545454545503,18.074999999999999,0.54848275862068885,18.082999999999998,0.54872551724137841,4.4260027662512414E-4]
[null,null,110,"Cordillera  110 kV - HT42 Transformador TR42 110/33 kV","HT42",32.954545454545503,18.074999999999999,0.54848275862068885,18.082999999999998,0.54872551724137841,4.4260027662512414E-4]
[null,null,110,"Cordillera  110 kV - HT43 Transformador TR43 110/13,8 kV","HT43",52.727272727272698,18.074999999999999,0.3428017241379312,18.082999999999998,0.34295344827586222,4.4260027662512414E-4]
[null,null,110,"Cordillera  110 kV - HT44 Transformador TR44 110/13,8 kV","HT44",52.727272727272698,18.074999999999999,0.3428017241379312,18.082999999999998,0.34295344827586222,4.4260027662512414E-4]
[null,null,110,"Cordillera  110 kV - HT45 Transformador TR46 110/33 kV","HT45",32.954545454545503,18.074999999999999,0.54848275862068885,18.082999999999998,0.54872551724137841,4.4260027662512414E-4]
[null,null,110,"Cordillera  110 kV - HT46 Transformador TR45 110/33 kV","HT46",32.954545454545503,18.074999999999999,0.54848275862068885,18.082999999999998,0.54872551724137841,4.4260027662512414E-4]
[null,null,110,"Cordillera  110 kV - HCE1 Condensador N°1","HCE1",40,18.074999999999999,0.45187499999999997,18.082999999999998,0.45207499999999995,4.4260027662512414E-4]
[null,"Coronel",154,"Coronel 154 kV - AT3-4 Transformador Coronel TR4 60/60/20MVA 154/66/13.8 kV ","AT3-4","S/I",13.305999999999999,"F/I",15.090999999999999,"F/I",0.13415000751540659]
[null,null,154,"Coronel 154 kV - AT5 Transformador Coronel TR5 40/56MVA 154/69/13.2 kV ","AT5","S/I",13.202999999999999,"F/I",14.952999999999999,"F/I",0.13254563356812846]
[null,null,154,"Coronel 154 kV - AT6 Transformador Coronel TR6 40/56MVA154/69/13.2 kV","AT6",31.5,13.309999999999999,0.42253968253968249,15.058999999999999,0.47806349206349202,0.13140495867768601]
[null,null,154,"Coronel 154 kV - A1 Línea 154 kV Coronel - Bocamina","A1","S/I",10.773,"F/I",12.455,"F/I",0.15613106841177021]
[null,"Costanera ",110,"Costanera  110 kV -  En Barra",null,null,9.2539999999999996,"N/A",9.2569999999999997,"N/A",3.241841365895952E-4]
[null,"Cristalerías",110,"Cristalerías 110 kV - HT1  Línea 110 kV Cristalerías - Las Vegas ","HT1 ",40,12.717000000000001,0.31792500000000001,12.803000000000001,0.320075,6.7626012424314144E-3]
[null,"Cunco ",110,"Cunco  110 kV -  H1 Línea 110 kV Cunco - Río Toltén "," H1",31.5,1.651,5.2412698412698411E-2,1.651,5.2412698412698411E-2,0]
[null,null,110,"Cunco  110 kV -  H2 Línea 110 kV Cunco - Melipeuco "," H2",31.5,1.65,5.2380952380952375E-2,1.65,5.2380952380952375E-2,0]
[null,null,110,"Cunco  110 kV - HT1 Transformador TR1 16 MVA 110/23 kV","HT1",31.5,1.99,6.3174603174603175E-2,1.99,6.3174603174603175E-2,0]
[null,"Dalcahue ",110,"Dalcahue  110 kV -  H1 Línea 110 kV Dalcahue - Chiloe "," H1",40,2.4460000000000002,6.1150000000000003E-2,2.4460000000000002,6.1150000000000003E-2,0]
[null,null,110,"Dalcahue  110 kV -  H2 Línea 110 kV Dalcahue - Pid Pid "," H2",40,2.4489999999999998,6.1224999999999995E-2,2.4500000000000002,6.1250000000000006E-2,4.0832993058404821E-4]
[null,null,110,"Dalcahue  110 kV - HT1 Transformador TR1 110/23 kV","HT1",40,4.5430000000000001,0.11357500000000001,4.5430000000000001,0.11357500000000001,0]
[null,"Degañ ",110,"Degañ  110 kV - HT1  Transformador Degañ TR1 110/23 kV","HT1 ",40,5.585,0.139625,5.585,0.139625,0]
[null,"Desalant",110,"Desalant 110 kV -  H1 Línea 110 kV Desalant - Mejillones/Antofagasta "," H1","S/I",7.4550000000000001,"F/I",7.4610000000000003,"F/I",8.048289738430888E-4]
[null,"Diego de Almagro",110,"Diego de Almagro 110 kV - HT1 Transformador TR1 28 MVA ","HT1",31.5,12.782,0.40577777777777779,12.785,0.40587301587301589,2.3470505398217131E-4]
[null,null,110,"Diego de Almagro 110 kV -  H5 Línea 110 kV Diego de Almagro - Central Javiera/Tal Tal (ELECDA)"," H5",32,13.232000000000001,0.41350000000000003,13.235000000000001,0.41359375000000004,2.2672309552600615E-4]
[null,null,110,"Diego de Almagro 110 kV -  H3 Línea 110 kV Diego de Almagro - Llanta 2 "," H3",31.5,13.448,0.42692063492063492,13.451000000000001,0.42701587301587302,2.2308149910768246E-4]
[null,null,110,"Diego de Almagro 110 kV - HT2 Transformador TR2 ","HT2",32,12.782,0.3994375,12.785,0.39953125,2.3470505398217131E-4]
[null,null,110,"Diego de Almagro 110 kV -  H1 Línea 110 kV Diego de Almagro - Central PV El Salvador"," H1",31.5,13.447000000000001,0.42688888888888893,13.450000000000001,0.42698412698412702,2.2309808879304778E-4]
[null,null,110,"Diego de Almagro 110 kV -  H2 Línea 110 kV Diego de Almagro - Llanta 1"," H2",31.5,13.448,0.42692063492063492,13.451000000000001,0.42701587301587302,2.2308149910768246E-4]
[null,null,110,"Diego de Almagro 110 kV - HT3 Autotransformador ATR3 120 MVA 220/110/13,8 kV ","HT3",31.5,7.3469999999999995,0.23323809523809522,7.3490000000000002,0.23330158730158732,2.7221995372269877E-4]
[null,null,110,"Diego de Almagro 110 kV -  H8 Línea 110 kV Diego de Almagro - Central Emelda "," H8",40,11.754000000000001,0.29385000000000006,11.757000000000001,0.29392500000000005,2.5523226135784529E-4]
[null,null,110,"Diego de Almagro 110 kV -  H6 Línea 110 kV Diego de Almagro - Manto Verde "," H6",40,13.448,0.3362,13.451000000000001,0.33627499999999999,2.2308149910768246E-4]
[null,null,110,"Diego de Almagro 110 kV -  H9 Línea 110 kV Diego de Almagro - Tap Off Chañares/El Salado"," H9",40,13.22,0.33050000000000002,13.223000000000001,0.33057500000000001,2.269288956127166E-4]
[null,null,110,"Diego de Almagro 110 kV - HT4 Autotransformador ATR4 120/90 MVA 220/110/13,8 kV ","HT4",40,10.285,0.25712499999999999,10.286000000000001,0.25715000000000005,9.722897423444065E-5]
[null,null,110,"Diego de Almagro 110 kV -  H7 Línea 110 kV Diego de Almagro - Minera Franke"," H7",40,13.448,0.3362,13.451000000000001,0.33627499999999999,2.2308149910768246E-4]
[null,null,110,"Diego de Almagro 110 kV - H10 Línea 110 kV Diego de Almagro - Central Andes Generación ","H10",31.5,12.523,0.39755555555555555,12.526,0.39765079365079364,2.3955921105167402E-4]
[null,"Dos Amigos ",110,"Dos Amigos  110 kV -  En Barra",null,null,2.9409999999999998,"N/A",2.9420000000000002,"N/A",3.4002040122418703E-4]
[null,"EB2",110,"EB2 110 kV - HT1 Transformador TR1 7,5MVA 110/4,16kV","HT1",40,3.528,8.8200000000000001E-2,3.5289999999999999,8.8224999999999998E-2,2.8344671201810937E-4]
[null,"EKA Chile ",154,"EKA Chile  154 kV -  En Barra",null,null,14.593,"N/A",15.007999999999999,"N/A",2.8438292331939913E-2]
[null,"El Bato",110,"El Bato 110 kV - HX Línea 110kV El bato - Ventanas","HX","S/I",29.228000000000002,"N/P",36.432000000000002,"N/P",0.24647598193513071]
[null,null,110,"El Bato 110 kV - HTX Transformador 110/12kV","HTX","S/I",29.228000000000002,"N/P",36.432000000000002,"N/P",0.24647598193513071]
[null,"El Cobre ",110,"El Cobre  110 kV -  H1 Línea 110 kV El Cobre - La Calera "," H1",20,4.6970000000000001,0.23485,4.72,0.23599999999999999,4.8967426016605677E-3]
[null,"El Cobre (Codelco)",110,"El Cobre (Codelco) 110 kV -  H1 Línea 110 kV El Cobre (Codelco) - Minero 1"," H1",83,8.6,0.10361445783132529,8.6050000000000004,0.10367469879518072,5.8139534883730026E-4]
[null,null,110,"El Cobre (Codelco) 110 kV -  H2 Línea 110 kV El Cobre (Codelco) - Minero 2"," H2",83,8.6,0.10361445783132529,8.6050000000000004,0.10367469879518072,5.8139534883730026E-4]
[null,null,110,"El Cobre (Codelco) 110 kV - HT1 Transformador TR3 110/13,8 kV ","HT1",52.73,17.199000000000002,0.32617106011758018,17.21,0.32637967001706814,6.3957206814345207E-4]
[null,null,110,"El Cobre (Codelco) 110 kV - HT2 Transformador TR4 110/13,8 kV ","HT2",52.73,17.199000000000002,0.32617106011758018,17.21,0.32637967001706814,6.3957206814345207E-4]
[null,null,110,"El Cobre (Codelco) 110 kV - HT3 Transformador TR2 110/13,8 kV ","HT3",52.73,17.199000000000002,0.32617106011758018,17.21,0.32637967001706814,6.3957206814345207E-4]
[null,null,110,"El Cobre (Codelco) 110 kV - HT4 Transformador TR1 110/13,8 kV ","HT4",33,17.199000000000002,0.52118181818181819,17.21,0.52151515151515149,6.3957206814345207E-4]
[null,null,110,"El Cobre (Codelco) 110 kV - HT7 Transformador T7 40-45-50MVA, 110/13,8kV","HT7",40,17.199000000000002,0.42997500000000005,17.21,0.43025000000000002,6.3957206814345207E-4]
[null,null,110,"El Cobre (Codelco) 110 kV - HT8 Transformador T8 40-45-50MVA, 110/13,8kV","HT8",40,17.199000000000002,0.42997500000000005,17.21,0.43025000000000002,6.3957206814345207E-4]
[null,null,110,"El Cobre (Codelco) 110 kV - T9 Transformador T9 40-45-50MVA, 110/13,8kV","T9",40,17.199000000000002,0.42997500000000005,17.21,0.43025000000000002,6.3957206814345207E-4]
[null,"El Empalme ",110,"El Empalme  110 kV -  H1 Línea 110 kV El Empalme - Molinos (Enlasa)"," H1",40,2.4359999999999999,6.0899999999999996E-2,2.4359999999999999,6.0899999999999996E-2,0]
[null,null,110,"El Empalme  110 kV -  H2 Línea 110kV Ilique - El Empalme"," H2",40,4.16,0.10400000000000001,4.16,0.10400000000000001,0]
[null,null,110,"El Empalme  110 kV -  H3 Línea 110 kV El Empalme - Colaco"," H3",40,2.4359999999999999,6.0899999999999996E-2,2.4359999999999999,6.0899999999999996E-2,0]
[null,null,110,"El Empalme  110 kV - HT1 Transformador TR1 16/11 MVA 115/24 kV ","HT1",40,4.16,0.10400000000000001,4.16,0.10400000000000001,0]
[null,"El Espino",110,"El Espino 110 kV - HX1 Línea 110kV El Espino-Combarbalá","HX1","S/I",2.0880000000000001,"N/P",2.0880000000000001,"N/P",0]
[null,null,110,"El Espino 110 kV - HX2 Línea 110kV Illapel - El Espino","HX2","S/I",2.085,"N/P",2.0860000000000003,"N/P",4.7961630695459665E-4]
[null,"El Lince",110,"El Lince 110 kV - HT  Línea 110 kV El Lince - Mejillones ","HT ","S/I",1.78,"F/I",1.78,"F/I",0]
[null,"El Peñón ",110,"El Peñón  110 kV - HT1 Transformador T1 30/24/18 MVA 115/25 kV ","HT1",25,9.3320000000000007,0.37328000000000006,9.3350000000000009,0.37340000000000001,3.2147449635663454E-4]
[null,null,110,"El Peñón  110 kV -  H3 Línea 110 kV El Peñón -  Minera Teck CDA"," H3",31.5,9.3320000000000007,0.29625396825396827,9.3350000000000009,0.29634920634920636,3.2147449635663454E-4]
[null,null,110,"El Peñón  110 kV -  H1 Línea 110 kV El Peñón - La Ruca C1 "," H1",40,8.6710000000000012,0.21677500000000002,8.6740000000000013,0.21685000000000004,3.4598085572599621E-4]
[null,null,110,"El Peñón  110 kV -  H2 Línea 110 kV El Peñón - Pan de Azúcar  "," H2",40,6.1490000000000009,0.15372500000000003,6.1510000000000007,0.15377500000000002,3.2525613920959172E-4]
[null,null,110,"El Peñón  110 kV -  H4 Línea 110 kV El Peñón - Central Las Piedras "," H4",40,7.6250000000000009,0.19062500000000002,7.628000000000001,0.19070000000000004,3.9344262295083456E-4]
[null,null,110,"El Peñón  110 kV -  H5 Línea 110 kV El Peñón - La Ruca C2"," H5",31.5,8.6660000000000004,0.27511111111111114,8.6690000000000005,0.27520634920634923,3.4618047542119934E-4]
[null,null,110,"El Peñón  110 kV -  H7 Línea 110 kV El Peñón - Pan de Azúcar "," H7",40,6.1490000000000009,0.15372500000000003,6.1510000000000007,0.15377500000000002,3.2525613920959172E-4]
[null,null,110,"El Peñón  110 kV - HT3 Transformador TR3 30 MVA 110/69/13,8 kV ","HT3",40,9.3320000000000007,0.23330000000000001,9.3350000000000009,0.23337500000000003,3.2147449635663454E-4]
[null,"El Romeral (CMP)",110,"El Romeral (CMP) 110 kV - L1 Línea 110 kV Romeral - Tap Off El Romeral ","L1",40,3.9969999999999999,9.9925E-2,3.9980000000000002,9.9950000000000011E-2,2.5018764073063144E-4]
[null,"El Salado ",110,"El Salado  110 kV - HT1 Transformador TR1 110/23 kV ","HT1",40,3.6549999999999998,9.1374999999999998E-2,3.6549999999999998,9.1374999999999998E-2,0]
[null,"El Salto ",110,"El Salto  110 kV - H1 Línea 110 kV El Salto - Los Almendros 1","H1",40,30.711999999999996,0.76779999999999993,30.823999999999998,0.77059999999999995,3.6467830164105849E-3]
[null,null,110,"El Salto  110 kV - H2 Línea 110 kV El Salto - Los Almendros 2","H2",40,30.711999999999996,0.76779999999999993,30.823999999999998,0.77059999999999995,3.6467830164105849E-3]
[null,null,110,"El Salto  110 kV - H5 Línea 110 kV El Salto - San Cristóbal 1 ","H5",40,30.297999999999995,0.75744999999999985,30.401999999999997,0.76004999999999989,3.4325698065879851E-3]
[null,null,110,"El Salto  110 kV - H6 Línea 110 kV El Salto - San Cristóbal 2","H6",40,30.297999999999995,0.75744999999999985,30.401999999999997,0.76004999999999989,3.4325698065879851E-3]
[null,null,110,"El Salto  110 kV - HT1 Transformador TR1 400 MVA 220/110/13,2 kV ","HT1",40,29.122999999999998,0.72807499999999992,29.224999999999998,0.73062499999999997,3.5023864299694508E-3]
[null,null,110,"El Salto  110 kV - HT2 Transformador TR2 400 MVA 220/110/13,2 kV ","HT2",40,29.122999999999998,0.72807499999999992,29.224999999999998,0.73062499999999997,3.5023864299694508E-3]
[null,null,110,"El Salto  110 kV - HCE Banco de CCEE 80 MVAr","HCE",40,35.875999999999998,0.89689999999999992,36.015999999999998,0.90039999999999998,3.9023302486342003E-3]
[null,"El Salvador ",110,"El Salvador  110 kV -  H1 Línea 110 kV El Salvador - Diego de Almagro"," H1",14.6,3.2189999999999999,0.22047945205479452,3.22,0.22054794520547946,3.1065548306937992E-4]
[null,null,110,"El Salvador  110 kV -  H2 Línea 110 kV El Salvador  - Llanta 1"," H2",14.6,3.343,0.22897260273972603,3.3440000000000003,0.229041095890411,2.9913251570455699E-4]
[null,null,110,"El Salvador  110 kV - HT3 Transformador TR3 20/15 MVA 110/12,5 kV ","HT3",26,4.9119999999999999,0.18892307692307692,4.9130000000000003,0.18896153846153846,2.035830618893188E-4]
[null,null,110,"El Salvador  110 kV - HT1 Transformador TR1 20/15 MVA 110/12,5 kV ","HT1",7.5,4.8959999999999999,0.65279999999999994,4.8970000000000002,0.65293333333333337,2.042483660131401E-4]
[null,null,110,"El Salvador  110 kV -  H3 Línea 110 kV El Salvador - Llanta 2"," H3",14.6,3.2770000000000001,0.22445205479452057,3.2780000000000005,0.22452054794520551,3.0515715593540859E-4]
[null,null,110,"El Salvador  110 kV - HT2 Transformador TR2 20/15 MVA 110/12,5 kV ","HT2",7.5,4.9119999999999999,0.65493333333333337,4.9130000000000003,0.65506666666666669,2.035830618893188E-4]
[null,null,110,"El Salvador  110 kV - H4 Línea 110 kV El Salvador - Línea Lixiviación","H4","S/I",4.9279999999999999,"F/I",4.9290000000000003,"F/I",2.029220779221457E-4]
[null,"Esmeralda ",110,"Esmeralda  110 kV - HT1 Transformador ATR Esmeralda 220/110 kV","HT1","S/I",5.4780000000000006,"F/I",5.4830000000000005,"F/I",9.1274187659727871E-4]
[null,null,110,"Esmeralda  110 kV -  H2 Línea 110 kV Esmeralda - Centro "," H2","S/I",9.1910000000000007,"F/I",9.2010000000000005,"F/I",1.0880208900010647E-3]
[null,null,110,"Esmeralda  110 kV -  H3 Línea 110kV Guardiamarina - Esmeralda"," H3","S/I",7.3969999999999994,"F/I",7.4039999999999999,"F/I",9.4632959307835096E-4]
[null,null,110,"Esmeralda  110 kV -  H1 Línea 110 kV Esmeralda - Sur"," H1","S/I",9.1910000000000007,"F/I",9.2010000000000005,"F/I",1.0880208900010647E-3]
[null,null,110,"Esmeralda  110 kV -  H4 Línea 110 kV Esmeralda - Tap Off Uribe/Uribe "," H4","S/I",6.17,"F/I",6.1750000000000007,"F/I",8.1037277147500515E-4]
[null,"Esperanza (HASA)",110,"Esperanza (HASA) 110 kV -  HT Transformador TR2 30 MVA 110/66 kV"," HT",31.5,26.344000000000001,0.83631746031746035,26.727999999999998,0.84850793650793643,1.4576374126935802E-2]
[null,null,110,"Esperanza (HASA) 110 kV - H1 Línea 110 kV  Esperanza (HASA) - Río Aconcagua C1","H1",40,20.266999999999999,0.50667499999999999,20.596999999999998,0.51492499999999997,1.6282626930478033E-2]
[null,null,110,"Esperanza (HASA) 110 kV -  H2 Línea 110 kV  Esperanza (HASA) - Río Aconcagua C2"," H2",40,20.266999999999999,0.50667499999999999,20.596999999999998,0.51492499999999997,1.6282626930478033E-2]
[null,"Estación de Bombeo Sierra Gorda N°1",110,"Estación de Bombeo Sierra Gorda N°1 110 kV - HT1  Transformador TR01 70/70/12 MVA 220/110/13,8 kV y Transformador TR Reserva 70/70/12 MVA 220/110/13,8 kV ","HT1 ",40,4.6109999999999998,0.11527499999999999,4.6120000000000001,0.1153,2.1687269572768033E-4]
[null,null,110,"Estación de Bombeo Sierra Gorda N°1 110 kV - HT2  Transformador TR02 37,5 MVA 110/6,9 kV ","HT2 ",40,4.6100000000000003,0.11525000000000001,4.6109999999999998,0.11527499999999999,2.1691973969619212E-4]
[null,null,110,"Estación de Bombeo Sierra Gorda N°1 110 kV - H3 Línea 110 kV Estación de Bombeo Sierra Gorda N° 1 - Estación de Bombeo Sierra Gorda N° 2","H3",40,4.609,0.11522499999999999,4.6099999999999994,0.11524999999999999,2.1696680407885566E-4]
[null,"Estación de Bombeo Sierra Gorda N°2",110,"Estación de Bombeo Sierra Gorda N°2 110 kV - HT1 Transformador TR01 37,5 MVA 110/6,9 kV ","HT1",40,1.5780000000000001,3.9449999999999999E-2,1.5780000000000001,3.9449999999999999E-2,0]
[null,"Fatima",154,"Fatima 154 kV - A1 Línea 154kV Fatima - Alto Jahuel C1","A1",40,10.899000000000001,0.27247500000000002,10.908999999999999,0.272725,9.1751536838223784E-4]
[null,null,154,"Fatima 154 kV - A2 Línea 154kV Fatima - Alto Jahuel C2","A2",40,10.899000000000001,0.27247500000000002,10.908999999999999,0.272725,9.1751536838223784E-4]
[null,null,154,"Fatima 154 kV - AX1 Línea 154kV Fatima - Tap Off Paine C1","AX1","S/I",11.117000000000001,"N/P",11.129,"N/P",1.079427903211179E-3]
[null,null,154,"Fatima 154 kV - AX2 Línea 154kV Fatima - Tap Off Paine C2","AX2","S/I",11.496,"N/P",11.507999999999999,"N/P",1.0438413361167952E-3]
[null,null,154,"Fatima 154 kV - AT3 Transformador Fatima 75MVA 154/66 kV","AT3",40,13.634,0.34084999999999999,13.647,0.34117500000000001,9.5349860642510642E-4]
[null,null,154,"Fatima 154 kV - ATX Transformador Fatima TR2 75MVA 154/66 kV","ATX","S/I",13.624000000000001,"N/P",13.638,"N/P",1.0275983558425826E-3]
[null,"Florida ",110,"Florida  110 kV -  H1 Línea 110 kV  Florida - Buin 1"," H1",40,33.139000000000003,0.82847500000000007,33.215000000000003,0.83037500000000009,2.2933703491354752E-3]
[null,null,110,"Florida  110 kV -  H2 Línea 110 kV  Florida - Buin 2"," H2",40,33.139000000000003,0.82847500000000007,33.215000000000003,0.83037500000000009,2.2933703491354752E-3]
[null,null,110,"Florida  110 kV -  H3 Línea 110 kV  Florida - Los Almendros 2"," H3",31.5,34.090000000000003,1.0822222222222224,34.167000000000002,1.0846666666666667,2.2587268993839301E-3]
[null,null,110,"Florida  110 kV -  H4 Línea 110 kV  Florida - Los Almendros 1"," H4",31.5,34.090000000000003,1.0822222222222224,34.167000000000002,1.0846666666666667,2.2587268993839301E-3]
[null,null,110,"Florida  110 kV -  H5 Línea 110 kV  Florida - Ochagavía 1 "," H5",31.5,31.798000000000002,1.0094603174603176,31.869,1.0117142857142858,2.2328448330083007E-3]
[null,null,110,"Florida  110 kV -  H6 Línea 110 kV  Florida - Ochagavía 2 "," H6",31.5,31.798000000000002,1.0094603174603176,31.869,1.0117142857142858,2.2328448330083007E-3]
[null,null,110,"Florida  110 kV - HT1 Transformador TR01 25 MVA 110/12 kV ","HT1",31.5,37.767000000000003,1.198952380952381,37.856000000000002,1.2017777777777778,2.3565546641247286E-3]
[null,null,110,"Florida  110 kV -  H7 Línea 110 kV  Florida - Las Vizcachas 1"," H7",40,35.117000000000004,0.87792500000000007,35.204000000000001,0.88009999999999999,2.4774325825097868E-3]
[null,null,110,"Florida  110 kV -  H8 Línea 110 kV  Florida - Las Vizcachas 2"," H8",40,34.944000000000003,0.87360000000000004,35.032000000000004,0.87580000000000013,2.5183150183150458E-3]
[null,"FPC",154,"FPC 154 kV - A1 acoplador ","A1","S/I",12.65,"F/I",13.837999999999999,"F/I",9.391304347826078E-2]
[null,"Fundición Chagres ",110,"Fundición Chagres  110 kV -  H2 Línea 110 kV Fundición Chagres - San Felipe 1\nLínea 110 kV Fundición Chagres - Esperanza (HASA) 1"," H2",40,10.500999999999998,0.26252499999999995,10.592000000000001,0.26480000000000004,8.66584134844328E-3]
[null,null,110,"Fundición Chagres  110 kV -  H1 Línea 110 kV Fundición Chagres - Nueva Panquehue"," H1",40,18.001999999999999,0.45004999999999995,18.163,0.45407500000000001,8.9434507276969985E-3]
[null,null,110,"Fundición Chagres  110 kV -  H3 Línea 110 kV Fundición Chagres - Río Aconcagua"," H3",40,10.653999999999998,0.26634999999999998,10.737000000000002,0.26842500000000002,7.7905012201993388E-3]
[null,null,110,"Fundición Chagres  110 kV - HT11 Transformador TR1 110/12 kV ","HT11",40,19.579999999999998,0.48949999999999994,19.748000000000001,0.49370000000000003,8.580183861082882E-3]
[null,null,110,"Fundición Chagres  110 kV - HT12 Transformador TR2 110/12 kV ","HT12",40,19.579999999999998,0.48949999999999994,19.748000000000001,0.49370000000000003,8.580183861082882E-3]
[null,null,110,"Fundición Chagres  110 kV - A Paño Acoplador","A",40,19.579999999999998,0.48949999999999994,19.748000000000001,0.49370000000000003,8.580183861082882E-3]
[null,"Fundición Paipote",110,"Fundición Paipote 110 kV -  HL Línea 110 kV Fundición Paipote - Cardones "," HL",31.5,4.5620000000000003,0.14482539682539683,4.5629999999999997,0.14485714285714285,2.1920210434008016E-4]
[null,null,110,"Fundición Paipote 110 kV - HT1 Autotransformador ATR1","HT1",31.5,4.5620000000000003,0.14482539682539683,4.5629999999999997,0.14485714285714285,2.1920210434008016E-4]
[null,null,110,"Fundición Paipote 110 kV - HT2 Autotransformador ATR2","HT2",31.5,4.5620000000000003,0.14482539682539683,4.5629999999999997,0.14485714285714285,2.1920210434008016E-4]
[null,"Galleguillos ",110,"Galleguillos  110 kV -  H1 Línea 110 kV Galleguillos - Copayapu 1"," H1",40,2.5890000000000004,6.4725000000000005E-2,2.59,6.4750000000000002E-2,3.8624951718788938E-4]
[null,null,110,"Galleguillos  110 kV -  H2 Línea 110 kV Galleguillos - Hernán Fuentes "," H2",40,2.9540000000000002,7.3849999999999999E-2,2.9549999999999996,7.3874999999999996E-2,3.3852403520631203E-4]
[null,null,110,"Galleguillos  110 kV -  H3 Línea 110 kV Galleguillos - Impulsión/Caldera"," H3",40,4.5460000000000003,0.11365,4.5469999999999997,0.113675,2.1997360316749795E-4]
[null,"Gamboa",110,"Gamboa 110 kV - HX1 Línea 110kV Pid Pid - Gamboa","HX1","S/I",4.7869999999999999,"N/P",4.7869999999999999,"N/P",0]
[null,null,110,"Gamboa 110 kV - HX2 Línea 110kV Gamboa-Castro","HX2","S/I",5.9539999999999997,"N/P",5.9539999999999997,"N/P",0]
[null,null,110,"Gamboa 110 kV - HX3 Línea 220kV (energizada en 110kV) Gamboa - Chonchi","HX3","S/I",5.7789999999999999,"N/P",5.7789999999999999,"N/P",0]
[null,null,110,"Gamboa 110 kV - HXT1 Transformador 90 MVA 220/110/23 kV Gamboa 1","HXT1","S/I",3.8460000000000001,"N/P",3.8460000000000001,"N/P",0]
[null,null,110,"Gamboa 110 kV - HXT2 Transformador 90 MVA 220/110/23 kV Gamboa 2","HXT2","S/I",3.8460000000000001,"N/P",3.8460000000000001,"N/P",0]
[null,"GNL Mejillones",110,"GNL Mejillones 110 kV - H1 Línea GNL Mejillones 110kV - Chacaya","H1","S/I",3.1640000000000001,"F/I",3.1659999999999999,"F/I",6.3211125158020847E-4]
[null,"GNL Quintero",110,"GNL Quintero 110 kV - HA2 Línea 110 kV GNL Quintero - Ventanas","HA2",40,16.754999999999999,0.418875,21.81,0.54525000000000001,0.30170098478066248]
[null,null,110,"GNL Quintero 110 kV - HB2 Línea 110 kV GNL Quintero - Central Quintero","HB2",40,16.722000000000001,0.41805000000000003,21.773,0.54432499999999995,0.30205717019495265]
[null,null,110,"GNL Quintero 110 kV - HA1 Transformador TR1 30/50 MVA 110/6.6 kV","HA1",40,22.093,0.55232499999999995,27.183,0.67957500000000004,0.23038971619970125]
[null,null,110,"GNL Quintero 110 kV - HB1 Transformador TR2 30/50 MVA 110/6.6 kV","HB1",40,22.093,0.55232499999999995,27.183,0.67957500000000004,0.23038971619970125]
[null,null,110,"GNL Quintero 110 kV - HA3 Línea 110 kV GNL Quintero - ENAP 1","HA3",40,22.093,0.55232499999999995,27.183,0.67957500000000004,0.23038971619970125]
[null,null,110,"GNL Quintero 110 kV - HB3 Línea 110 kV GNL Quintero - ENAP 2","HB3",40,22.093,0.55232499999999995,27.183,0.67957500000000004,0.23038971619970125]
[null,"Guayaques ",110,"Guayaques  110 kV - HT3 Transformador TR02 37,5 MVA 110/3,45 kV ","HT3","S/I",1.746,"F/I",1.746,"F/I",0]
[null,null,110,"Guayaques  110 kV - HT1 Transformador TR01 37,5 MVA 110/3,45 kV ","HT1","S/I",1.746,"F/I",1.746,"F/I",0]
[null,"Hernán Fuentes ",110,"Hernán Fuentes  110 kV - HT1 Transformador T1 12/10 MVA 110/23 kV ","HT1",40,5.1740000000000004,0.12935000000000002,5.1760000000000002,0.12940000000000002,3.8654812524155E-4]
[null,null,110,"Hernán Fuentes  110 kV -  H3 Línea 110 kV Hernán Fuentes - Impulsión/Caldera/Galleguillos"," H3",40,3.0570000000000004,7.6425000000000007E-2,3.0580000000000003,7.6450000000000004E-2,3.2711808963032047E-4]
[null,null,110,"Hernán Fuentes  110 kV -  H1 Línea 110 kV Hernán Fuentes - Copiapo"," H1",40,3.0870000000000002,7.7175000000000007E-2,3.0880000000000001,7.7200000000000005E-2,3.2393909944926786E-4]
[null,"Huachipato",154,"Huachipato 154 kV - AT1 Transformador TR1 50MVA 154/13.8 kV ","AT1",40,17.044,0.42610000000000003,17.584,0.43959999999999999,3.1682703590706358E-2]
[null,null,154,"Huachipato 154 kV - AT2 Transformador TR2 50MVA 154/13.8 kV ","AT2",40,17.044,0.42610000000000003,17.584,0.43959999999999999,3.1682703590706358E-2]
[null,null,154,"Huachipato 154 kV - AT3 Transformador TR3 50MVA 154/13.8 kV ","AT3",40,17.044,0.42610000000000003,17.584,0.43959999999999999,3.1682703590706358E-2]
[null,null,154,"Huachipato 154 kV - AT5 Transformador TR4 50MVA 154/13,8 kV ","AT5",25,17.044,0.68176000000000003,17.584,0.70335999999999999,3.1682703590706358E-2]
[null,"Hualpen",154,"Hualpen 154 kV - A1 Línea 154 kV Hualpen - San Vicente 1","A1",40,15.975999999999999,0.39939999999999998,16.731999999999999,0.41830000000000001,4.7320981472208326E-2]
[null,null,154,"Hualpen 154 kV - A2 Línea 154 kV Hualpen - San Vicente 2","A2",40,15.981,0.39952500000000002,16.737000000000002,0.41842500000000005,4.7306176084099996E-2]
[null,null,154,"Hualpen 154 kV - A3 Línea 154 kV Hualpen - Petropower","A3",40,18.731000000000002,0.46827500000000005,19.532,0.48830000000000001,4.276333351129135E-2]
[null,null,154,"Hualpen 154 kV - A4 Línea 154 kV Hualpen - Mapal","A4",40,16.151,0.403775,16.522000000000002,0.41305000000000003,2.297071388768511E-2]
[null,null,154,"Hualpen 154 kV - AT1 Transformador Hualpen ATR1 300MVA 225/15/66 kV","AT1",40,11.359,0.28397499999999998,11.886000000000001,0.29715000000000003,4.6394929131085574E-2]
[null,"Huasco",110,"Huasco 110 kV - H1 Línea 110 kV Central Huasco - Maintencillo 1 ","H1",31.5,4.7699999999999996,0.15142857142857141,4.7690000000000001,0.15139682539682539,-2.0964360586990478E-4]
[null,null,110,"Huasco 110 kV - H2 Línea 110 kV Central Huasco - Maintencillo 2","H2",31.5,4.7389999999999999,0.15044444444444444,4.7389999999999999,0.15044444444444444,0]
[null,null,110,"Huasco 110 kV - H3 Línea 110 kV Central Huasco - Pellets 2","H3",31.5,6.87,0.21809523809523809,6.87,0.21809523809523809,0]
[null,null,110,"Huasco 110 kV - H4 Línea 110 kV Central Huasco - Pellets 1","H4",31.5,6.87,0.21809523809523809,6.87,0.21809523809523809,0]
[null,null,110,"Huasco 110 kV - HT3 Transformador 110/11.5KV 28MVA 2","HT3",31.5,6.0150000000000006,0.19095238095238096,6.0150000000000006,0.19095238095238096,0]
[null,null,110,"Huasco 110 kV - HT4 Transformador 110/11.5KV 28MVA 3","HT4",31.5,6.0150000000000006,0.19095238095238096,6.0150000000000006,0.19095238095238096,0]
[null,null,110,"Huasco 110 kV - HT5 Transformador 110/11.5KV 28MVA 1","HT5",31.5,6.0150000000000006,0.19095238095238096,6.0150000000000006,0.19095238095238096,0]
[null,"Illapel ",110,"Illapel  110 kV - HT2 Transformador TR02 13 MVA 110/24/13,8 kV ","HT2",25,4.0999999999999996,0.16399999999999998,4.101,0.16403999999999999,2.4390243902447172E-4]
[null,null,110,"Illapel  110 kV - HT1 Transformador TR01 25 MVA 110/66 kV","HT1",40,3.9239999999999995,9.8099999999999993E-2,3.9249999999999998,9.812499999999999E-2,2.5484199796134915E-4]
[null,null,110,"Illapel  110 kV -  H3 Línea 110 kV Illapel - Punitaqui/Ovalle "," H3",25,2.6489999999999996,0.10595999999999998,2.65,0.106,3.7750094375248552E-4]
[null,null,110,"Illapel  110 kV -  H1 Línea 110 kV Illapel - Salamanca "," H1",31.5,4.0999999999999996,0.13015873015873014,4.101,0.13019047619047619,2.4390243902447172E-4]
[null,null,110,"Illapel  110 kV -  H2 Línea 110 kV Illapel - Choapa "," H2",25,2.496,9.9839999999999998E-2,2.4969999999999999,9.9879999999999997E-2,4.006410256409815E-4]
[null,"Impulsión",110,"Impulsión 110 kV - HT Transformador TR1 110/23 kV ","HT","S/I",4.0090000000000003,"F/I",4.01,"F/I",2.4943876278359832E-4]
[null,"Incahuasi ",110,"Incahuasi  110 kV - H1 Línea 110 kV Incahuasi - Las Compañias/Tap Off El Romeral","H1",40,1.2899999999999998,3.2249999999999994E-2,1.2899999999999998,3.2249999999999994E-2,0]
[null,"Itahue",154,"Itahue 154 kV - A1 Línea 154 kV Itahue - Cipreses C1","A1",40,19.088000000000001,0.47720000000000001,19.103999999999999,0.47759999999999997,8.3822296730921191E-4]
[null,null,154,"Itahue 154 kV - A2 Línea 154 kV Itahue - Cipreses C2","A2",40,19.162000000000003,0.47905000000000009,19.178000000000001,0.47945000000000004,8.3498590961268325E-4]
[null,null,154,"Itahue 154 kV - A3 Línea 154 kV Itahue - Tinguiririca 1","A3",40,17.975000000000001,0.44937500000000002,17.989999999999998,0.44974999999999998,8.3449235048662111E-4]
[null,null,154,"Itahue 154 kV - A4 Línea 154 kV Itahue - Tinguiririca 2/Convento Viejo","A4",40,17.975000000000001,0.44937500000000002,17.989999999999998,0.44974999999999998,8.3449235048662111E-4]
[null,null,154,"Itahue 154 kV - A5 Línea 154 kV Itahue - Charrúa (Parral/Linares)","A5",40,17.707000000000001,0.44267500000000004,17.721,0.443025,7.9064776642002294E-4]
[null,null,154,"Itahue 154 kV - AT Transformador Itahue TR01 75MVA 154/13.8 kV N°1","AT","S/I",19.438000000000002,"F/I",19.452999999999999,"F/I",7.7168432966339198E-4]
[null,null,154,"Itahue 154 kV - AT2 Transformador Itahue TR02 56MVA 154/69/13.8 kV N°2","AT2",40,19.573,0.48932500000000001,19.588999999999999,0.48972499999999997,8.1745261329373305E-4]
[null,null,154,"Itahue 154 kV - AT4 Transformador ATR Itahue N°4","AT4",40,10.601000000000001,0.26502500000000001,10.606999999999999,0.26517499999999999,5.6598434109975007E-4]
[null,null,154,"Itahue 154 kV - AT5 Transformador Itahue TR05N 154/66/13.2 kV N°5","AT5",40,18.240000000000002,0.45600000000000007,18.254999999999999,0.45637499999999998,8.2236842105246793E-4]
[null,"K1 ",100,"K1  100 kV - H12 Línea 100 kV K1 - Chuquicamata","H12","S/I",6.1199999999999992,"F/I",6.266,"F/I",2.3856209150326931E-2]
[null,null,100,"K1  100 kV - H23 Línea 100 kV K1 - 10","H23","S/I",6.1260000000000003,"F/I",6.2720000000000002,"F/I",2.3832843617368576E-2]
[null,null,100,"K1  100 kV - HT1 Transformador TR01 26,6/20 MVA 100/13,8 kV ","HT1","S/I",10.54,"F/I",10.795,"F/I",2.419354838709685E-2]
[null,null,100,"K1  100 kV - HT2 Transformador TR02 26,6/20 MVA 100/13,8 kV ","HT2","S/I",10.54,"F/I",10.795,"F/I",2.419354838709685E-2]
[null,null,100,"K1  100 kV - HT3 Transformador TR03 25/20 MVA 100/13,8 kV ","HT3","S/I",10.54,"F/I",10.795,"F/I",2.419354838709685E-2]
[null,null,100,"K1  100 kV - HAB Paño Acoplador ","HAB","S/I",10.54,"F/I",10.795,"F/I",2.419354838709685E-2]
[null,"KM6",100,"KM6 100 kV - H13 Línea 100 kV KM6 - Chuquicamata","H13",25,8.0449999999999999,0.32179999999999997,8.2420000000000009,0.32968000000000003,2.4487259167184704E-2]
[null,null,100,"KM6 100 kV - H22 Línea 100 kV KM6 - 10A","H22","S/I",6.9169999999999998,"F/I",7.0830000000000002,"F/I",2.3998843429232381E-2]
[null,null,100,"KM6 100 kV - H24 Línea 100 kV KM6 - Sopladores","H24","S/I",11.007,"F/I",11.282,"F/I",2.4984101026619458E-2]
[null,null,100,"KM6 100 kV - H25 Línea 100 kV KM6 - Salar C1","H25",31.5,9.0289999999999999,0.28663492063492063,9.26,0.29396825396825393,2.5584228596743811E-2]
[null,null,100,"KM6 100 kV - H26 Línea 100 kV KM6 - Salar C2","H26",31.5,9.0289999999999999,0.28663492063492063,9.26,0.29396825396825393,2.5584228596743811E-2]
[null,null,100,"KM6 100 kV - HT1 Transformador KM6 TR01 25/20 MVA 100/13.8 kV ","HT1","S/I",11.007,"F/I",11.282,"F/I",2.4984101026619458E-2]
[null,null,100,"KM6 100 kV - HT2 Transformador KM6 TR02 33/25 MVA 100/13.8 kV","HT2","S/I",11.007,"F/I",11.282,"F/I",2.4984101026619458E-2]
[null,null,100,"KM6 100 kV - HT3 Transformador KM6 TR03 25/20 MVA 100/13.8 kV","HT3","S/I",11.007,"F/I",11.282,"F/I",2.4984101026619458E-2]
[null,null,100,"KM6 100 kV - HACOP Paño Acoplador ","HACOP","S/I",11.007,"F/I",11.282,"F/I",2.4984101026619458E-2]
[null,"La Calera",110,"La Calera 110 kV - H5 Línea 110 kV La Calera - El Cobre","H5",31.5,14.555,0.46206349206349207,14.78,0.46920634920634918,1.5458605290278231E-2]
[null,null,110,"La Calera 110 kV - HT1 Transformador TR1 30 MVA 115/44 kV","HT1",40,14.249000000000001,0.35622500000000001,14.472,0.36180000000000001,1.5650221068145061E-2]
[null,null,110,"La Calera 110 kV - HT2 Transformador TR2 22,5 MVA 115/12 kV","HT2",40,14.555,0.363875,14.78,0.3695,1.5458605290278231E-2]
[null,null,110,"La Calera 110 kV - HT3 Transformador TR3 25 MVA 115/12 kV","HT3",40,14.555,0.363875,14.78,0.3695,1.5458605290278231E-2]
[null,"La Cisterna",110,"La Cisterna 110 kV - H1 Línea 110 kV La Cisterna - Chena/Ochagavía 1","H1",40,19.702000000000002,0.49255000000000004,19.760999999999999,0.49402499999999999,2.9946198355495631E-3]
[null,null,110,"La Cisterna 110 kV - H2 Línea 110 kV La Cisterna - Chena/Ochagavía 2","H2",40,19.702000000000002,0.49255000000000004,19.760999999999999,0.49402499999999999,2.9946198355495631E-3]
[null,null,110,"La Cisterna 110 kV - HT5 Transformador TR05 50 MVA 110/13.2 kV","HT5","S/I",39.404000000000003,"F/I",39.521999999999998,"F/I",2.9946198355495631E-3]
[null,"La Dehesa",110,"La Dehesa 110 kV - HT1 Transformador TR01 25MVA 110/13.2 kV ","HT1",31.5,22.259,0.70663492063492062,22.309000000000001,0.70822222222222231,2.2462824026236896E-3]
[null,null,110,"La Dehesa 110 kV - HT2 Transformador TR02 50MVA 110/12.5 kV","HT2",40,22.259,0.55647500000000005,22.309000000000001,0.55772500000000003,2.2462824026236896E-3]
[null,null,110,"La Dehesa 110 kV - HT3 Transformador TR03 50MVA 110/23.5 kV","HT3",40,22.259,0.55647500000000005,22.309000000000001,0.55772500000000003,2.2462824026236896E-3]
[null,null,110,"La Dehesa 110 kV - H4 Transformador TR04 20MVA  110/23 kV ","H4",40,22.259,0.55647500000000005,22.309000000000001,0.55772500000000003,2.2462824026236896E-3]
[null,"La Pintana",110,"La Pintana 110 kV - H1 Línea 110 kV La Pintana - Buin / Florida 1","H1",40,16.085999999999999,0.40214999999999995,16.119,0.40297499999999997,2.0514733308467769E-3]
[null,null,110,"La Pintana 110 kV - H2 Línea 110 kV La Pintana - Buin / Florida 2","H2",40,16.085999999999999,0.40214999999999995,16.119,0.40297499999999997,2.0514733308467769E-3]
[null,null,110,"La Pintana 110 kV - A-T4 Transformador TR04 25MVA 110/12.5 kV","A-T4",31.5,32.171999999999997,1.0213333333333332,32.238,1.0234285714285714,2.0514733308467769E-3]
[null,"La Portada",110,"La Portada 110 kV - H1 Línea 110kV Guardiamarina - La Portada","H1","S/I",7.9669999999999996,"F/I",7.9729999999999999,"F/I",7.5310656457891652E-4]
[null,null,110,"La Portada 110 kV - HT1 Transformador TR1 110/23 kV ","HT1","S/I",7.9660000000000002,"F/I",7.9729999999999999,"F/I",8.7873462214407144E-4]
[null,null,110,"La Portada 110 kV - HT3 Transformador TR3 110/23 kV","HT3","S/I",7.9870000000000001,"F/I",7.9939999999999998,"F/I",8.7642418930758393E-4]
[null,"La Reina",110,"La Reina 110 kV -  H1 Línea 110 kV La Reina - Florida/Los Almendros 1"," H1",40,10.397,0.25992500000000002,10.412000000000001,0.26030000000000003,1.442723862652743E-3]
[null,null,110,"La Reina 110 kV -  H2 Línea 110 kV La Reina - Florida/Los Almendros 2"," H2",40,10.397,0.25992500000000002,10.412000000000001,0.26030000000000003,1.442723862652743E-3]
[null,"Lagunillas",154,"Lagunillas 154 kV -  A2 Línea 154kV Lagunillas - Hualpén "," A2",40,5.0439999999999996,0.12609999999999999,5.2290000000000001,0.13072500000000001,3.6677240285487807E-2]
[null,null,154,"Lagunillas 154 kV -  A3 Línea 154kV Lagunillas - Hualpén "," A3",40,9.1910000000000007,0.22977500000000001,9.9570000000000007,0.24892500000000001,8.3342400174083342E-2]
[null,null,154,"Lagunillas 154 kV -  A4 ATR Lagunilla 220/154 kV"," A4",40,13.66,0.34150000000000003,14.882,0.37204999999999999,8.9458272327964827E-2]
[null,null,154,"Lagunillas 154 kV -  A5 ATR Lagunilla 220/154 kV"," A5",40,5.0439999999999996,0.12609999999999999,5.2290000000000001,0.13072500000000001,3.6677240285487807E-2]
[null,null,154,"Lagunillas 154 kV - A5 Línea 154kV Lagunillas - Bocamina","A5",40,5.0439999999999996,0.12609999999999999,5.2290000000000001,0.13072500000000001,3.6677240285487807E-2]
[null,null,154,"Lagunillas 154 kV -  A6 Línea 154kV Lagunillas - Bocamina"," A6",40,9.1910000000000007,0.22977500000000001,9.9570000000000007,0.24892500000000001,8.3342400174083342E-2]
[null,"Las Acacias",110,"Las Acacias 110 kV -  H1 Línea 110 kV Las Acacias - Buin/Lo Espejo 1"," H1",40,20.907000000000004,0.52267500000000011,20.972000000000001,0.52429999999999999,3.1090065528290869E-3]
[null,null,110,"Las Acacias 110 kV -  H2 Línea 110 kV Las Acacias - Buin/Lo Espejo 2"," H2",40,20.907000000000004,0.52267500000000011,20.972000000000001,0.52429999999999999,3.1090065528290869E-3]
[null,"Las Arañas ",110,"Las Arañas  110 kV - HL1 Línea 110 kV Las Arañas - Quelentaro","HL1",40,3.46,8.6499999999999994E-2,3.4620000000000002,8.6550000000000002E-2,5.7803468208098951E-4]
[null,null,110,"Las Arañas  110 kV - HT2 AutoTransformador ATR2 40/40/8 MVA 110/66/13.8 kV","HT2",40,3.46,8.6499999999999994E-2,3.4620000000000002,8.6550000000000002E-2,5.7803468208098951E-4]
[null,null,110,"Las Arañas  110 kV - HT1 AutoTransformador ATR1 40/40/8 MVA 110/66/13.8 kV","HT1","S/I",3.46,"F/I",3.4620000000000002,"F/I",5.7803468208098951E-4]
[null,"Las Compañias ",110,"Las Compañias  110 kV - H2 Línea 110 kV Las Compañias - Maintencillo/Tap Off Romeral 1","H2",40,4.8869999999999996,0.12217499999999999,4.8879999999999999,0.1222,2.0462451401684757E-4]
[null,null,110,"Las Compañias  110 kV - H1 Línea 110 kV Las Compañias - Pan de Azucar 1","H1",40,4.9130000000000003,0.122825,4.9139999999999997,0.12284999999999999,2.035416242620488E-4]
[null,null,110,"Las Compañias  110 kV - HT Transformador TR1 110/14.2 kV","HT",40,5.6079999999999997,0.14019999999999999,5.609,0.14022499999999999,1.7831669044228495E-4]
[null,"Las Luces",110,"Las Luces 110 kV - HT1 Transformador Las Luces 110/33 kV N°1","HT1","S/I",1.3120000000000001,"F/I",1.3120000000000001,"F/I",0]
[null,null,110,"Las Luces 110 kV - H2 Línea 110 kV Las Luces - Tal Tal (ELECDA)  1","H2",31.5,1.3120000000000001,4.1650793650793654E-2,1.3120000000000001,4.1650793650793654E-2,0]
[null,"Las Vegas",110,"Las Vegas 110 kV -  H1 Línea 110 kV Las Vegas - San Pedro/Cerro Calera/Calera 1"," H1",40,22.984000000000002,0.5746,23.251999999999999,0.58129999999999993,1.1660285415941399E-2]
[null,null,110,"Las Vegas 110 kV -  H3 Línea 110 kV Las Vegas - Central Santiago Solar 1"," H3",40,24.51,0.61275000000000002,24.899000000000001,0.622475,1.587107303141572E-2]
[null,null,110,"Las Vegas 110 kV -  H4 Línea 110 kV Las Vegas - Cerro Navia (Enel)/Tap Off Punta Peuco 2"," H4",40,24.51,0.61275000000000002,24.899000000000001,0.622475,1.587107303141572E-2]
[null,null,110,"Las Vegas 110 kV -  H6 Línea 110 kV Las Vegas - Esperanza (HASA) C1"," H6",40,14.461000000000002,0.36152500000000004,14.74,0.36849999999999999,1.929327155798341E-2]
[null,null,110,"Las Vegas 110 kV -  H2 Línea 110 kV Las Vegas - San Pedro/Cerro Calera/Calera 2"," H2",40,22.984000000000002,0.5746,23.251999999999999,0.58129999999999993,1.1660285415941399E-2]
[null,null,110,"Las Vegas 110 kV - HR Acoplador","HR",40,26.513000000000002,0.662825,26.91,0.67274999999999996,1.4973786444385713E-2]
[null,null,110,"Las Vegas 110 kV - HT4 Transformador TR4 160 MVA 110/15 kV","HT4",40,23.305,0.58262499999999995,23.701999999999998,0.59254999999999991,1.7034971036258249E-2]
[null,null,110,"Las Vegas 110 kV - HT1 Transformador TR1 28 MVA 110/44 kV","HT1",40,26.445,0.66112499999999996,26.838999999999999,0.67097499999999999,1.4898846662885171E-2]
[null,null,110,"Las Vegas 110 kV - HT2 Transformador TR2 30 MVA 110/44 kV","HT2",40,26.447000000000003,0.66117500000000007,26.841999999999999,0.67104999999999992,1.4935531440238816E-2]
[null,null,110,"Las Vegas 110 kV - HT3 Tranaformador TR3 25 MVA 110/13.2 kV","HT3",25,26.421000000000003,1.0568400000000002,26.818000000000001,1.0727200000000001,1.5025926346466765E-2]
[null,null,110,"Las Vegas 110 kV - HT5 Transformador TR5 30 MVA 115/13.2 kV","HT5",40,26.513000000000002,0.662825,26.91,0.67274999999999996,1.4973786444385713E-2]
[null,null,110,"Las Vegas 110 kV - H7 Línea 110 kV Las Vegas - Cristalerías (Llay Llay)","H7",40,26.513000000000002,0.662825,26.91,0.67274999999999996,1.4973786444385713E-2]
[null,"Las Vizcachas",110,"Las Vizcachas 110 kV - H1 Línea 110kV Las Vizcachas - Puente Alto (EEPA)","H1",40,20.018000000000001,0.50045000000000006,20.036999999999999,0.50092499999999995,9.4914576880799034E-4]
[null,"Leyda",110,"Leyda 110 kV - HT1 Transformador TR1 12,5/10 MVA 115/13.8 kV","HT1",31.5,5.4630000000000001,0.17342857142857143,5.4690000000000003,0.17361904761904762,1.0982976386601185E-3]
[null,null,110,"Leyda 110 kV - H1 Línea 110 kV Leyda - Alto Melipilla C2","H1",31.5,3.4809999999999999,0.1105079365079365,3.484,0.11060317460317461,8.6182131571390806E-4]
[null,null,110,"Leyda 110 kV - H2 Línea 110 kV Leyda - San Antonio C2","H2",31.5,3.48,0.11047619047619048,3.4830000000000005,0.11057142857142858,8.6206896551740161E-4]
[null,"Linares",154,"Linares 154 kV - AT1 Transformador TR01 60/75MVA","AT1",40,5.2870000000000008,0.13217500000000001,5.29,0.13225000000000001,5.674295441647863E-4]
[null,"Llanta C1",110,"Llanta C1 110 kV -  En Barra",null,null,5.125,"N/A",5.1260000000000003,"N/A",1.9512195121957737E-4]
[null,"Llanta C2",110,"Llanta C2 110 kV -  En Barra",null,null,5.3040000000000003,"N/A",5.3049999999999997,"N/A",1.8853695324273109E-4]
[null,"Lo Aguirre",110,"Lo Aguirre 110 kV - H1 Línea 110 kV Lo Aguirre - Cerro Navia (Enel)/Lo Prado 2","H1",40,7.23,0.18075000000000002,7.234,0.18085000000000001,5.5325034578140517E-4]
[null,"Lo Boza",110,"Lo Boza 110 kV - H1 Línea 110 kV Lo Boza - San Cristóbal/Cerro Navia (Enel) 1","H1",40,17.724,0.44309999999999999,17.78,0.44450000000000001,3.159557661927383E-3]
[null,null,110,"Lo Boza 110 kV - H2 Línea 110 kV Lo Boza - San Cristóbal/Cerro Navia (Enel) 2","H2",40,17.724,0.44309999999999999,17.78,0.44450000000000001,3.159557661927383E-3]
[null,null,110,"Lo Boza 110 kV - HT3 Transformador TR03 12,5 MVA 110/23.5 kV ","HT3",40,35.447000000000003,0.88617500000000005,35.56,0.88900000000000001,3.1878579287386672E-3]
[null,"Lo Espejo",110,"Lo Espejo 110 kV -  En Barra",null,null,51.759,"N/A",51.966999999999999,"N/A",4.0186247802314265E-3]
[null,"Lo Espejo (FFCC)",110,"Lo Espejo (FFCC) 110 kV -  En Barra",null,null,47.048999999999999,"N/A",47.216000000000001,"N/A",3.5494909562371483E-3]
[null,"Lo Prado",110,"Lo Prado 110 kV - H1 Línea 110 kV Lo Prado - Lo Aguirre","H1",40,7.056,0.1764,7.06,0.17649999999999999,5.6689342403621874E-4]
[null,"Lo Valledor",110,"Lo Valledor 110 kV - H1 Línea 110 kV Lo Valledor - Cerro Navia (Enel)/Chena 1","H1",40,14.429,0.36072500000000002,14.462,0.36154999999999998,2.2870607803728237E-3]
[null,null,110,"Lo Valledor 110 kV - HT1 Transformador TR01 25 MVA 110/13.2 kV","HT1",31.5,28.856999999999999,0.91609523809523807,28.923999999999999,0.91822222222222216,2.3217936722459082E-3]
[null,null,110,"Lo Valledor 110 kV - HT4 Transformador TR04 110/12.5 kV","HT4",40,28.856999999999999,0.72142499999999998,28.923999999999999,0.72309999999999997,2.3217936722459082E-3]
[null,null,110,"Lo Valledor 110 kV - HT3 Transformador TR03 50 MVA 110/12.5 kV","HT3",40,28.856999999999999,0.72142499999999998,28.923999999999999,0.72309999999999997,2.3217936722459082E-3]
[null,null,110,"Lo Valledor 110 kV - HT2 Transformador TR02 25 MVA 110/12.5 kV","HT2",40,28.856999999999999,0.72142499999999998,28.923999999999999,0.72309999999999997,2.3217936722459082E-3]
[null,null,110,"Lo Valledor 110 kV - H2 Línea 110 kV Lo Valledor - Cerro Navia (Enel)/ Chena 2","H2",40,14.429,0.36072500000000002,14.462,0.36154999999999998,2.2870607803728237E-3]
[null,"Lord Cochrane",110,"Lord Cochrane 110 kV - HT1 Transformador TR01 44,7 MVA 110/12.5 kV ","HT1",31.5,48.33,1.5342857142857143,48.503999999999998,1.5398095238095237,3.6002482929857129E-3]
[null,null,110,"Lord Cochrane 110 kV - HT2 Transformador TR02 44,7 MVA 110/12.5 kV ","HT2",31.5,48.33,1.5342857142857143,48.503999999999998,1.5398095238095237,3.6002482929857129E-3]
[null,"Los Almendros",110,"Los Almendros 110 kV -  H1 Línea 110 kV Los Almendros - Los Dominicos/El Salto 1"," H1",40,26.514999999999997,0.66287499999999988,26.574000000000005,0.66435000000000011,2.225155572317864E-3]
[null,null,110,"Los Almendros 110 kV -  H2 Línea 110 kV Los Almendros - El Salto C2"," H2",40,27.236999999999998,0.680925,27.299000000000003,0.68247500000000005,2.2763153063848707E-3]
[null,null,110,"Los Almendros 110 kV -  H3 Línea 110 kV Los Almendros - Florida C1"," H3",40,28.198999999999998,0.70497499999999991,28.273000000000003,0.70682500000000004,2.6242065321467134E-3]
[null,null,110,"Los Almendros 110 kV -  H4 Línea 110 kV Los Almendros - Andes/Florida C2"," H4",40,28.198999999999998,0.70497499999999991,28.273000000000003,0.70682500000000004,2.6242065321467134E-3]
[null,null,110,"Los Almendros 110 kV - HT1 Transformador TR01 400 MVA 220/110 kV","HT1",40,21.706999999999997,0.54267499999999991,21.770000000000003,0.54425000000000012,2.9022895840054336E-3]
[null,"Los Angeles",154,"Los Angeles 154 kV - AT3 Transformador Los Ángeles TR03 56MVA 154/66 kV N°3","AT3",40,5.4039999999999999,0.1351,5.4080000000000004,0.13520000000000001,7.4019245003709242E-4]
[null,null,154,"Los Angeles 154 kV - AT4 Transformador Los Ángeles TR04 56MVA 154/66 kV N°4","AT4",40,4.9989999999999997,0.12497499999999999,5.0030000000000001,0.12507499999999999,8.0016003200649084E-4]
[null,null,154,"Los Angeles 154 kV - A1 Línea 154 kV Los Ángeles - Charrúa","A1","S/I",4.1550000000000002,"F/I",4.1580000000000004,"F/I",7.2202166064984678E-4]
[null,null,154,"Los Angeles 154 kV - A2 Línea 154 kV Los Ángeles - Negrete Cuel /Tap Santa Luisa/Santa Fe","A2",40,6.1150000000000002,0.15287500000000001,6.1189999999999998,0.152975,6.5412919051505473E-4]
[null,"Los Colorados",110,"Los Colorados 110 kV - H1 Transformador TR01 110/13.2 kV ","H1",25,3.0680000000000001,0.12272,3.069,0.12275999999999999,3.2594524119944259E-4]
[null,"Los Dominicos",110,"Los Dominicos 110 kV - H1 Línea 110 kV Los Dominicos - Los Almendros/El Salto 1","H1",40,11.250999999999999,0.281275,11.271000000000001,0.281775,1.7776197671319305E-3]
[null,null,110,"Los Dominicos 110 kV - H2 Línea 110 kV Los Dominicos - Los Almendros/ El Salto 2","H2",40,11.250999999999999,0.281275,11.271000000000003,0.28177500000000005,1.7776197671320886E-3]
[null,"Los Libertadores",110,"Los Libertadores 110 kV - HX1 Línea 110kV TO Libertadores-Libertadores C2","HX1","S/I",14.318,"N/P",14.366,"N/P",3.3524235228383882E-3]
[null,null,110,"Los Libertadores 110 kV - HX2 Línea 110kV TO Libertadores-Libertadores C1","HX2","S/I",14.318,"N/P",14.366,"N/P",3.3524235228383882E-3]
[null,"Los Loros",110,"Los Loros 110 kV - HT1 Transformador T1 20/16/12 MVA 110/24-13,8 kV","HT1",31.5,2.9780000000000002,9.4539682539682549E-2,2.9780000000000002,9.4539682539682549E-2,0]
[null,null,110,"Los Loros 110 kV - H1 Línea 110 kV Los Loros - Central PV Los Loros 1","H1",40,2.5350000000000001,6.3375000000000001E-2,2.5350000000000001,6.3375000000000001E-2,0]
[null,"Los Maquis",110,"Los Maquis 110 kV - H3 Línea 110 kV Los Maquis - Aconcagua/Fundición Chagres 1","H3",40,8.9439999999999991,0.22359999999999997,8.9559999999999995,0.22389999999999999,1.3416815742397648E-3]
[null,null,110,"Los Maquis 110 kV - H4 Línea 110 kV Los Maquis - Aconcagua / Totoralillo / Esperanza (HASA) 2","H4",40,8.7949999999999999,0.21987499999999999,8.8070000000000004,0.22017500000000001,1.3644115974986305E-3]
[null,null,110,"Los Maquis 110 kV - H5 Línea 110 kV Los Maquis - Central Los Quilos 1","H5",40,10.712999999999999,0.26782499999999998,10.728,0.26819999999999999,1.4001680201624726E-3]
[null,null,110,"Los Maquis 110 kV - HS Transformador TR01 95 MVA 220/110/12 kV","HS",40,6.4250000000000007,0.16062500000000002,6.4370000000000003,0.16092500000000001,1.8677042801555743E-3]
[null,"Los Placeres (Placeres)",110,"Los Placeres (Placeres) 110 kV - HT1 Transformador TR1 110/12 kV ","HT1",40,16.303000000000001,0.40757500000000002,16.564,0.41410000000000002,1.6009323437404112E-2]
[null,null,110,"Los Placeres (Placeres) 110 kV - HT2 Transformador TR2 110/12 kV ","HT2",31.5,16.303000000000001,0.51755555555555555,16.564,0.52584126984126989,1.6009323437404112E-2]
[null,"Macul",110,"Macul 110 kV - H1 Línea 110 kV Macul - Ochagavia/Florida 1","H1",40,17.033999999999999,0.42584999999999995,17.071000000000002,0.42677500000000002,2.1721263355643176E-3]
[null,null,110,"Macul 110 kV - H2 Línea 110 kV Macul - Ochagavia/Florida 2","H2",40,17.033999999999999,0.42584999999999995,17.071000000000002,0.42677500000000002,2.1721263355643176E-3]
[null,null,110,"Macul 110 kV - H4 Transformador TR04 50 MVA 110/12.5 kV ","H4",40,34.067,0.85167499999999996,34.140999999999998,0.85352499999999998,2.1721900959872625E-3]
[null,null,110,"Macul 110 kV - H6 Transformador TR06 50 MVA 110/20.4 kV","H6",40,34.067,0.85167499999999996,34.140999999999998,0.85352499999999998,2.1721900959872625E-3]
[null,"Magnetita",110,"Magnetita 110 kV - H7 Transformador TR 28MVA 110/4,16kV","H7",40,4.1989999999999998,0.104975,4.2,0.10500000000000001,2.3815194093839819E-4]
[null,"Maipo",110,"Maipo 110 kV - H1 Línea 110 kV Maipo - Puente Alto (CMPC)/Pirque ","H1",25,2.7039999999999997,0.10815999999999999,2.7039999999999997,0.10815999999999999,0]
[null,"Maipú",110,"Maipú 110 kV - H1 Línea 110 kV Maipu - Cerro Navia (Enel)/Chena 1","H1",40,24.939,0.623475,25.039000000000001,0.62597500000000006,4.0097838726493211E-3]
[null,null,110,"Maipú 110 kV - H2 Línea 110 kV Maipu - Cerro Navia (Enel)/Chena 2","H2",40,24.939,0.623475,25.039000000000001,0.62597500000000006,4.0097838726493211E-3]
[null,"Maitencillo",110,"Maitencillo 110 kV - H1 Línea 110 kV Maitencillo - Pan de Azucar","H1",31.5,11.489000000000001,0.36473015873015874,11.492000000000001,0.36482539682539683,2.6111933153452117E-4]
[null,null,110,"Maitencillo 110 kV - HT2 Transformador ATR2 90 MVA 220/115/13.2 kV","HT2",22,8.4269999999999996,0.38304545454545452,8.4290000000000003,0.38313636363636366,2.3733238400387659E-4]
[null,null,110,"Maitencillo 110 kV - H2 Línea 110 kV Maitencillo - Huasco C2","H2",31.5,11.303000000000001,0.35882539682539683,11.306000000000001,0.35892063492063497,2.6541626116961104E-4]
[null,null,110,"Maitencillo 110 kV - HT1 Transformador ATR1 90 MVA 220/115/13.2 kV","HT1",40,8.5300000000000011,0.21325000000000002,8.532,0.21329999999999999,2.3446658851100719E-4]
[null,null,110,"Maitencillo 110 kV - H3 Línea 110 kV Maitencillo - Huasco 1","H3",31.5,11.316000000000001,0.35923809523809525,11.319000000000001,0.35933333333333334,2.6511134676565162E-4]
[null,null,110,"Maitencillo 110 kV - H4 Línea 110 kV Maitencillo - Vallenar","H4",31.5,11.868,0.3767619047619048,11.871,0.37685714285714289,2.5278058645097012E-4]
[null,null,110,"Maitencillo 110 kV - HTX Transformador 67MVA 110/13.2kV","HTX","S/I",10.06,"N/P",10.063000000000001,"N/P",2.9821073558649241E-4]
[null,null,110,"Maitencillo 110 kV - H5 Línea 110 kV Maitencillo - Cardones/Tap Off Punta Toro","H5",31.5,11.208,0.3558095238095238,11.211,0.35590476190476189,2.6766595289080244E-4]
[null,"Malloco",110,"Malloco 110 kV - HT1 Transformador TR01 22,4 MVA 110/12.5 kV","HT1",31.5,7.3230000000000004,0.23247619047619048,7.327,0.23260317460317459,5.4622422504432052E-4]
[null,null,110,"Malloco 110 kV - HT2 Transformador TR02 22,4 MVA 110/12.5 kV ","HT2",31.5,7.3230000000000004,0.23247619047619048,7.327,0.23260317460317459,5.4622422504432052E-4]
[null,null,110,"Malloco 110 kV - HT3 Transformador TR03 37,5 MVA 110/23.5 kV ","HT3",31.5,7.3230000000000004,0.23247619047619048,7.327,0.23260317460317459,5.4622422504432052E-4]
[null,null,110,"Malloco 110 kV - H4 Transformador TR04 50 MVA 110/23.5 kV ","H4",40,7.3230000000000004,0.18307500000000002,7.327,0.183175,5.4622422504432052E-4]
[null,"Mantilhue",110,"Mantilhue 110 kV - H1 Línea 110 kV Mantilhue - Chirre","H1",40,2.637,6.5924999999999997E-2,2.637,6.5924999999999997E-2,0]
[null,null,110,"Mantilhue 110 kV - H2 Línea 110 kV Mantilhue - Mocho","H2",40,3.0629999999999997,7.657499999999999E-2,3.0640000000000001,7.6600000000000001E-2,3.2647730982707609E-4]
[null,"Mantos de la Luna",110,"Mantos de la Luna 110 kV - H1 Línea 110 kV Mantos de la Luna - Tap Off Barriles ","H1",40,1.119,2.7975E-2,1.121,2.8025000000000001E-2,1.7873100983020571E-3]
[null,"Manto Verde",110,"Manto Verde 110 kV - HT1 Transformador TR1 110/13.8 kV ","HT1","S/I",2.6869999999999998,"F/I",2.6869999999999998,"F/I",0]
[null,null,110,"Manto Verde 110 kV - HT2 Transformador TR2 110/13.8 kV","HT2","S/I",2.6869999999999998,"F/I",2.6869999999999998,"F/I",0]
[null,null,110,"Manto Verde 110 kV - H1 Línea 110 kV Manto Verde - Diego de Almagro","H1",40,2.6869999999999998,6.7174999999999999E-2,2.6869999999999998,6.7174999999999999E-2,0]
[null,null,110,"Manto Verde 110 kV - H2 Línea 110 kV Manto Verde - Planta Bombeo 2/Planta Desaladora y Planta Bombeo 1 ","H2",40,2.6869999999999998,6.7174999999999999E-2,2.6869999999999998,6.7174999999999999E-2,0]
[null,"Mapal",154,"Mapal 154 kV -  AT Transformador TR1 24MVA 154/15kV"," AT",31.5,13.03,0.41365079365079366,13.692,0.43466666666666665,5.0805832693783644E-2]
[null,"Marbella",110,"Marbella 110 kV -  H1 Línea 110 kV Marbella - Casas Viejas C1"," H1",40,2.665,6.6625000000000004E-2,2.6770000000000005,6.6925000000000012E-2,4.5028142589119908E-3]
[null,null,110,"Marbella 110 kV - HT1 Transformador TR1 13 MVA 110/24 kV ","HT1",40,3.9169999999999998,9.7924999999999998E-2,3.93,9.8250000000000004E-2,3.3188664794486459E-3]
[null,null,110,"Marbella 110 kV - H2 Línea 110 kV Marbella - Quillota C1","H2",40,2.665,6.6625000000000004E-2,2.677,6.6924999999999998E-2,4.5028142589118242E-3]
[null,"Marga Marga",110,"Marga Marga 110 kV - HT1 Transformador TR1 115/13.6 kV","HT1",31.5,20.652999999999999,0.6556507936507936,21.606999999999999,0.68593650793650796,4.6191836537064865E-2]
[null,null,110,"Marga Marga 110 kV - HT2 Transformador TR2 115/14.2 kV","HT2",31.5,20.652999999999999,0.6556507936507936,21.606999999999999,0.68593650793650796,4.6191836537064865E-2]
[null,null,110,"Marga Marga 110 kV - HT3 Transformador TR3 115/15.3 kV","HT3",40,20.652999999999999,0.51632499999999992,21.606999999999999,0.54017499999999996,4.6191836537064865E-2]
[null,"Mariscal",110,"Mariscal 110 kV - H1 Línea 110 kV Mariscal - La Pintana/Santa Rosa Sur 2","H1",40,11.78,0.29449999999999998,11.797000000000001,0.29492499999999999,1.4431239388795617E-3]
[null,null,110,"Mariscal 110 kV - H2 Línea 110 kV Mariscal - La Pintana/Santa Rosa Sur 1","H2",40,11.78,0.29449999999999998,11.797000000000001,0.29492499999999999,1.4431239388795617E-3]
[null,null,110,"Mariscal 110 kV - HT1 Transformador TR01 50 MVA 110/12 kV","HT1",40,23.559000000000001,0.58897500000000003,23.594000000000001,0.58984999999999999,1.485631817988885E-3]
[null,null,110,"Mariscal 110 kV - HT2 Transformador TR02 30 MVA 110/23 kV ","HT2",40,23.559000000000001,0.58897500000000003,23.594000000000001,0.58984999999999999,1.485631817988885E-3]
[null,null,110,"Mariscal 110 kV - HT3 Transformador TR03 30 MVA 110/23 kV ","HT3",40,23.559000000000001,0.58897500000000003,23.594000000000001,0.58984999999999999,1.485631817988885E-3]
[null,"Mauco",110,"Mauco 110 kV - HL1 Línea 110 kV Mauco - Torquemada 1","HL1",40,10.196000000000002,0.25490000000000002,10.812000000000001,0.27030000000000004,6.0415849352687283E-2]
[null,null,110,"Mauco 110 kV - HL2 Línea 110 kV Mauco - Torquemada 2","HL2",40,10.196000000000002,0.25490000000000002,10.812000000000001,0.27030000000000004,6.0415849352687283E-2]
[null,null,110,"Mauco 110 kV - HT1 Transformador TR1 110/12 kV ","HT1",40,18.643000000000001,0.46607500000000002,19.876000000000001,0.49690000000000001,6.6137424234297082E-2]
[null,null,110,"Mauco 110 kV - HT2 Transformador TR2110/12 kV ","HT2",40,18.643000000000001,0.46607500000000002,19.876000000000001,0.49690000000000001,6.6137424234297082E-2]
[null,"Maule",154,"Maule 154 kV -  A1 Línea 154kV Maule - Itahue"," A1",40,11.181000000000001,0.27952500000000002,11.189,0.279725,7.1549950809400933E-4]
[null,null,154,"Maule 154 kV -  A2 Línea 154kV Maule - Linares/Yerbas Buenas"," A2",40,12.63,0.31575000000000003,12.638,0.31595000000000001,6.3341250989700068E-4]
[null,null,154,"Maule 154 kV -  AT Interruptor común Trafo 01 y Trafo 02."," AT",31.5,12.822999999999999,0.40707936507936504,12.831,0.40733333333333333,6.2387896748037871E-4]
[null,null,154,"Maule 154 kV - HTX Transformador ATR5 300MVA 220/154/24kV","HTX","S/I",8.27,"N/P",8.2739999999999991,"N/P",4.8367593712207491E-4]
[null,"Mayaca",110,"Mayaca 110 kV - HTX Transformador 30MVA 110/12kV","HTX","S/I",15.826000000000001,"N/P",16.155000000000001,"N/P",2.0788575761405321E-2]
[null,null,110,"Mayaca 110 kV - HX1 Línea 110kV TO Mayaca - Mayaca C1","HX1","S/I",7.9130000000000003,"N/P",8.0779999999999994,"N/P",2.0851762921774188E-2]
[null,null,110,"Mayaca 110 kV - HX2 Línea 110kV TO Mayaca - Mayaca C2","HX2","S/I",7.9130000000000003,"N/P",8.0779999999999994,"N/P",2.0851762921774188E-2]
[null,"MDP Teno (Paneles MDP)",154,"MDP Teno (Paneles MDP) 154 kV - A1 Línea 154 kV MDP Teno - Teno","A1",40,6.9740000000000002,0.17435,6.976,0.1744,2.8677946659016052E-4]
[null,"Mejillones",110,"Mejillones 110 kV - H4 Línea 110 kV Mejillones - Central Diesel Enaex 1","H4",38.4,8.2840000000000007,0.21572916666666669,8.2889999999999997,0.21585937499999999,6.0357315306603146E-4]
[null,null,110,"Mejillones 110 kV - H5 Línea 110 kV Mejillones - Chacaya C1","H5",40,7.394000000000001,0.18485000000000001,7.3979999999999997,0.18495,5.4097917230168662E-4]
[null,null,110,"Mejillones 110 kV - H1 Línea 110 kV Mejillones - Antofagasta/Desalant 1","H1",57.2,6.6840000000000011,0.11685314685314686,6.6879999999999997,0.11692307692307691,5.984440454815486E-4]
[null,null,110,"Mejillones 110 kV - H2 Línea 110 kV Mejillones - El Lince ","H2",31.5,8.33,0.26444444444444443,8.3349999999999991,0.26460317460317456,6.0024009603829595E-4]
[null,null,110,"Mejillones 110 kV - HT Transformador TR01 80/80/20 MVA 220/115/13.8 kV ","HT",16,4.7279999999999998,0.29549999999999998,4.7309999999999999,0.29568749999999999,6.3451776649748606E-4]
[null,null,110,"Mejillones 110 kV - H3/HT2 Transformador TR03 30/25 MVA 110/13.8 kV","H3/HT2",25,7.3120000000000012,0.29248000000000007,7.3170000000000002,0.29268,6.8380743982480909E-4]
[null,"Melipeuco",110,"Melipeuco 110 kV - H1 Línea 110 kV Melipeuco - Río Tolten/Cunco","H1",40,1.1619999999999999,2.9049999999999999E-2,1.1619999999999999,2.9049999999999999E-2,0]
[null,"Melipulli",110,"Melipulli 110 kV - H1 Línea 110 kV Melipulli - Alto Bonito/Central Trapén/Molinos (Enlasa) 1","H1",40,3.8519999999999994,9.6299999999999983E-2,3.8519999999999994,9.6299999999999983E-2,0]
[null,null,110,"Melipulli 110 kV - HT11 Transformador T11 60 MVA 230/115/69 kV","HT11",40,3.1179999999999999,7.7949999999999992E-2,3.1179999999999999,7.7949999999999992E-2,0]
[null,"Metro",110,"Metro 110 kV - ITRA1 Transformador TRA1 110/20 kV ","ITRA1","S/I",48.28,"F/I",48.453000000000003,"F/I",3.5832642916321833E-3]
[null,null,110,"Metro 110 kV - ITRB1 Transformador TRB2 110/20 kV ","ITRB1","S/I",48.28,"F/I",48.453000000000003,"F/I",3.5832642916321833E-3]
[null,null,110,"Metro 110 kV - ITRC1 Transformador TRC1 110/20 kV","ITRC1","S/I",48.28,"F/I",48.453000000000003,"F/I",3.5832642916321833E-3]
[null,"Minera Franke",110,"Minera Franke 110 kV -  En Barra",null,null,1.603,"N/A",1.6040000000000001,"N/A",6.2383031815353208E-4]
[null,"Minera Maricunga",110,"Minera Maricunga 110 kV - 00-BK-101 Transformador  ATR1 110/23 kV","00-BK-101","S/I",1.163,"F/I",1.163,"F/I",0]
[null,null,110,"Minera Maricunga 110 kV - 00-BK-102 Transformador ATR2 110/23 kV N°2","00-BK-102","S/I",1.163,"F/I",1.163,"F/I",0]
[null,"Minera Teck CDA",110,"Minera Teck CDA 110 kV - H1 Transformador TR 12/15 MVA 220/13.2 kV","H1",31.5,3.4359999999999999,0.10907936507936508,3.4369999999999998,0.1091111111111111,2.9103608847493885E-4]
[null,"Minera Valle Central",154,"Minera Valle Central 154 kV - AT1 Transformador TR1 154/4,16kV","AT1",20,10.273999999999999,0.51369999999999993,10.277999999999999,0.51389999999999991,3.8933229511383684E-4]
[null,null,154,"Minera Valle Central 154 kV - AT2 Transformador TR2 154/4,16kV","AT2",20,10.273999999999999,0.51369999999999993,10.277999999999999,0.51389999999999991,3.8933229511383684E-4]
[null,null,154,"Minera Valle Central 154 kV - AT3 Transformador 154/23 kV N°3 ","AT3",20,10.426,0.52129999999999999,10.43,0.52149999999999996,3.8365624400532892E-4]
[null,"Minero",110,"Minero 110 kV - H1 Línea 110 kV Minero - Colón 1","H1",40,21.463999999999999,0.53659999999999997,21.475999999999999,0.53689999999999993,5.5907566157288742E-4]
[null,null,110,"Minero 110 kV - H2 Línea 110 kV Minero - Colón 2","H2",40,21.463999999999999,0.53659999999999997,21.475999999999999,0.53689999999999993,5.5907566157288742E-4]
[null,null,110,"Minero 110 kV - H3 Línea 110 kV Minero - Cordillera 1","H3",40,21.463999999999999,0.53659999999999997,21.475999999999999,0.53689999999999993,5.5907566157288742E-4]
[null,null,110,"Minero 110 kV - H4 Línea 110 kV Minero - Cordillera 2","H4",40,21.463999999999999,0.53659999999999997,21.475999999999999,0.53689999999999993,5.5907566157288742E-4]
[null,null,110,"Minero 110 kV - H5 Línea 110 kV Minero - Sauzal 3","H5",40,19.196999999999999,0.47992499999999999,19.207999999999998,0.48019999999999996,5.7300619888520251E-4]
[null,null,110,"Minero 110 kV - H6 Línea 110 kV Minero - Interconexión Chacayes/Sauzal 1","H6",40,18.954000000000001,0.47384999999999999,18.965,0.47412500000000002,5.8035243220424355E-4]
[null,null,110,"Minero 110 kV - H7 Línea 110 kV Minero - Interconexión Chacayes/Sauzal 2","H7",40,18.954000000000001,0.47384999999999999,18.965,0.47412500000000002,5.8035243220424355E-4]
[null,null,110,"Minero 110 kV - H8 Línea 110 kV Minero -  Sewell 1","H8",40,21.463999999999999,0.53659999999999997,21.475999999999999,0.53689999999999993,5.5907566157288742E-4]
[null,null,110,"Minero 110 kV - H9 Línea 110 kV Minero -  Sewell 2","H9",40,21.463999999999999,0.53659999999999997,21.475999999999999,0.53689999999999993,5.5907566157288742E-4]
[null,null,110,"Minero 110 kV - HR Paño Acoplador ","HR",40,21.463999999999999,0.53659999999999997,21.475999999999999,0.53689999999999993,5.5907566157288742E-4]
[null,null,110,"Minero 110 kV - HT1 Transformador  TR1 230/115/13.8 kV ","HT1",40,16.715999999999998,0.41789999999999994,16.724999999999998,0.41812499999999997,5.3840631730081015E-4]
[null,null,110,"Minero 110 kV - HT2 Transformador  TR2 230/115/13.8 kV ","HT2",40,16.715999999999998,0.41789999999999994,16.724999999999998,0.41812499999999997,5.3840631730081015E-4]
[null,null,110,"Minero 110 kV - HT3 Transformador  TR3  230/115/13.8 kV ","HT3",40,16.715999999999998,0.41789999999999994,16.724999999999998,0.41812499999999997,5.3840631730081015E-4]
[null,null,110,"Minero 110 kV - H10 Línea 110 kV Minero - El Cobre (Codelco) 1","H10",40,21.463999999999999,0.53659999999999997,21.475999999999999,0.53689999999999993,5.5907566157288742E-4]
[null,null,110,"Minero 110 kV - H11 Línea 110 kV Minero - El Cobre (Codelco) 2","H11",40,21.463999999999999,0.53659999999999997,21.475999999999999,0.53689999999999993,5.5907566157288742E-4]
[null,"Minsal",110,"Minsal 110 kV - H1 Transformador TR01 25/20 MVA 110/23 kV ","H1",40,1.36,3.4000000000000002E-2,1.36,3.4000000000000002E-2,0]
[null,null,110,"Minsal 110 kV - H2 Transformador TR02 30 MVA 110/23 kV","H2","S/I",1.36,"F/I",1.36,"F/I",0]
[null,"Miraflores",110,"Miraflores 110 kV - H3 Línea 110 kV Miraflores - San Pedro (AES GENER) 1","H3",25,20.734000000000002,0.8293600000000001,21.827999999999999,0.87312000000000001,5.276357673386696E-2]
[null,null,110,"Miraflores 110 kV - H4 Línea 110 kV Miraflores - San Pedro (AES GENER) 2","H4",25,20.734000000000002,0.8293600000000001,21.827999999999999,0.87312000000000001,5.276357673386696E-2]
[null,null,110,"Miraflores 110 kV - H5 Línea 110 kV Miraflores - Agua Santa 3","H5",25,18.98,0.75919999999999999,20.298000000000002,0.81192000000000009,6.944151738672294E-2]
[null,null,110,"Miraflores 110 kV - H6 Línea 110 kV Miraflores - Agua Santa 4","H6",20,18.98,0.94900000000000007,20.298000000000002,1.0149000000000001,6.944151738672294E-2]
[null,null,110,"Miraflores 110 kV - HS Paño Acoplador ","HS",40,24.66,0.61650000000000005,26.044,0.65110000000000001,5.6123276561232782E-2]
[null,null,110,"Miraflores 110 kV - HT1 Transformador TR1 110/12 kV ","HT1",20,24.66,1.2330000000000001,26.044,1.3022,5.6123276561232782E-2]
[null,null,110,"Miraflores 110 kV - HT2 Transformador TR2 110/12 kV ","HT2",25,24.66,0.98640000000000005,26.044,1.04176,5.6123276561232782E-2]
[null,null,110,"Miraflores 110 kV - HT3 Transformador TR3 110/13.6 kV","HT3",20,24.66,1.2330000000000001,26.044,1.3022,5.6123276561232782E-2]
[null,null,110,"Miraflores 110 kV - H1 Línea 110 kV Miraflores - Ventanas/Torquemada 1","H1",40,21.817,0.54542500000000005,22.853999999999999,0.57135000000000002,4.7531741302653849E-2]
[null,null,110,"Miraflores 110 kV - H2 Línea 110 kV Miraflores - Ventanas/Torquemada 2","H2",40,21.817,0.54542500000000005,22.853999999999999,0.57135000000000002,4.7531741302653849E-2]
[null,null,110,"Miraflores 110 kV - H10 Línea 110 kV Miraflores -  Marga Marga 1","H10",31.5,24.66,0.78285714285714281,26.044,0.82679365079365086,5.6123276561232782E-2]
[null,null,110,"Miraflores 110 kV - H11 Línea 110 kV Miraflores -  Marga Marga 2","H11",40,24.66,0.61650000000000005,26.044,0.65110000000000001,5.6123276561232782E-2]
[null,"Mocho",110,"Mocho 110 kV - H1 Línea 110 kV Mocho - Mantilhue","H1",40,2.4430000000000001,6.1075000000000004E-2,2.4430000000000001,6.1075000000000004E-2,0]
[null,"Molinos (Enlasa)",110,"Molinos (Enlasa) 110 kV - HT Transformador TR1 100/80 MVA 110/23 kV ","HT",40,3.2439999999999998,8.1099999999999992E-2,3.2439999999999998,8.1099999999999992E-2,0]
[null,null,110,"Molinos (Enlasa) 110 kV - H1 Línea 110 kV Molinos (Enlasa) - Alto Bonito 1","H1",50,2.6359999999999997,5.2719999999999996E-2,2.6349999999999998,5.2699999999999997E-2,-3.7936267071316009E-4]
[null,null,110,"Molinos (Enlasa) 110 kV - H2 Línea 110 kV Molinos (Enlasa) -  El Empalme 1","H2",40,3.6109999999999998,9.0274999999999994E-2,3.6109999999999998,9.0274999999999994E-2,0]
[null,"Monterrico",154,"Monterrico 154 kV - A1 Línea 154kV Monterrico - Parral","A1",40,4.8209999999999997,0.12052499999999999,4.8239999999999998,0.1206,6.2227753578098194E-4]
[null,null,154,"Monterrico 154 kV - AX Línea 154kV Monterrico - Pueblo Seco","AX","S/I",3.758,"N/P",3.76,"N/P",5.3219797764762636E-4]
[null,null,154,"Monterrico 154 kV - ATX Transformador TR2 60/75 MVA 154/66/13,2kV","ATX","S/I",5.5579999999999998,"N/P",5.5629999999999997,"N/P",8.9960417416334892E-4]
[null,null,154,"Monterrico 154 kV - AT1 Transformador TR1 75MVA 154/66/13,2kV","AT1",40,5.5579999999999998,0.13894999999999999,5.5629999999999997,0.139075,8.9960417416334892E-4]
[null,"Muelle",110,"Muelle 110 kV - H1 Línea 110 kV Muelle - Chacaya C1","H1","S/I",1.7170000000000001,"F/I",1.718,"F/I",5.8241118229463589E-4]
[null,null,110,"Muelle 110 kV - H4 Línea 110 kV Muelle - Tap Off Antucoya/Tap Off Licancabur/Tap Off Sairecabur 1","H4","S/I",1.7169999999999999,"F/I",1.7170000000000001,"F/I",1.2932126087654708E-16]
[null,null,110,"Muelle 110 kV - H2 Transformador Muelle 110/24 kV N°1","H2","S/I",2.2229999999999999,"F/I",2.2240000000000002,"F/I",4.4984255510586323E-4]
[null,"Ochagavia",110,"Ochagavia 110 kV - H1 Línea 110 kV Ochagavia - Metro 1","H1",31.5,28.732999999999997,0.91215873015873006,28.834,0.91536507936507938,3.5151219851739341E-3]
[null,null,110,"Ochagavia 110 kV - H2 Línea 110 kV Ochagavia - Florida 2","H2",31.5,43.936999999999998,1.3948253968253967,44.099000000000004,1.3999682539682541,3.6870974349638378E-3]
[null,null,110,"Ochagavia 110 kV - H3 Línea 110 kV Ochagavia - Florida 1","H3",40,43.936999999999998,1.098425,44.099000000000004,1.1024750000000001,3.6870974349638378E-3]
[null,null,110,"Ochagavia 110 kV - H4 Línea 110 kV Ochagavia - Chena 1","H4",40,38.837999999999994,0.97094999999999987,38.975000000000001,0.97437499999999999,3.5274730933623662E-3]
[null,null,110,"Ochagavia 110 kV - H5 Línea 110 kV Ochagavia - Chena 2","H5",31.5,38.837999999999994,1.2329523809523808,38.975000000000001,1.2373015873015873,3.5274730933623662E-3]
[null,null,110,"Ochagavia 110 kV - HT1 Transformador TR01 40 MVA 105/12 kV ","HT1",40,48.595999999999997,1.2148999999999999,48.771000000000001,1.2192750000000001,3.6011194336983349E-3]
[null,null,110,"Ochagavia 110 kV - AC1 Banco de Condensadores 1 ","AC1",40,48.595999999999997,1.2148999999999999,48.771000000000001,1.2192750000000001,3.6011194336983349E-3]
[null,null,110,"Ochagavia 110 kV - HT2 Transformador TR02 50 MVA  110/12.5 kV ","HT2",40,48.595999999999997,1.2148999999999999,48.771000000000001,1.2192750000000001,3.6011194336983349E-3]
[null,"Ovalle",110,"Ovalle 110 kV - H2 Línea 110 kV Ovalle -  La Ruca C2","H2",40,3.4949999999999997,8.7374999999999994E-2,3.4949999999999997,8.7374999999999994E-2,0]
[null,null,110,"Ovalle 110 kV - HT3 Transformador TR03 30 MVA 110/66/23 kV","HT3",40,4.58,0.1145,4.58,0.1145,0]
[null,null,110,"Ovalle 110 kV - H1 Línea 110 kV Ovalle - Punitaqui 1","H1",40,3.8849999999999998,9.7124999999999989E-2,3.8849999999999998,9.7124999999999989E-2,0]
[null,null,110,"Ovalle 110 kV - HT4 Transformador TR 04 60 MVA 110/69/23 kV ","HT4",40,4.6920000000000002,0.1173,4.6929999999999996,0.11732499999999998,2.1312872975265255E-4]
[null,null,110,"Ovalle 110 kV - H3 Línea 110 kV Ovalle -  La Ruca C1","H3",31.5,3.4979999999999993,0.11104761904761902,3.4969999999999999,0.11101587301587301,-2.85877644368052E-4]
[null,"Oxy",154,"Oxy 154 kV - A Transformador 154/69/13.8 kV N°1 ; Transformador 154/69/13.8 kV N°2","A",31.5,14.551,0.46193650793650792,14.965,0.4750793650793651,2.8451652807367171E-2]
[null,"Pacífico",110,"Pacífico 110 kV - HT1 Transformador TRAFO 33/25 MVA 110/13.8 kV ","HT1","S/I",3.3340000000000001,"F/I",3.4929999999999999,"F/I",4.7690461907618414E-2]
[null,"Padre Hurtado",110,"Padre Hurtado 110 kV - HTX Transformador TR01 30 MVA 110/23 kV","HTX","S/I",17.077000000000002,"N/P",17.100000000000001,"N/P",1.346840779996468E-3]
[null,null,110,"Padre Hurtado 110 kV - HX Línea 110 kV Padre Hurtado - Santa Marta","HX","S/I",17.077000000000002,"N/P",17.100000000000001,"N/P",1.346840779996468E-3]
[null,"Paine",154,"Paine 154 kV - AT Transformador TR1 56MVA 154/66/13,2kV","AT",40,11.858000000000001,0.29644999999999999,11.868,0.29670000000000002,8.4331253162420194E-4]
[null,"Pajaritos",110,"Pajaritos 110 kV - H1 Línea 110 kV Pajaritos - Cerro Navia (Enel)/ Chena 1","H1",40,17.356999999999999,0.43392500000000001,17.405999999999999,0.43514999999999998,2.8230685026213913E-3]
[null,null,110,"Pajaritos 110 kV - H2 Línea 110 kV Pajaritos - Cerro Navia (Enel)/Chena 2","H2",40,17.356999999999999,0.43392500000000001,17.405999999999999,0.43514999999999998,2.8230685026213913E-3]
[null,null,110,"Pajaritos 110 kV - HT1 Transformador Pajaritos 110/12.5 kV N°1","HT1",31.5,34.713999999999999,1.1020317460317459,34.811999999999998,1.105142857142857,2.8230685026213913E-3]
[null,null,110,"Pajaritos 110 kV - HT2 Transformador Pajaritos 110/12.5 kV N°2","HT2",40,34.713999999999999,0.86785000000000001,34.811999999999998,0.87029999999999996,2.8230685026213913E-3]
[null,null,110,"Pajaritos 110 kV - HT3 Transformador Pajaritos 110/23.5 kV N°3","HT3",40,34.713999999999999,0.86785000000000001,34.811999999999998,0.87029999999999996,2.8230685026213913E-3]
[null,null,110,"Pajaritos 110 kV - H4 Transformador Pajaritos 110/23.5 kV N°4","H4",40,34.713999999999999,0.86785000000000001,34.811999999999998,0.87029999999999996,2.8230685026213913E-3]
[null,"Pajonales (Infotécnica interna)",110,"Pajonales (Infotécnica interna) 110 kV -  En Barra",null,null,2.6880000000000002,"N/A",2.6880000000000002,"N/A",0]
[null,"Palafitos",110,"Palafitos 110 kV - HT1 Transformador Trafo1 25/33MVA 110/13,8 kV","HT1","S/I",3.0139999999999998,"F/I",3.1440000000000001,"F/I",4.3132050431320616E-2]
[null,"Palmar",110,"Palmar 110 kV - HT1 Transformador 15MVA 110/13.2kV T1","HT1",40,2.633,6.5824999999999995E-2,2.633,6.5824999999999995E-2,0]
[null,null,110,"Palmar 110 kV - HT2 Transformador 15MVA 110/13.2kVT2","HT2",40,2.633,6.5824999999999995E-2,2.633,6.5824999999999995E-2,0]
[null,null,110,"Palmar 110 kV - H1 Línea 110kV PALMAR - COPIHUES","H1",40,2.5070000000000001,6.2675000000000008E-2,2.5070000000000001,6.2675000000000008E-2,0]
[null,"Pan de Azúcar",110,"Pan de Azúcar 110 kV - HT4 Transformador 150 MVA 220/110/13,2kV ATR4  ","HT4",31,15.209999999999999,0.49064516129032254,15.219000000000001,0.4909354838709678,5.9171597633150017E-4]
[null,null,110,"Pan de Azúcar 110 kV - HT1 Transformador TR01 48MVA 110/110kV","HT1",28,15.434999999999999,0.55124999999999991,15.445,0.55160714285714285,6.4787819889870844E-4]
[null,null,110,"Pan de Azúcar 110 kV - HT3 Transformador ATR3 75MVA 220/110/13,2kV y ATR9 90 MVA 220/110/13.2 kV","HT3",40,15.082999999999998,0.37707499999999994,15.091999999999999,0.37729999999999997,5.9669826957504089E-4]
[null,null,110,"Pan de Azúcar 110 kV - H2 Línea 110 kV Pan de Azucar - Maitencillo - Las Compañias C1","H2",40,18.878,0.47194999999999998,18.89,0.47225,6.3566055726244595E-4]
[null,null,110,"Pan de Azúcar 110 kV - HT7 Transformador TR7 35MVA 110/110kV","HT7",28,19.452999999999999,0.69474999999999998,19.465,0.69517857142857142,6.1687143371204724E-4]
[null,null,110,"Pan de Azúcar 110 kV - H1 Línea 110 kV Pan de Azucar - Ovalle (El Peñon)","H1",31.5,18.299999999999997,0.58095238095238089,18.312999999999999,0.58136507936507931,7.1038251366129391E-4]
[null,null,110,"Pan de Azúcar 110 kV - H6 Línea 110 kV Pan de Azucar - San Joaquin","H6",40,19.456,0.4864,19.468,0.48670000000000002,6.1677631578949707E-4]
[null,null,110,"Pan de Azúcar 110 kV - HT2 Transformador T10 60MVA 110/66/23kV TR2 60 MVA 110/66/23 kV","HT2",31.5,19.308,0.61295238095238092,19.32,0.6133333333333334,6.2150403977628214E-4]
[null,null,110,"Pan de Azúcar 110 kV - HT10 Transformador 220/110/13.2 kV N°10","HT10",50,15.093,0.30186000000000002,15.102,0.30204000000000003,5.9630292188433986E-4]
[null,null,110,"Pan de Azúcar 110 kV - H8 Línea 110 kV Pan de Azucar - El Peñon C2","H8",40,18.299999999999997,0.45749999999999991,18.312999999999999,0.45782499999999998,7.1038251366129391E-4]
[null,null,110,"Pan de Azúcar 110 kV - HT8/11 TR8 - TR11","HT8/11",31.5,19.456,0.61765079365079367,19.468,0.61803174603174604,6.1677631578949707E-4]
[null,null,110,"Pan de Azúcar 110 kV - HT11 Transformador TR11 24MVA 110/13,8kV","HT11",40,19.456,0.4864,19.468,0.48670000000000002,6.1677631578949707E-4]
[null,null,110,"Pan de Azúcar 110 kV - HT8 Transformador TR8 24MVA 110/13,8kV","HT8",40,19.456,0.4864,19.468,0.48670000000000002,6.1677631578949707E-4]
[null,"Panamericana",110,"Panamericana 110 kV - HT1 Transformador TR01 25MVA 110/13,2kV","HT1",31.5,51.774999999999999,1.6436507936507936,51.984000000000002,1.6502857142857144,4.0366972477064835E-3]
[null,null,110,"Panamericana 110 kV - HT2 Transformador TR02 22,4MVA 110/12,5kV","HT2",31.5,51.774999999999999,1.6436507936507936,51.984000000000002,1.6502857142857144,4.0366972477064835E-3]
[null,null,110,"Panamericana 110 kV - H4 Transformador TR04 22,4MVA 110/12,5kV","H4",40,51.774999999999999,1.2943750000000001,51.984000000000002,1.2996000000000001,4.0366972477064835E-3]
[null,"Pargua",110,"Pargua 110 kV - HTX Transformador 60 MVA 230/115/13.8 kV","HTX","S/I",2.68,"N/P",2.68,"N/P",0]
[null,null,110,"Pargua 110 kV - HX1 Línea 110 kV Colaco-Pargua","HX1","S/I",3.294,"N/P",3.294,"N/P",0]
[null,null,110,"Pargua 110 kV - HX2 Línea 110kV Pargua - Ancud 110 kV","HX2","S/I",4.4130000000000003,"N/P",4.4130000000000003,"N/P",0]
[null,"Parral",154,"Parral 154 kV - A2 Línea 154kV Parral  - Monterrico","A2","S/I",7.4159999999999995,"F/I",7.4200000000000008,"F/I",5.3937432578227292E-4]
[null,null,154,"Parral 154 kV - A1 Línea 154kV Parral  - Itahue/Linares","A1","S/I",7.0410000000000004,"F/I",7.0449999999999999,"F/I",5.6810112199965333E-4]
[null,null,154,"Parral 154 kV - AT1 Transformador TR1 75MVA 154/66/13,2kV","AT1",40,5.5270000000000001,0.13817499999999999,5.53,0.13825000000000001,5.4278994029312712E-4]
[null,null,154,"Parral 154 kV - AT2 Transformador TR2 56/56/22,4MVA 154/66/13,2kV","AT2",40,8.4960000000000004,0.21240000000000001,8.5,0.21249999999999999,4.7080979284363925E-4]
[null,"Pellets",110,"Pellets 110 kV - H1 Línea 110 kV Pellets - Central Huasco C1","H1",40,3.2639999999999998,8.1599999999999992E-2,3.2639999999999998,8.1599999999999992E-2,0]
[null,null,110,"Pellets 110 kV - H2 Línea 110 kV Pellets - Central Huasco C2","H2",40,3.2639999999999998,8.1599999999999992E-2,3.2639999999999998,8.1599999999999992E-2,0]
[null,"Peñablanca",110,"Peñablanca 110 kV - H1 Línea 110 kV Peñablanca - San Pedro C2","H1",40,6.1909999999999998,0.154775,6.3240000000000007,0.15810000000000002,2.1482797609433193E-2]
[null,null,110,"Peñablanca 110 kV - H2 Línea 110 kV Peñablanca - Miraflores C1","H2",40,6.1959999999999997,0.15489999999999998,6.3289999999999997,0.158225,2.1465461588121369E-2]
[null,null,110,"Peñablanca 110 kV - HT2 Transformador TR2 25MVA110/12,5 kV ","HT2",40,11.484,0.28710000000000002,11.742000000000001,0.29355000000000003,2.2466039707419096E-2]
[null,"Petrodow",154,"Petrodow 154 kV - CT Transformador Petrodow 154/4.16 kV","CT",16,13.787000000000001,0.86168750000000005,14.157999999999999,0.88487499999999997,2.6909407412780056E-2]
[null,"Pid Pid",110,"Pid Pid 110 kV - H1 Línea 110 kV Pid Pid - Gamboa","H1",25,3.2749999999999999,0.13100000000000001,3.2749999999999999,0.13100000000000001,0]
[null,null,110,"Pid Pid 110 kV - HT1 Transformador TR1 16MVA115/69/24/13.8 kV","HT1",40,4.7430000000000003,0.11857500000000001,4.7439999999999998,0.1186,2.1083702298111865E-4]
[null,null,110,"Pid Pid 110 kV - H2 Línea 110 kV Pid Pid - Chiloe/ Dalcahue ","H2",40,3.2640000000000002,8.1600000000000006E-2,3.2640000000000002,8.1600000000000006E-2,0]
[null,"Pirque",110,"Pirque 110 kV - HX1 Línea 110 kV Pirque - CMPC Puente Alto","HX1","S/I",2.0790000000000002,"N/P",2.08,"N/P",4.81000481000428E-4]
[null,null,110,"Pirque 110 kV - HX2 Línea 110 kV Pirque - Maipo","HX2","S/I",2.081,"N/P",2.081,"N/P",0]
[null,null,110,"Pirque 110 kV - HTX Transformador TR2 4/5MVA 110/13.2 kV ","HTX","S/I",3.472,"N/P",3.472,"N/P",0]
[null,null,110,"Pirque 110 kV - HT Transformador TR1 3.75/4.2/5.2MVA 110/13.2 kV ","HT",40,3.472,8.6800000000000002E-2,3.472,8.6800000000000002E-2,0]
[null,"Placilla",110,"Placilla 110 kV - HX1 Línea 110 kV Placilla - Agua Santa","HX1","S/I",11.308,"N/P",11.567,"N/P",2.2904138662893557E-2]
[null,null,110,"Placilla 110 kV - HX2 Línea 110 kV Agua Santa - Placilla C2 ","HX2","S/I",11.162000000000001,"N/P",11.422000000000001,"N/P",2.3293316609926517E-2]
[null,null,110,"Placilla 110 kV - HT2 Transformador TR2 30MVA 110/12kV ","HT2",40,20.358000000000001,0.50895000000000001,20.833000000000002,0.52082500000000009,2.3332350918557884E-2]
[null,"Planta de Óxidos",110,"Planta de Óxidos 110 kV - HT1 Transformador ATR1 4MVA 110/33 kV N°1","HT1","S/I",1.4450000000000001,"F/I",1.4450000000000001,"F/I",0]
[null,null,110,"Planta de Óxidos 110 kV - H2 Línea 110 kV Planta de Oxidos - Las Luces","H2","S/I",1.4450000000000001,"F/I",1.4450000000000001,"F/I",0]
[null,"Planta Matta ",110,"Planta Matta  110 kV - HT TR - Cardones","HT",31.5,4.4059999999999997,0.13987301587301587,4.4059999999999997,0.13987301587301587,0]
[null,"Plantas",110,"Plantas 110 kV - HT1 Transformador T1 16-20-24MVA 110-24/13,8kV","HT1",40,7.8369999999999997,0.19592499999999999,7.84,0.19600000000000001,3.8279954064056576E-4]
[null,null,110,"Plantas 110 kV - HTX Transformador 150MVA 220/110/13,8 kV","HTX","S/I",4.7469999999999999,"N/P",4.7480000000000002,"N/P",2.1065936380879166E-4]
[null,null,110,"Plantas 110 kV - HX Línea 110 kV Plantas - Tierra Amarilla","HX","S/I",4.6660000000000004,"N/P",4.6679999999999993,"N/P",4.2863266180859222E-4]
[null,"Playa Ancha",110,"Playa Ancha 110 kV - HT1 Transformador TR1 22,4MVA 110/12 kV N°1","HT1",40,14.333,0.358325,14.500999999999999,0.36252499999999999,1.1721202818670151E-2]
[null,null,110,"Playa Ancha 110 kV - HT2 Transformador TR2 22,4MVA 110/12 kV N°2","HT2",40,14.333,0.358325,14.500999999999999,0.36252499999999999,1.1721202818670151E-2]
[null,"Portezuelo",110,"Portezuelo 110 kV - H1 Línea 110kV Litueche - Portezuelo","H1",40,2.5409999999999999,6.3524999999999998E-2,2.5430000000000001,6.3575000000000007E-2,7.8709169618269338E-4]
[null,null,110,"Portezuelo 110 kV - HT2 Transformador TR2 15/18MVA 110/66/13.8 kV N°2","HT2",40,3.9490000000000003,9.8725000000000007E-2,3.95,9.8750000000000004E-2,2.5322866548490501E-4]
[null,null,110,"Portezuelo 110 kV - HT1 Transformador TR1 75 MVA 110/66/13.8 kV N°1","HT1","S/I",3.2720000000000002,"F/I",3.2729999999999997,"F/I",3.0562347188247118E-4]
[null,"Potrerillos",110,"Potrerillos 110 kV -  H3 Línea 110 kV Potrerillos - Llanta 1/ Diego de Almagro 1"," H3",14.6,1.859,0.12732876712328767,1.859,0.12732876712328767,0]
[null,null,110,"Potrerillos 110 kV - H2 Línea 110 kV Potrerillos - Llanta 2/ Diego de Almagro 2","H2",14.6,1.8589999999999998,0.12732876712328767,1.8589999999999998,0.12732876712328767,0]
[null,null,110,"Potrerillos 110 kV - HT1 Transformador TR01 110/12/2.1 kV N°1","HT1",14.6,3.3889999999999998,0.23212328767123286,3.3889999999999998,0.23212328767123286,0]
[null,null,110,"Potrerillos 110 kV - HT2 Transformador TR02 110/12/2.1 kV N°2","HT2",14.6,3.3889999999999998,0.23212328767123286,3.3889999999999998,0.23212328767123286,0]
[null,"Pozo Almonte",110,"Pozo Almonte 110 kV - H1 Línea 110 kV Pozo Almonte - Tap Off Cerro Balcón","H1",31.5,5.5759999999999996,0.17701587301587302,5.8180000000000005,0.18469841269841272,4.3400286944046074E-2]
[null,null,110,"Pozo Almonte 110 kV - H2 Línea 110 kV Pozo Almonte - Cerro Colorado ","H2",40,5.8549999999999995,0.14637499999999998,6.1059999999999999,0.15265000000000001,4.2869342442357017E-2]
[null,null,110,"Pozo Almonte 110 kV - H3 Línea 110 kV Pozo Almonte - Cerro Colorado ","H3",31.5,5.8549999999999995,0.18587301587301586,6.1059999999999999,0.19384126984126984,4.2869342442357017E-2]
[null,null,110,"Pozo Almonte 110 kV - HT2 Transformador ATR 2 100/100/25MVA 220/115/13.8 kV","HT2",31.5,3.2820000000000005,0.10419047619047621,3.4050000000000002,0.10809523809523811,3.7477148080438685E-2]
[null,null,110,"Pozo Almonte 110 kV - HT1 Transformador ATR1 90MVA 110/66/13.8  kV ","HT1",31.5,5.3959999999999999,0.17130158730158729,5.641,0.17907936507936509,4.5404002965159396E-2]
[null,null,110,"Pozo Almonte 110 kV - HTX Transformador 30MVA 110/23kV","HTX","S/I",5.8559999999999999,"N/P",6.1070000000000002,"N/P",4.2862021857923552E-2]
[null,null,110,"Pozo Almonte 110 kV - HT5 Transformador ATR 5 100/100/25MVA 220/115/13.8 kV N°5","HT5",31.5,3.3420000000000005,0.10609523809523812,3.4579999999999997,0.10977777777777777,3.4709754637941112E-2]
[null,"Pudahuel",110,"Pudahuel 110 kV - HT1 Transformador TR01 22,4MVA 110/12.5 kV N°1","HT1",50,63.709000000000003,1.2741800000000001,63.963999999999999,1.27928,4.0025742045864078E-3]
[null,null,110,"Pudahuel 110 kV - HT2 Transformador TR02 22,4MVA 110/12.5 kV N°2","HT2",50,63.709000000000003,1.2741800000000001,63.963999999999999,1.27928,4.0025742045864078E-3]
[null,null,110,"Pudahuel 110 kV - HT3 Transformador TR03 20MVA 110/12.5 kV N°3","HT3",50,63.709000000000003,1.2741800000000001,63.963999999999999,1.27928,4.0025742045864078E-3]
[null,"Puente Alto (CMPC)",110,"Puente Alto (CMPC) 110 kV - A-1 Línea 110 kV Puente Alto - Pirque C1","A-1",40,1.911,4.7774999999999998E-2,1.911,4.7774999999999998E-2,0]
[null,null,110,"Puente Alto (CMPC) 110 kV - H-T3 Transformador TR3 45/60MVA 110/11.5 kV","H-T3",40,1.9029999999999998,4.7574999999999992E-2,1.9040000000000001,4.7600000000000003E-2,5.2548607461919811E-4]
[null,"Puente Alto (EEPA)",110,"Puente Alto (EEPA) 110 kV - H2 Línea 100 kV Puente Alto - Costanera","H2",31.5,9.5760000000000005,0.30399999999999999,9.5790000000000006,0.30409523809523814,3.1328320802006198E-4]
[null,null,110,"Puente Alto (EEPA) 110 kV - H3 Línea 110 kV Puente Alto - Central Puntilla","H3",40,9.229000000000001,0.23072500000000001,9.2320000000000011,0.23080000000000003,3.2506230360820383E-4]
[null,null,110,"Puente Alto (EEPA) 110 kV - H1 Línea 110 kV Puente Alto - Las Vizcachas","H1",40,9.2609999999999992,0.23152499999999998,9.2639999999999993,0.23159999999999997,3.2393909944931584E-4]
[null,"Punitaqui",110,"Punitaqui 110 kV - HT2 Transformador T2 20MVA 110/13,2kV","HT2",31.5,3.5739999999999998,0.11346031746031746,3.5739999999999998,0.11346031746031746,0]
[null,"Punta de Cortés",154,"Punta de Cortés 154 kV - A2 Línea 154 kV Punta de Cortés - Tinguiririca 1/Tap Tilcoco C1","A2",40,18.350999999999999,0.45877499999999999,18.366,0.45915,8.1739414745793523E-4]
[null,null,154,"Punta de Cortés 154 kV - A3 Línea 154 kV Punta de Cortés - Tinguiririca 2/Tap Tilcoco C2","A3",40,18.350999999999999,0.45877499999999999,18.366,0.45915,8.1739414745793523E-4]
[null,null,154,"Punta de Cortés 154 kV - AX3 Línea 154 kV Tap Punta de Cortés - Alto Jahuel / Rancagua C1","AX3","S/I",17.634,"N/P",17.647000000000002,"N/P",7.3721220369749778E-4]
[null,null,154,"Punta de Cortés 154 kV - AX4 Línea 154 kV Tap Punta de Cortés - Alto Jahuel /Rancagua C2","AX4","S/I",17.640999999999998,"N/P",17.655000000000001,"N/P",7.9360580465976424E-4]
[null,null,154,"Punta de Cortés 154 kV - AT Acoplador","AT","S/I",19.899000000000001,"F/I",18.915000000000003,"F/I",-4.9449721091512043E-2]
[null,null,154,"Punta de Cortés 154 kV - AT1 Transformador TR1 56MVA 154/69/13,8kV","AT1",40,20.126000000000001,0.50314999999999999,20.142000000000003,0.50355000000000005,7.9499155321483602E-4]
[null,null,154,"Punta de Cortés 154 kV - AT2 Transformador TR2 36/48/60MVA 154/69/13,8kV","AT2",40,19.864000000000001,0.49660000000000004,19.879000000000001,0.49697500000000006,7.5513491743861095E-4]
[null,null,154,"Punta de Cortés 154 kV - A1 Transformador TR3 60/75MVA 154/69/14,8kV","A1",40,19.829000000000001,0.49572500000000003,19.844000000000001,0.49610000000000004,7.5646779968735532E-4]
[null,null,154,"Punta de Cortés 154 kV - ATX Transformador 300MVA 220/154kV","ATX","S/I",11.745000000000001,"N/P",11.754999999999999,"N/P",8.5142613878229118E-4]
[null,"Punta Padrones",110,"Punta Padrones 110 kV - H1 Línea 110kV Caldera - Punta Padrones","H1",40,2.0489999999999999,5.1225E-2,2.0489999999999999,5.1225E-2,0]
[null,"Punta Peuco (Cemento Polpaico)",110,"Punta Peuco (Cemento Polpaico) 110 kV - HT1 Transformador TR1 15/22MVA110/44kV","HT1",31.5,14.397,0.45704761904761904,14.452,0.45879365079365081,3.8202403278460592E-3]
[null,null,110,"Punta Peuco (Cemento Polpaico) 110 kV - HT2 Transformador TR2 20MVA110/44kV","HT2",31.5,14.397,0.45704761904761904,14.452,0.45879365079365081,3.8202403278460592E-3]
[null,"Quelentaro",110,"Quelentaro 110 kV - H1 Línea 110 kV Quelentaro - Las Arañas","H1",40,19.547999999999998,0.48869999999999997,19.573999999999998,0.48934999999999995,1.3300593411090548E-3]
[null,null,110,"Quelentaro 110 kV - H2 Línea 110kV Litueche - Quelentaro","H2",40,18.582999999999998,0.46457499999999996,18.607999999999997,0.46519999999999995,1.3453156110422742E-3]
[null,null,110,"Quelentaro 110 kV - HT1 Transformador AT1 195MVA 220/110kV","HT1",40,19.446000000000002,0.48615000000000003,19.472999999999999,0.48682499999999995,1.3884603517431589E-3]
[null,null,110,"Quelentaro 110 kV - HT5 Transformador TR5 13MVA 110/23 kV","HT5",31.5,19.931999999999999,0.63276190476190475,19.957999999999998,0.63358730158730159,1.3044350792695064E-3]
[null,"Quellon",110,"Quellon 110 kV -  H1 Línea 110 kV Quellón - Chonchi"," H1",40,1.554,3.8850000000000003E-2,1.554,3.8850000000000003E-2,0]
[null,null,110,"Quellon 110 kV - HT1 Transformador TR1 16MVA 115/13,8 kV N°1","HT1",40,1.7310000000000001,4.3275000000000001E-2,1.7310000000000001,4.3275000000000001E-2,0]
[null,null,110,"Quellon 110 kV - HT2 Transformador TR2 16MVA  115/24 kV N°2","HT2",40,1.7470000000000001,4.3675000000000005E-2,1.7470000000000001,4.3675000000000005E-2,0]
[null,"Quereo",110,"Quereo 110 kV -  En Barra",null,null,9.2579999999999991,"N/A",9.2669999999999995,"N/A",9.7213220998059434E-4]
[null,"Quilicura",110,"Quilicura 110 kV -  H1 Línea 110 kV Qulicura - San Cristobal /Cerro Navia C1"," H1",40,20.128000000000004,0.50320000000000009,20.204000000000001,0.50509999999999999,3.7758346581874477E-3]
[null,null,110,"Quilicura 110 kV -  H2 Línea 110 kV Qulicura - San Cristobal /Cerro Navia C2"," H2",40,20.128000000000004,0.50320000000000009,20.204000000000001,0.50509999999999999,3.7758346581874477E-3]
[null,null,110,"Quilicura 110 kV - HT1 Transformador TR01 50MVA 110/23kV","HT1",40,40.255000000000003,1.006375,40.406999999999996,1.0101749999999998,3.7759284560922595E-3]
[null,null,110,"Quilicura 110 kV - HT2 Transformador TR02 25MVA 110/12kV","HT2",31.5,40.255000000000003,1.2779365079365079,40.406999999999996,1.2827619047619045,3.7759284560922595E-3]
[null,null,110,"Quilicura 110 kV - HT3 Transformador TR03 50MVA 110/12kV","HT3",40,40.255000000000003,1.006375,40.406999999999996,1.0101749999999998,3.7759284560922595E-3]
[null,null,110,"Quilicura 110 kV - AT4 Transformador TR04 22,4MVA 110/12kV","AT4",31.5,40.255000000000003,1.2779365079365079,40.406999999999996,1.2827619047619045,3.7759284560922595E-3]
[null,"Quillota",110,"Quillota 110 kV - H3 Línea 110 kV Quillota - Marbella/ Illapel","H3",31.5,40.855999999999995,1.2970158730158727,42.631,1.3533650793650793,4.3445271196397246E-2]
[null,null,110,"Quillota 110 kV - HT3 Transformador TR03 48MVA 110/110 kV N°3","HT3",40,40.855999999999995,1.0213999999999999,42.631,1.0657749999999999,4.3445271196397246E-2]
[null,null,110,"Quillota 110 kV - H2 Línea 110 kV Quillota - San Pedro","H2",32,26.648999999999997,0.83278124999999992,27.34,0.854375,2.5929678411948012E-2]
[null,null,110,"Quillota 110 kV - HT1/2 Transformador ATR1 75 MVA 220/115/13.8 kV ATR2 75 MVA 220/115/13.8 kV","HT1/2",32,39.376999999999995,1.2305312499999999,41.122,1.2850625,4.4315209386190026E-2]
[null,null,110,"Quillota 110 kV - HT4 Transformador ATR4 150MVA 220/115/13.8 kV N°4","HT4",50,37.085999999999999,0.74171999999999993,38.798999999999999,0.77598,4.6189936903413713E-2]
[null,null,110,"Quillota 110 kV - HT5 Tranformador ATR5 150MVA  ","HT5",50,37.004999999999995,0.74009999999999987,38.719000000000001,0.77438000000000007,4.6318065126334441E-2]
[null,"Quilpue",110,"Quilpue 110 kV - HT1 Transformador TR1 25MVA 110/12 kV ","HT1",40,14.205,0.35512500000000002,14.627000000000001,0.36567500000000003,2.970784934882088E-2]
[null,null,110,"Quilpue 110 kV - HT2 Transformador TR2 110/12 kV ","HT2",40,14.205,0.35512500000000002,14.627000000000001,0.36567500000000003,2.970784934882088E-2]
[null,null,110,"Quilpue 110 kV - HT3 Transformador TR3 25MVA 110/12 kV","HT3",25,14.205,0.56820000000000004,14.627000000000001,0.58508000000000004,2.970784934882088E-2]
[null,"Quinquimo",110,"Quinquimo 110 kV - HT1 Transformador 20MVA 110/23 kV","HT1",25,3.4129999999999998,0.13652,3.419,0.13675999999999999,1.7579841781424634E-3]
[null,null,110,"Quinquimo 110 kV -  H1 Línea 110 kV Quinquimo - Choapa"," H1",40,1.744,4.36E-2,1.7450000000000001,4.3625000000000004E-2,5.7339449541290825E-4]
[null,null,110,"Quinquimo 110 kV -  H2 Línea 110 kV Quinquimo - Casas Viejas"," H2",40,1.7429999999999999,4.3574999999999996E-2,1.744,4.36E-2,5.7372346528979459E-4]
[null,null,110,"Quinquimo 110 kV -  H3 Línea 110 kV Quinquimo - Cabildo"," H3",40,3.4129999999999998,8.5324999999999998E-2,3.419,8.5474999999999995E-2,1.7579841781424634E-3]
[null,"Quintero (Chilquinta)",110,"Quintero (Chilquinta) 110 kV - H1 Transformador TR1 22,5MVA 110/12 kV ","H1",40,29.718,0.74295,37.195,0.92987500000000001,0.25159835789757051]
[null,null,110,"Quintero (Chilquinta) 110 kV - H2 Transformador TR2 20MVA 110/12 kV ","H2",40,29.718,0.74295,37.195,0.92987500000000001,0.25159835789757051]
[null,"Rancagua",154,"Rancagua 154 kV - A1 Línea 154kV Rancagua - Tinguiririca 2/Alto Jahuel 2","A1",40,9.31,0.23275000000000001,9.3160000000000007,0.23290000000000002,6.4446831364127033E-4]
[null,null,154,"Rancagua 154 kV - A2 Línea 154kV Rancagua - Tinguiririca 1/Alto Jahuel 1","A2",40,9.3170000000000002,0.23292499999999999,9.322000000000001,0.23305000000000003,5.3665342921549659E-4]
[null,null,154,"Rancagua 154 kV - A3 Línea 154kV Rancagua - Sauzal/Minera del Valle Central","A3",32,11.178000000000001,0.34931250000000003,11.187000000000001,0.34959375000000004,8.0515297906605301E-4]
[null,null,154,"Rancagua 154 kV - AT2/3 Transformador TR02 25MVA 154/66kV","AT2/3",9,14.292,1.5880000000000001,14.303000000000001,1.5892222222222223,7.6966134900650776E-4]
[null,null,154,"Rancagua 154 kV - AT4 Transformador TR04 45/60/75MVA 154/69/14,8kV","AT4",40,13.686,0.34215000000000001,13.696000000000002,0.34240000000000004,7.3067368113411974E-4]
[null,null,154,"Rancagua 154 kV - AT2 Transformador TR01 35/45/56MVA 154/69/13,8kV","AT2",40,13.776,0.34439999999999998,13.786000000000001,0.34465000000000001,7.259001161441321E-4]
[null,"Recoleta",110,"Recoleta 110 kV - H1 Línea 110 kV Recoleta - San Cristobal/Cerro Navia C1","H1",40,16.039000000000001,0.40097500000000003,16.09,0.40225,3.1797493609326253E-3]
[null,null,110,"Recoleta 110 kV - H2 Línea 110 kV Recoleta - San Cristobal/Cerro Navia C2","H2",40,16.039000000000001,0.40097500000000003,16.09,0.40225,3.1797493609326253E-3]
[null,null,110,"Recoleta 110 kV - HT3 Transformador TR03 110/12,5kV","HT3",40,32.076999999999998,0.801925,32.18,0.80449999999999999,3.2110234747638974E-3]
[null,null,110,"Recoleta 110 kV - HT1 Transformador TR01 25MVA 110/13.2 kV","HT1",40,32.076999999999998,0.801925,32.18,0.80449999999999999,3.2110234747638974E-3]
[null,"Renca",110,"Renca 110 kV - H4 Línea 110 kV Renca - Brasil C2","H4",40,54.667000000000002,1.3666750000000001,54.893999999999998,1.37235,4.152413704794424E-3]
[null,null,110,"Renca 110 kV - H3 Línea 110 kV Renca - Brasil C1","H3",40,54.667000000000002,1.3666750000000001,54.893999999999998,1.37235,4.152413704794424E-3]
[null,null,110,"Renca 110 kV - H1 Línea 110 kV Renca - Cerro Navia C1","H1",40,40.204000000000001,1.0051000000000001,40.326999999999998,1.008175,3.0593970749178577E-3]
[null,null,110,"Renca 110 kV - H2 Línea 110 kV Renca - Cerro Navia C2","H2",40,40.204000000000001,1.0051000000000001,40.326999999999998,1.008175,3.0593970749178577E-3]
[null,null,110,"Renca 110 kV - H5 Línea 110 kV Renca - Metro C1","H5",40,40.707999999999998,1.0177,40.859000000000002,1.0214750000000001,3.709344600569995E-3]
[null,null,110,"Renca 110 kV - H7 Enlace unidad a Gas central nueva renca - Renca","H7",31.5,50.550000000000004,1.6047619047619048,50.777000000000001,1.6119682539682541,4.4906033630068591E-3]
[null,null,110,"Renca 110 kV - H8 Enlace unidad a Vapor central nueva renca - Renca","H8",40,50.858000000000004,1.2714500000000002,51.085000000000001,1.2771250000000001,4.4634079200911708E-3]
[null,"Reñaca",110,"Reñaca 110 kV - HX Línea 110kV Reñaca - Bosquemar","HX","S/I",10.326000000000001,"N/P",10.756,"N/P",4.1642455936471014E-2]
[null,null,110,"Reñaca 110 kV - HT1 Transformador TR1 22,4MVA 110/12 kV N°1","HT1",40,14.821,0.37052499999999999,15.486000000000001,0.38714999999999999,4.4868767289656629E-2]
[null,null,110,"Reñaca 110 kV - HT2 Transformador TR2 30MVA 110/12 kV N°2","HT2",40,14.821,0.37052499999999999,15.486000000000001,0.38714999999999999,4.4868767289656629E-2]
[null,"Río Bonito",110,"Río Bonito 110 kV - HT1 Transformador T1 40MVA 110/66/23 kV","HT1",40,1.962,4.9049999999999996E-2,1.962,4.9049999999999996E-2,0]
[null,"Río Toltén",110,"Río Toltén 110 kV - H1 Línea 110 kV Rio Toltén - Cunco/Melipeuco","H1",40,2.8609999999999998,7.1524999999999991E-2,2.8609999999999998,7.1524999999999991E-2,0]
[null,"S/E ACONCAGUA TG [En_Revision]",110,"S/E ACONCAGUA TG [En_Revision] 110 kV -  En Barra",null,null,18.643000000000001,"N/A",19.876000000000001,"N/A",6.6137424234297082E-2]
[null,"S/E CENTRAL CUEL",154,"S/E CENTRAL CUEL 154 kV - AL Línea 154 kV Negrete Cuel - Tap Santa Luisa","AL",40,4.4969999999999999,0.112425,4.4980000000000002,0.11245000000000001,2.2237046920176427E-4]
[null,"S/E CENTRAL SAUZALITO",154,"S/E CENTRAL SAUZALITO 154 kV - A1 Línea 154 kV Sauzal - Minera Valle Central / Rancagua","A1","S/I",6.8570000000000002,"F/I",6.8609999999999998,"F/I",5.83345486364235E-4]
[null,"S/E INTERCONEXION CHACAYES",110,"S/E INTERCONEXION CHACAYES 110 kV - J1 Línea 110 kV Interconexión Chacayes - Arranque a: Sauzal 1 / Central Chacayes 1","J1",40,12.279,0.306975,12.284000000000001,0.30710000000000004,4.0719928332932497E-4]
[null,null,110,"S/E INTERCONEXION CHACAYES 110 kV - J2 Línea 110 kV Interconexión Chacayes - Arranque a: Sauzal 2 / Central Chacayes 2","J2","S/I",12.279,"F/I",12.284000000000001,"F/I",4.0719928332932497E-4]
[null,null,110,"S/E INTERCONEXION CHACAYES 110 kV - JT  Transformador Interconexión Chacayes 110/110 kV","JT ","S/I",10.454000000000001,"F/I",10.458,"F/I",3.8262865888650843E-4]
[null,null,110,"S/E INTERCONEXION CHACAYES 110 kV - HT Transformador Interconexión Chacayes 110/110 kV","HT","S/I",10.454999999999998,"F/I",10.457000000000001,"F/I",1.9129603060759871E-4]
[null,null,110,"S/E INTERCONEXION CHACAYES 110 kV - H1 Línea 110 kV Interconexión Chacayes - Minero 1","H1","S/I",13.879,"F/I",13.885,"F/I",4.3230780315586337E-4]
[null,null,110,"S/E INTERCONEXION CHACAYES 110 kV - H2 Línea 110 kV Interconexión Chacayes - Minero 2","H2","S/I",13.879,"F/I",13.885,"F/I",4.3230780315586337E-4]
[null,"S/E MALLOA NUEVA",154,"S/E MALLOA NUEVA 154 kV - AT1 Transformador TR01 60/75MVA 220-154/66/15kV","AT1",40,14.856999999999999,0.37142500000000001,14.864000000000001,0.37160000000000004,4.7115837652294878E-4]
[null,null,154,"S/E MALLOA NUEVA 154 kV - A1 Línea 154 kV Nueva Malloa - Tap Malloa 2","A1",40,7.9069999999999991,0.19767499999999999,7.9119999999999999,0.1978,6.3235108132044795E-4]
[null,null,154,"S/E MALLOA NUEVA 154 kV - A2 Línea 154 kV Nueva Malloa - Tap Malloa 1","A2",40,7.9069999999999991,0.19767499999999999,7.9119999999999999,0.1978,6.3235108132044795E-4]
[null,null,154,"S/E MALLOA NUEVA 154 kV - AT2 Transformador TR02 ","AT2",40,14.856999999999999,0.37142500000000001,14.864000000000001,0.37160000000000004,4.7115837652294878E-4]
[null,"S/E POLPAICO (ENEL DISTRIBUCIÓN)",110,"S/E POLPAICO (ENEL DISTRIBUCIÓN) 110 kV -  En Barra",null,null,14.353999999999999,"N/A",14.407999999999999,"N/A",3.7620175560819473E-3]
[null,"Salamanca ",110,"Salamanca  110 kV - HT1 Transformador TR1 ","HT1",40,2.391,5.9775000000000002E-2,2.391,5.9775000000000002E-2,0]
[null,null,110,"Salamanca  110 kV - HT2 Transformador TR2","HT2",31.5,2.391,7.5904761904761905E-2,2.391,7.5904761904761905E-2,0]
[null,"Salar ",110,"Salar  110 kV - H25 Línea 100 kV Salar - KM6 ","H25",31.5,7.5779999999999994,0.24057142857142855,7.7570000000000006,0.24625396825396828,2.3621008181578407E-2]
[null,null,110,"Salar  110 kV - HT3 Transformador  ATR1 120/120/30 MVA 220/110/13,8 kV ","HT3",31.5,6.9390000000000001,0.22028571428571428,7.173,0.2277142857142857,3.372243839169909E-2]
[null,null,110,"Salar  110 kV - H26 Línea 100 kV Salar - KM6 ","H26",31.5,7.5779999999999994,0.24057142857142855,7.7570000000000006,0.24625396825396828,2.3621008181578407E-2]
[null,null,110,"Salar  110 kV - H4 Línea 100 kV Salar - Central Tamaya ","H4","S/I",10.081999999999999,"F/I",10.297000000000001,"F/I",2.1325133902003735E-2]
[null,null,110,"Salar  110 kV - HPT1 Transformador TR1 40/32/40 MVA 100/13,8/13,8 kV ","HPT1","S/I",10.728999999999999,"F/I",10.989000000000001,"F/I",2.423338614968791E-2]
[null,null,110,"Salar  110 kV - HPT2 Transformador TR2 40/32/40 MVA 100/13,8/13,8 kV ","HPT2","S/I",10.728999999999999,"F/I",10.989000000000001,"F/I",2.423338614968791E-2]
[null,null,110,"Salar  110 kV - HAB Acoplador ","HAB",31.5,10.728999999999999,0.34060317460317457,10.989000000000001,0.34885714285714287,2.423338614968791E-2]
[null,"San Antonio ",110,"San Antonio  110 kV -  H1 Línea 110 kV San Antonio - Alto Melipilla "," H1",40,3.0830000000000002,7.7075000000000005E-2,3.0870000000000002,7.7175000000000007E-2,1.2974375608173867E-3]
[null,null,110,"San Antonio  110 kV - HT2 Transformador TR2 25 MVA 110/12 kV  ","HT2",40,5.3090000000000002,0.13272500000000001,5.3150000000000004,0.13287500000000002,1.1301563382935067E-3]
[null,null,110,"San Antonio  110 kV - HT3 Transformador 60MVA ATR 110/66 kV","HT3",40,4.4409999999999998,0.111025,4.4450000000000003,0.111125,9.0069804098186169E-4]
[null,null,110,"San Antonio  110 kV -  H2 Línea 110 kV San Antonio - Leyda "," H2",40,3.0840000000000001,7.7100000000000002E-2,3.0870000000000002,7.7175000000000007E-2,9.7276264591443376E-4]
[null,null,110,"San Antonio  110 kV - HT4 Transformador TR4 25 MVA 110/23 kV ","HT4",31.5,5.3090000000000002,0.16853968253968254,5.3150000000000004,0.16873015873015873,1.1301563382935067E-3]
[null,null,110,"San Antonio  110 kV - HT1 Transformador TR1 30 MVA 110/12 kV  ","HT1",40,5.3090000000000002,0.13272500000000001,5.3150000000000004,0.13287500000000002,1.1301563382935067E-3]
[null,null,110,"San Antonio  110 kV - HT5 Transformador TR5 50 MVA 110/23 kV","HT5",40,5.3090000000000002,0.13272500000000001,5.3150000000000004,0.13287500000000002,1.1301563382935067E-3]
[null,"San Bernardo ",110,"San Bernardo  110 kV -  H1 Línea 110 kV San Bernardo - Buin/Lo Espejo 1 "," H1",40,18.471000000000004,0.4617750000000001,18.518999999999998,0.46297499999999997,2.5986681825561531E-3]
[null,null,110,"San Bernardo  110 kV -  H2 Línea 110 kV San Bernardo - Buin/Lo Espejo 2"," H2",40,18.471000000000004,0.4617750000000001,18.518999999999998,0.46297499999999997,2.5986681825561531E-3]
[null,null,110,"San Bernardo  110 kV -  H3 Línea 110 kV San Bernardo - Malloco "," H3",18.8,36.941000000000003,1.9649468085106383,37.037999999999997,1.9701063829787231,2.625808722016031E-3]
[null,"San Cristóbal ",110,"San Cristóbal  110 kV -  H1 Línea 110 kV San Cristóbal - El Salto/Cerro Navia 1 "," H1",31.5,13.781000000000001,0.43749206349206349,13.82,0.43873015873015875,2.8299833103548147E-3]
[null,null,110,"San Cristóbal  110 kV -  H2 Línea 110 kV San Cristóbal - El Salto/Cerro Navia 2"," H2",31.5,13.781000000000001,0.43749206349206349,13.82,0.43873015873015875,2.8299833103548147E-3]
[null,null,110,"San Cristóbal  110 kV - HT1 Transformador TR01 40 MVA 110/12 kV ","HT1",31.5,27.562000000000001,0.87498412698412698,27.64,0.8774603174603175,2.8299833103548147E-3]
[null,null,110,"San Cristóbal  110 kV - HT2 Transformador TR02 40 MVA 110/12 kV ","HT2",31.5,27.562000000000001,0.87498412698412698,27.64,0.8774603174603175,2.8299833103548147E-3]
[null,null,110,"San Cristóbal  110 kV - HT3 TR03-TR04","HT3",31.5,27.562000000000001,0.87498412698412698,27.64,0.8774603174603175,2.8299833103548147E-3]
[null,null,110,"San Cristóbal  110 kV - HT4 Transformador TR04 50 MVA 110/12,5 kV ","HT4",31.5,27.562000000000001,0.87498412698412698,27.64,0.8774603174603175,2.8299833103548147E-3]
[null,null,110,"San Cristóbal  110 kV - HT5 Transformador TR05 50 MVA 110/12 kV ","HT5",25,27.562000000000001,1.1024800000000001,27.64,1.1055999999999999,2.8299833103548147E-3]
[null,"San Felipe ",110,"San Felipe  110 kV - H1 Línea 110 kV San Felipe - Tap San Felipe C1","H1",31.5,4.851,0.154,4.8659999999999997,0.15447619047619046,3.0921459492887406E-3]
[null,null,110,"San Felipe  110 kV - H2 Línea 110 kV San Felipe - Tap San Felipe C2","H2",31.5,4.851,0.154,4.8659999999999997,0.15447619047619046,3.0921459492887406E-3]
[null,"San Fernando",154,"San Fernando 154 kV - AT1 Transformador 220-154/69/14.8 kV N°1","AT1",40,15.747999999999999,0.39369999999999999,15.755999999999998,0.39389999999999997,5.0800101600197612E-4]
[null,null,154,"San Fernando 154 kV - AT2 Transformador 154/69/13.8 kV N°2","AT2",40,15.449,0.38622499999999998,15.456999999999999,0.38642499999999996,5.1783286944133075E-4]
[null,null,154,"San Fernando 154 kV - AT3 Transformador 154/69/13.2 kV N°3","AT3",31.5,16.143000000000001,0.51247619047619053,16.151,0.5127301587301587,4.9557083565626703E-4]
[null,"San Joaquín (Enel Distribución) ",110,"San Joaquín (Enel Distribución)  110 kV - H1 Línea 110 kV San Joaquín (Chilectra) - Ochagavía/Florida 1 ","H1",31.5,19.067000000000004,0.60530158730158745,19.117000000000001,0.60688888888888892,2.6223317774163291E-3]
[null,null,110,"San Joaquín (Enel Distribución)  110 kV - H2 Línea 110 kV San Joaquín (Chilectra) - Ochagavía/Florida 2","H2",31.5,19.067000000000004,0.60530158730158745,19.117000000000001,0.60688888888888892,2.6223317774163291E-3]
[null,"San Joaquín (Transnet)",110,"San Joaquín (Transnet) 110 kV - HT2 Transformador TR2 30/24/18 MVA 110/13,8 kV ","HT2",40,7.992,0.19980000000000001,7.9950000000000001,0.199875,3.7537537537538958E-4]
[null,null,110,"San Joaquín (Transnet) 110 kV - HT1 Transformador TR1 30/24/18 MVA 110/13,8 kV ","HT1",25,7.992,0.31968000000000002,7.9950000000000001,0.31980000000000003,3.7537537537538958E-4]
[null,"San José ",110,"San José  110 kV - H1 Línea 110 kV San José - Cerro Navia/Chena 1","H1",40,18.355,0.45887500000000003,18.411999999999999,0.46029999999999999,3.1054208662489027E-3]
[null,null,110,"San José  110 kV - H2 Línea 110 kV San José - Cerro Navia/Chena 2","H2",40,18.355,0.45887500000000003,18.411999999999999,0.46029999999999999,3.1054208662489027E-3]
[null,null,110,"San José  110 kV - HT3 Transformador TR03 22,4 MVA 110/12,5 kV ","HT3","S/I",36.71,"F/I",36.823999999999998,"F/I",3.1054208662489027E-3]
[null,null,110,"San José  110 kV - H4 Transformador TR04 50 MVA 110/12,5 kV ","H4",40,36.71,0.91775000000000007,36.823999999999998,0.92059999999999997,3.1054208662489027E-3]
[null,"San Pablo ",110,"San Pablo  110 kV -  H1 Línea 110 kV San Pablo - Cerro Navia/Lo Aguirre 1"," H1",40,17.143999999999998,0.42859999999999998,17.193999999999999,0.42984999999999995,2.9164722351843627E-3]
[null,null,110,"San Pablo  110 kV -  H2 Línea 110 kV San Pablo - Cerro Navia/Lo Aguirre 2"," H2",40,17.143000000000001,0.42857500000000004,17.193000000000001,0.42982500000000001,2.9166423613136969E-3]
[null,null,110,"San Pablo  110 kV - HT1 Transformador TR01 37,5MVA 110/23,5kV","HT1","S/I",33.896000000000001,"F/I",33.994,"F/I",2.8911966013688627E-3]
[null,null,110,"San Pablo  110 kV - HT2 Transformador TR02 37,5MVA 110/23,5kV","HT2","S/I",33.896000000000001,"F/I",33.994,"F/I",2.8911966013688627E-3]
[null,"San Pedro (AES GENER)",110,"San Pedro (AES GENER) 110 kV - H6 Línea 110 kV San Pedro - TO Mayaca C1","H6",31.5,29.355000000000004,0.93190476190476201,30.756,0.97638095238095235,4.77261113949922E-2]
[null,null,110,"San Pedro (AES GENER) 110 kV - H7 Línea 110 kV San Pedro - TO Mayaca C2","H7",31.5,29.355000000000004,0.93190476190476201,30.756,0.97638095238095235,4.77261113949922E-2]
[null,null,110,"San Pedro (AES GENER) 110 kV - HT Transformador TR1 110/12 kV / TR2 110/12 kV","HT","S/I",32.444000000000003,"F/I",33.853999999999999,"F/I",4.3459499445197773E-2]
[null,null,110,"San Pedro (AES GENER) 110 kV - H3 Línea 110 kV San Pedro - Quillota","H3",31.5,17.295000000000002,0.54904761904761912,18.567999999999998,0.58946031746031735,7.3605088175773117E-2]
[null,null,110,"San Pedro (AES GENER) 110 kV - H1 Línea 110 kV San Pedro - Ventanas /Codelco Div. Ventanas 1 ","H1",31.5,29.972000000000001,0.9514920634920635,30.988999999999997,0.98377777777777764,3.3931669558254232E-2]
[null,null,110,"San Pedro (AES GENER) 110 kV - H2 Línea 110 kV San Pedro - Ventanas /Codelco Div. Ventanas 2","H2",31.5,29.972000000000001,0.9514920634920635,30.988999999999997,0.98377777777777764,3.3931669558254232E-2]
[null,null,110,"San Pedro (AES GENER) 110 kV - H4 Línea 110 kV San Pedro - Miraflores 1 ","H4",31.5,29.849000000000004,0.94758730158730176,31.126999999999999,0.98815873015873013,4.2815504707025193E-2]
[null,null,110,"San Pedro (AES GENER) 110 kV - H5 Línea 110 kV San Pedro - Miraflores 2","H5",31.5,30.881000000000004,0.98034920634920641,32.210999999999999,1.0225714285714285,4.3068553479485593E-2]
[null,null,110,"San Pedro (AES GENER) 110 kV - HR Acoplador ","HR","S/I",32.444000000000003,"F/I",33.853999999999999,"F/I",4.3459499445197773E-2]
[null,"San Rafael (Chilquinta)",110,"San Rafael (Chilquinta) 110 kV - HT1 Transformador TR1 25MVA 110/12kV","HT1",40,9.2240000000000002,0.2306,9.2449999999999992,0.23112499999999997,2.2766695576755223E-3]
[null,null,110,"San Rafael (Chilquinta) 110 kV - HT2 Transformador TR2 22,5MVA 110/12kV","HT2",40,9.2240000000000002,0.2306,9.2449999999999992,0.23112499999999997,2.2766695576755223E-3]
[null,null,110,"San Rafael (Chilquinta) 110 kV - HT3 Transformador TR3 30MVA 110/23kV","HT3",40,9.2240000000000002,0.2306,9.2449999999999992,0.23112499999999997,2.2766695576755223E-3]
[null,"San Vicente",154,"San Vicente 154 kV - A1 Línea 154kV San Vicente - Hualpén 2","A1",40,13.613999999999999,0.34034999999999999,13.990000000000002,0.34975000000000006,2.7618627883061776E-2]
[null,null,154,"San Vicente 154 kV - A2 Línea 154kV San Vicente - EKA Chile /Hualpén 1","A2",40,13.606999999999999,0.34017500000000001,13.982000000000001,0.34955000000000003,2.7559344455060027E-2]
[null,null,154,"San Vicente 154 kV - A3 Línea 154kV San Vicente - Concepción 1","A3",40,14.511999999999999,0.36279999999999996,15.085000000000001,0.37712500000000004,3.948456449834635E-2]
[null,null,154,"San Vicente 154 kV - A10 Línea 154kV San Vicente - Concepción 2","A10",40,14.511999999999999,0.36279999999999996,15.085000000000001,0.37712500000000004,3.948456449834635E-2]
[null,null,154,"San Vicente 154 kV - A9 Línea 154kV San Vicente - Huachipato 2","A9",40,18.248999999999999,0.45622499999999999,18.87,0.47175,3.4029261877363264E-2]
[null,null,154,"San Vicente 154 kV - ACE1 Condensador CCEE1","ACE1",40,18.248999999999999,0.45622499999999999,18.87,0.47175,3.4029261877363264E-2]
[null,null,154,"San Vicente 154 kV - A6 Línea 154kV San Vicente - Huachipato 1","A6",40,18.248999999999999,0.45622499999999999,18.87,0.47175,3.4029261877363264E-2]
[null,null,154,"San Vicente 154 kV - AT4 Transformador TR4","AT4","S/I",18.248999999999999,"F/I",18.87,"F/I",3.4029261877363264E-2]
[null,null,154,"San Vicente 154 kV - AT3 Transformador TR3 40/20/30MVA 154/69/13,8kV","AT3",40,18.081,0.45202500000000001,18.704000000000001,0.46760000000000002,3.445605884630281E-2]
[null,null,154,"San Vicente 154 kV - AT2 Transformador TR2 26MVA 154/13,8kV","AT2",40,18.248999999999999,0.45622499999999999,18.87,0.47175,3.4029261877363264E-2]
[null,null,154,"San Vicente 154 kV - A5 Línea 154kV San Vicente - Talcahuano","A5",40,16.896999999999998,0.42242499999999994,17.483000000000001,0.43707499999999999,3.4680712552524244E-2]
[null,"Santa Elena",110,"Santa Elena 110 kV - HT2 Transformador TR02 50MVA 110/12,5kV","HT2",40,31.51,0.78775000000000006,31.577999999999999,0.78944999999999999,2.1580450650586429E-3]
[null,null,110,"Santa Elena 110 kV - H3 Transformador TR03 50MVA 110/13,2kV","H3","S/I",31.51,"F/I",31.577999999999999,"F/I",2.1580450650586429E-3]
[null,null,110,"Santa Elena 110 kV - H4 Transformador TR04 50MVA 110/12,5kV","H4","S/I",31.51,"F/I",31.577999999999999,"F/I",2.1580450650586429E-3]
[null,null,110,"Santa Elena 110 kV - AT5 Transformador TR05 22,4MVA 110/12,5kV","AT5","S/I",31.51,"F/I",31.577999999999999,"F/I",2.1580450650586429E-3]
[null,null,110,"Santa Elena 110 kV - H1 Línea 110kV Santa Elena - Ochagavía/Florida1","H1",40,15.755000000000001,0.39387500000000003,15.789,0.39472499999999999,2.1580450650586429E-3]
[null,null,110,"Santa Elena 110 kV - H2 Línea 110kV Santa Elena - Ochagavía/Florida2","H2",40,15.755000000000001,0.39387500000000003,15.789,0.39472499999999999,2.1580450650586429E-3]
[null,"Santa Fe",154,"Santa Fe 154 kV -  En Barra",null,null,4.883,"N/A",4.8849999999999998,"N/A",4.0958427196391146E-4]
[null,"Santa Marta",110,"Santa Marta 110 kV - HT2 Transformador TR02 50MVA 110/12,5kV","HT2",40,34.115000000000002,0.85287500000000005,34.207999999999998,0.85519999999999996,2.7260735746737919E-3]
[null,null,110,"Santa Marta 110 kV - HT4 Transformador TR04 37,5MVA 110/23,5kV","HT4",40,34.115000000000002,0.85287500000000005,34.207999999999998,0.85519999999999996,2.7260735746737919E-3]
[null,null,110,"Santa Marta 110 kV - H1 Línea 110kV Santa Marta - Cerro Navia/Chena1","H1",40,17.058000000000003,0.42645000000000011,17.103999999999999,0.42759999999999998,2.6966819087815576E-3]
[null,null,110,"Santa Marta 110 kV - H2 Línea 110kV Santa Marta - Cerro Navia/Chena2","H2",40,17.058000000000003,0.42645000000000011,17.103999999999999,0.42759999999999998,2.6966819087815576E-3]
[null,null,110,"Santa Marta 110 kV - HX Línea 110kV Santa Marta  - Padre Hurtado","HX","S/I",34.115000000000002,"N/P",34.207999999999998,"N/P",2.7260735746737919E-3]
[null,"Santa Raquel",110,"Santa Raquel 110 kV - HT1 Transformador TR01 50MVA 110/12,5kV","HT1",40,24.462,0.61155000000000004,24.498000000000001,0.61245000000000005,1.471670345842587E-3]
[null,null,110,"Santa Raquel 110 kV - HT2 Transformador TR02 25MVA 110/12,5kV","HT2",40,24.462,0.61155000000000004,24.498000000000001,0.61245000000000005,1.471670345842587E-3]
[null,null,110,"Santa Raquel 110 kV - H4 Transformador TR04 22,4MVA 110/12,5kV","H4",40,24.462,0.61155000000000004,24.498000000000001,0.61245000000000005,1.471670345842587E-3]
[null,null,110,"Santa Raquel 110 kV - H1 Línea 110kV Santa Raquel - Buin/Florida1","H1",40,12.231,0.30577500000000002,12.249000000000001,0.30622500000000002,1.471670345842587E-3]
[null,null,110,"Santa Raquel 110 kV - H2 Línea 110kV Santa Raquel - Buin/Florida2","H2",40,12.231,0.30577500000000002,12.249000000000001,0.30622500000000002,1.471670345842587E-3]
[null,null,110,"Santa Raquel 110 kV - H5 Transformador TR05 50MVA 110/20,4kV","H5",40,24.462,0.61155000000000004,24.498000000000001,0.61245000000000005,1.471670345842587E-3]
[null,null,110,"Santa Raquel 110 kV - HT6 Transformador N°6 12/16/20/22,4MVA 110/12,5kV","HT6","S/I",24.462,"F/I",24.498000000000001,"F/I",1.471670345842587E-3]
[null,"Santa Rosa Sur",110,"Santa Rosa Sur 110 kV - H1 Línea 110kV Santa Rosa Sur - Buin/Florida1","H1",40,16.032000000000004,0.4008000000000001,16.064000000000004,0.40160000000000007,1.9960079840319373E-3]
[null,null,110,"Santa Rosa Sur 110 kV - H2 Línea 110kV Santa Rosa Sur - Buin/Florida2","H2",40,16.032000000000004,0.4008000000000001,16.064000000000004,0.40160000000000007,1.9960079840319373E-3]
[null,null,110,"Santa Rosa Sur 110 kV - HT3 Transformador TR03 25MVA 110/12,5kV","HT3",40,32.063000000000002,0.80157500000000004,32.127000000000002,0.80317500000000008,1.9960702367214562E-3]
[null,null,110,"Santa Rosa Sur 110 kV - H4 Transformador TR04 22,4MVA 110/12,5kV","H4",40,32.063000000000002,0.80157500000000004,32.127000000000002,0.80317500000000008,1.9960702367214562E-3]
[null,"Sauzal (C.Sauzal)",110,"Sauzal (C.Sauzal) 110 kV - HT4 Transformador TR4 50 MVA 154/110/13.8 kV y TR7 70 MVA 154/110/13.8 kV","HT4",28,15.294,0.54621428571428576,15.302,0.54649999999999999,5.2308094677645605E-4]
[null,null,110,"Sauzal (C.Sauzal) 110 kV - H4 Línea 110kV Sauzal - Minero 2/Interconexión Chacayes 2","H4",22,17.705000000000002,0.80477272727272731,17.713000000000001,0.80513636363636365,4.5184975995476523E-4]
[null,null,110,"Sauzal (C.Sauzal) 110 kV - H3 Línea 110kV Sauzal - Minero 1/Interconexión Chacayes 1","H3",22,17.705000000000002,0.80477272727272731,17.713000000000001,0.80513636363636365,4.5184975995476523E-4]
[null,null,110,"Sauzal (C.Sauzal) 110 kV - H1 Línea 110kV Codegua - Sauzal C1","H1",40,18.686,0.46715000000000001,18.693999999999999,0.46734999999999999,4.2812801027502508E-4]
[null,null,110,"Sauzal (C.Sauzal) 110 kV - H2 Línea 110kV Codegua - Sauzal C2","H2",40,18.686,0.46715000000000001,18.693999999999999,0.46734999999999999,4.2812801027502508E-4]
[null,null,110,"Sauzal (C.Sauzal) 110 kV - H5 Línea 110kV Sauzal - Minero 3 ","H5",31.5,18.152000000000001,0.57625396825396824,18.158999999999999,0.57647619047619048,3.8563243719688721E-4]
[null,null,110,"Sauzal (C.Sauzal) 110 kV - HT6 Transformador TR6 30 MVA 110/66/6 kV","HT6","S/I",20.11,"F/I",20.119,"F/I",4.4753853804079273E-4]
[null,null,110,"Sauzal (C.Sauzal) 110 kV - HT1 Transformador T1 29 MVA 110/13.2 kV","HT1",40,19.608000000000001,0.49020000000000002,19.617000000000001,0.490425,4.5899632802939313E-4]
[null,null,110,"Sauzal (C.Sauzal) 110 kV - HT2 Transformador T2 29 MVA 110/13.2 kV","HT2",40,19.608000000000001,0.49020000000000002,19.617000000000001,0.490425,4.5899632802939313E-4]
[null,null,110,"Sauzal (C.Sauzal) 110 kV - HT3 Transformador T3 29 MVA 110/13.2 kV","HT3",40,19.504000000000001,0.48760000000000003,19.512,0.48780000000000001,4.1017227235434366E-4]
[null,null,110,"Sauzal (C.Sauzal) 110 kV - T5 Transformador T5 10 MVA 110/13.8 kV","T5",28,20.407,0.72882142857142862,20.416,0.7291428571428572,4.4102513843290739E-4]
[null,"Seat El Sol (El Sol)",110,"Seat El Sol (El Sol) 110 kV - 3 Transformador TR1 ",3,40,14.205,0.35512500000000002,14.627000000000001,0.36567500000000003,2.970784934882088E-2]
[null,null,110,"Seat El Sol (El Sol) 110 kV - 5 Transformador TR2",5,40,14.205,0.35512500000000002,14.627000000000001,0.36567500000000003,2.970784934882088E-2]
[null,null,110,"Seat El Sol (El Sol) 110 kV - 1 Línea",1,40,14.205,0.35512500000000002,14.627000000000001,0.36567500000000003,2.970784934882088E-2]
[null,null,110,"Seat El Sol (El Sol) 110 kV - 2 Línea",2,40,14.205,0.35512500000000002,14.627000000000001,0.36567500000000003,2.970784934882088E-2]
[null,"Sewell",110,"Sewell 110 kV - H1 Línea 100kV Sewell - Minero C1","H1",40,6.2770000000000001,0.15692500000000001,6.28,0.157,4.7793531942012324E-4]
[null,null,110,"Sewell 110 kV - H2 Línea 100kV Sewell - Minero C2","H2",40,6.2770000000000001,0.15692500000000001,6.28,0.157,4.7793531942012324E-4]
[null,null,110,"Sewell 110 kV - HR Acoplador","HR",40,12.554,0.31385000000000002,12.56,0.314,4.7793531942012324E-4]
[null,null,110,"Sewell 110 kV - HT1 Transformador TR1 110/34,5kV","HT1",40,12.554,0.31385000000000002,12.56,0.314,4.7793531942012324E-4]
[null,null,110,"Sewell 110 kV - HT2 Transformador TR2 110/34,5kV","HT2",40,12.554,0.31385000000000002,12.56,0.314,4.7793531942012324E-4]
[null,null,110,"Sewell 110 kV - HT3 Transformador TR3 110/34,5kV","HT3",40,12.554,0.31385000000000002,12.56,0.314,4.7793531942012324E-4]
[null,"Sierra Miranda",110,"Sierra Miranda 110 kV -  En Barra",null,null,7.6340000000000003,"N/A",7.641,"N/A",9.1695048467378476E-4]
[null,"Sopladores",110,"Sopladores 110 kV - HT1 Transformador TR01 25/33MVA 100/13,8kV","HT1","S/I",8.4719999999999995,"F/I",8.6839999999999993,"F/I",2.5023607176581652E-2]
[null,null,110,"Sopladores 110 kV - HT2 Transformador TR02 25/33MVA 100/13,8kV","HT2","S/I",8.4719999999999995,"F/I",8.6839999999999993,"F/I",2.5023607176581652E-2]
[null,null,110,"Sopladores 110 kV - HACOP Acoplador","HACOP","S/I",8.4719999999999995,"F/I",8.6839999999999993,"F/I",2.5023607176581652E-2]
[null,null,110,"Sopladores 110 kV - H24 Línea 100kV Sopladores - KM6","H24","S/I",8.4719999999999995,"F/I",8.6839999999999993,"F/I",2.5023607176581652E-2]
[null,"Sur",110,"Sur 110 kV - HT1 Transformador TR1 110/13,8kV","HT1","S/I",6.5090000000000003,"F/I",6.5140000000000002,"F/I",7.6816715317251389E-4]
[null,"Tal Tal (ELECDA)",110,"Tal Tal (ELECDA) 110 kV -  En Barra",null,null,0.99,"N/A",0.99099999999999999,"N/A",1.010101010101011E-3]
[null,"Talcahuano ",154,"Talcahuano  154 kV - AT3 Transformador TR03 18,7MVA 154/15kV","AT3",40,17.158000000000001,0.42895000000000005,17.707000000000001,0.44267500000000004,3.1996736216342199E-2]
[null,"Talcahuano ",154,"Talcahuano  154 kV - AT1 Transformador TR01 75MVA 154/69/14,8kV","AT1",40,16.536999999999999,0.41342499999999999,17.07,0.42675000000000002,3.2230755276047726E-2]
[null,null,154,"Talcahuano  154 kV - ATX Transformador TR04 56MVA 154/69/14,8kV","ATX","S/I",16.545000000000002,"N/P",17.077000000000002,"N/P",3.2154729525536413E-2]
[null,null,154,"Talcahuano  154 kV - A Línea 154kV Talcahuano - San Vicente","A",40,15.811,0.39527499999999999,16.324999999999999,0.40812499999999996,3.2509012712668352E-2]
[null,"Tap Off Achupallas",110,"Tap Off Achupallas 110 kV -  En Barra",null,null,24.164000000000001,"N/A",25.507000000000001,"N/A",5.5578546598245321E-2]
[null,"Tap Off Alto Melipilla",110,"Tap Off Alto Melipilla 110 kV - H1 Línea 110kV Tap Alto Melipilla - Melipilla","H1",40,11.236000000000001,0.28090000000000004,11.254,0.28134999999999999,1.6019935920255344E-3]
[null,null,110,"Tap Off Alto Melipilla 110 kV - H2 Línea 110kV Tap Alto Melipilla - Bollenar","H2",40,11.416,0.28539999999999999,11.433999999999999,0.28584999999999999,1.5767344078485377E-3]
[null,"Tap Off Antucoya",110,"Tap Off Antucoya 110 kV - HT Línea 110kV Tap Antucoya - Antucoya","HT","S/I",1.161,"F/I",1.1619999999999999,"F/I",8.6132644272169669E-4]
[null,"Tap Off Barriles ",110,"Tap Off Barriles  110 kV - HT1 Transformador TR1 220/110/13,2kV","HT1",40,1.37,3.4250000000000003E-2,1.371,3.4275E-2,7.2992700729918958E-4]
[null,"Tap Off Cerro Balcón ",110,"Tap Off Cerro Balcón  110 kV -  En Barra",null,null,1.7929999999999999,"N/A",1.8220000000000001,"N/A",1.6174010039040791E-2]
[null,"Tap Off Chañares",110,"Tap Off Chañares 110 kV - H1 Línea 110kV Tap Chañares - Central Chañares","H1",31.5,7.7610000000000001,0.24638095238095239,7.7629999999999999,0.24644444444444444,2.5769875016103333E-4]
[null,"Tap Off Chiza",110,"Tap Off Chiza 110 kV -  En Barra",null,null,1.7929999999999999,"N/A",1.8220000000000001,"N/A",1.6174010039040791E-2]
[null,"Tap Off Codelco Ventanas",110,"Tap Off Codelco Ventanas 110 kV - E Línea 110 kV Ventanas 1 - Tap Codelco Ventanas","E",40,25.003999999999998,0.62509999999999999,30.164999999999999,0.75412499999999993,0.20640697488401863]
[null,"Tap Off Coyanco",154,"Tap Off Coyanco 154 kV -  En Barra",null,null,4.883,"N/A",4.8849999999999998,"N/A",4.0958427196391146E-4]
[null,"Tap Off Cuya",110,"Tap Off Cuya 110 kV -  En Barra",null,null,1.8420000000000001,"N/A",1.8620000000000001,"N/A",1.0857763300760053E-2]
[null,"Tap Off Desalant",110,"Tap Off Desalant 110 kV -  En Barra",null,null,8.1639999999999997,"N/A",8.1709999999999994,"N/A",8.5742283194508492E-4]
[null,"Dolores",110,"Dolores 110 kV - HTX Transformador 15MVA TR1 110/24kV","HTX","S/I",1.7929999999999999,"N/P",1.8220000000000001,"N/P",1.6174010039040791E-2]
[null,null,110,"Dolores 110 kV - HX1 Línea 110 kV Dolores - Tap Chiza","HX1","S/I",1.2569999999999999,"N/P",1.2789999999999999,"N/P",1.750198886237074E-2]
[null,null,110,"Dolores 110 kV - HX2 Línea 110 kV Dolores - Tap Cerro Balcón","HX2","S/I",1.2589999999999999,"N/P",1.2809999999999999,"N/P",1.7474185861795093E-2]
[null,"Tap Off Eden",110,"Tap Off Eden 110 kV - H1 Línea 110 kV Tap Off Eden - Central Río Huasco/Alto del Carmen","H1",40,4.2190000000000003,0.10547500000000001,4.2190000000000003,0.10547500000000001,0]
[null,"Tap Off El Negro ",110,"Tap Off El Negro  110 kV - HT1 Transformador TR1 110/23kV","HT1",40,6.7060000000000004,0.16765000000000002,6.7119999999999997,0.1678,8.947211452429673E-4]
[null,"Tap Off El Romeral",110,"Tap Off El Romeral 110 kV -  En Barra",null,null,3.9969999999999999,"N/A",3.9980000000000002,"N/A",2.5018764073063144E-4]
[null,"Tap Off Impulsión",110,"Tap Off Impulsión 110 kV - H Línea 110kV TO Impulsión - Impulsión ","H",25,4.3710000000000004,0.17484000000000002,4.3719999999999999,0.17488000000000001,2.2878059940504363E-4]
[null,"Tap Off La Laja",110,"Tap Off La Laja 110 kV - H2 Línea 110 kV Tap La Laja - Central Queltehues 1","H2",40,21.377000000000002,0.53442500000000004,21.393000000000001,0.53482499999999999,7.4846797960416499E-4]
[null,null,110,"Tap Off La Laja 110 kV - H3 Línea 110 kV Tap La Laja - Central Queltehues 2","H3",40,21.386000000000003,0.53465000000000007,21.402000000000001,0.53505000000000003,7.4815299728786294E-4]
[null,null,110,"Tap Off La Laja 110 kV - HX2 Línea 110 kV Alto Maipo - Tap La Laja C2","HX2","S/I",19.171000000000003,"N/P",19.187000000000001,"N/P",8.3459391789673129E-4]
[null,null,110,"Tap Off La Laja 110 kV - HX1 Línea 110 kV Alto Maipo - Tap La Laja C1","HX1","S/I",19.14,"N/P",19.155999999999999,"N/P",8.3594566353177829E-4]
[null,"La Laja (Energía coyanco)",110,"La Laja (Energía coyanco) 110 kV - BTP Transformador 110/23 kV 15 MVA ","BTP",40,21.620999999999999,0.54052499999999992,21.635999999999999,0.54089999999999994,6.9376994588597057E-4]
[null,"Tap Off Licancabur (Licancabur)",110,"Tap Off Licancabur (Licancabur) 110 kV - HT1 Transformador TR01 37,5MVA 110/3,45kV","HT1","S/I",2.0880000000000001,"F/I",2.089,"F/I",4.7892720306508133E-4]
[null,null,110,"Tap Off Licancabur (Licancabur) 110 kV - HT2 Transformador TR02 37,5MVA 110/3,45kV","HT2","S/I",2.0880000000000001,"F/I",2.089,"F/I",4.7892720306508133E-4]
[null,"Tap Off Mal Paso",110,"Tap Off Mal Paso 110 kV -  En Barra",null,null,2.9910000000000001,"N/A",3.0329999999999999,"N/A",1.404212637913735E-2]
[null,"Tap Off Malloa",154,"Tap Off Malloa 154 kV -  En Barra",null,null,15.138999999999999,"N/A",15.148,"N/A",5.9449104960699792E-4]
[null,"Tap Off Mayaca",110,"Tap Off Mayaca 110 kV - HX1 Línea 110kV TO Mayaca - TO Pachacama C1","HX1","S/I",18.022000000000002,"N/P",18.548000000000002,"N/P",2.9186549772500264E-2]
[null,null,110,"Tap Off Mayaca 110 kV - HX2 Línea 110kV TO Mayaca - TO Pachacama C2","HX2","S/I",18.022000000000002,"N/P",18.548000000000002,"N/P",2.9186549772500264E-2]
[null,null,110,"Tap Off Mayaca 110 kV - HX3 Línea 110kV TO Mayaca - San Pedro C1","HX3","S/I",15.786999999999999,"N/P",16.155000000000001,"N/P",2.3310318616583399E-2]
[null,null,110,"Tap Off Mayaca 110 kV - HX4 Línea 110kV TO Mayaca - San Pedro C2","HX4","S/I",15.786999999999999,"N/P",16.155000000000001,"N/P",2.3310318616583399E-2]
[null,null,110,"Tap Off Mayaca 110 kV - HX5 Línea 110kV TO Mayaca - Mayaca C1","HX5","S/I",22.349,"N/P",22.904,"N/P",2.4833325875878103E-2]
[null,null,110,"Tap Off Mayaca 110 kV - HX6 Línea 110kV TO Mayaca - Mayaca C2","HX6","S/I",22.35,"N/P",22.905000000000001,"N/P",2.4832214765100658E-2]
[null,"Tap Off Oeste ",110,"Tap Off Oeste  110 kV - H1 Línea 110 kV Tap Off Oeste (Oeste) - Minsal ","H1",40,1.9950000000000001,4.9875000000000003E-2,1.9960000000000002,4.9900000000000007E-2,5.0125313283213625E-4]
[null,"Petroquímicas",154,"Petroquímicas 154 kV -  En Barra",null,null,17.044,"N/A",17.613,"N/A",3.3384182116873919E-2]
[null,"Tap Off Punta Peuco",110,"Tap Off Punta Peuco 110 kV - HT3 Línea 110kV Tap Punta Peuco - Polpaico (Enel distribución)","HT3",31.5,14.448,0.45866666666666667,14.503,0.46041269841269844,3.8067552602436125E-3]
[null,null,110,"Tap Off Punta Peuco 110 kV - HL Línea 110kV Tap Punta Peuco - Central Loma los Colorados","HL",15,14,0.93333333333333335,14.055,0.93699999999999994,3.928571428571408E-3]
[null,null,110,"Tap Off Punta Peuco 110 kV - HT Línea 110kV Tap Punta Peuco - Punta Peuco (Cementos Polpaico)","HT",31.5,14.448,0.45866666666666667,14.503,0.46041269841269844,3.8067552602436125E-3]
[null,"Tap Off Punta Toro",110,"Tap Off Punta Toro 110 kV - L-1 Línea 110 kV Tap Punta Toro - Los Colorados ","L-1",10,4.7779999999999996,0.47779999999999995,4.7789999999999999,0.47789999999999999,2.0929259104234701E-4]
[null,"Tap Off Quiñenco",154,"Tap Off Quiñenco 154 kV -  En Barra",null,null,14.759,"N/A",16.780999999999999,"N/A",0.13700115183955541]
[null,"Central Río Melado",154,"Central Río Melado 154 kV - AT Línea 154 kV Tap Río Melado - Itahue2/Cipreses2","AT",31.5,5.0179999999999998,0.15930158730158731,5.0179999999999998,0.15930158730158731,0]
[null,"Tap Off Sairecabur (Sairecabur)",110,"Tap Off Sairecabur (Sairecabur) 110 kV - HT1 Transformador TR01 37,5MVA 110/3,45kV","HT1","S/I",2.1789999999999998,"F/I",2.1800000000000002,"F/I",4.5892611289597709E-4]
[null,null,110,"Tap Off Sairecabur (Sairecabur) 110 kV - HT2 Transformador TR02 37,5MVA 110/3,45kV","HT2","S/I",2.1789999999999998,"F/I",2.1800000000000002,"F/I",4.5892611289597709E-4]
[null,"Tap Off Santa Luisa",154,"Tap Off Santa Luisa 154 kV -  En Barra",null,null,4.883,"N/A",4.8849999999999998,"N/A",4.0958427196391146E-4]
[null,"Tap Off Tilcoco",154,"Tap Off Tilcoco 154 kV -  En Barra",null,null,14.779,"N/A",14.79,"N/A",7.4429934366325413E-4]
[null,"Tuniche",154,"Tuniche 154 kV -  En Barra",null,null,14.667999999999999,"N/A",14.68,"N/A",8.1810744477777851E-4]
[null,"Tap Off Uribe",110,"Tap Off Uribe 110 kV - H1 Acoplador  (Une los arranques (Uribe - Esmeralda con Antofagasta - Capricornio) ","H1","S/I",5.8360000000000003,"F/I",5.8419999999999996,"F/I",1.0281014393419018E-3]
[null,"Tap Off Vítor",110,"Tap Off Vítor 110 kV -  En Barra",null,null,1.8420000000000001,"N/A",1.8620000000000001,"N/A",1.0857763300760053E-2]
[null,"Tap Off Vítor N°2 Móvil (Movil Vítor)",110,"Tap Off Vítor N°2 Móvil (Movil Vítor) 110 kV - HTT Transformador  20/25/30MVA 110/23kV","HTT",31.5,1.4870000000000001,4.720634920634921E-2,1.5070000000000001,4.7841269841269844E-2,1.3449899125756568E-2]
[null,"Teno",154,"Teno 154 kV - AT1 Transformador TR1 154/13,2kV - 33,3 MVA","AT1",40,11.959,0.29897499999999999,11.965,0.29912499999999997,5.017141901496971E-4]
[null,null,154,"Teno 154 kV - AT2 Transformador TR2 154/13,2kV - 33,3 MVA","AT2",40,11.959,0.29897499999999999,11.965,0.29912499999999997,5.017141901496971E-4]
[null,null,154,"Teno 154 kV - AT Interruptor transformadores N°3 y N°5","AT",40,12.132999999999999,0.30332499999999996,12.138999999999999,0.30347499999999999,4.9451908019452963E-4]
[null,null,154,"Teno 154 kV - A9 Línea 154kV Teno - Paneles MDP Teno","A9",40,12.132999999999999,0.30332499999999996,12.138999999999999,0.30347499999999999,4.9451908019452963E-4]
[null,"Teno Empalme",154,"Teno Empalme 154 kV - A Línea 154 kV Teno Empalme - Teno","A",40,11.92,0.29799999999999999,11.928000000000001,0.29820000000000002,6.7114093959739054E-4]
[null,"Tierra Amarilla",110,"Tierra Amarilla 110 kV - HT1 Transformador T1 10-12MVA 110/23kV","HT1",40,7.9139999999999997,0.19785,7.9169999999999998,0.19792499999999999,3.7907505686127289E-4]
[null,null,110,"Tierra Amarilla 110 kV - HT2 Transformador T2 25-30MVA 110/23kV","HT2",40,7.9139999999999997,0.19785,7.9169999999999998,0.19792499999999999,3.7907505686127289E-4]
[null,null,110,"Tierra Amarilla 110 kV - H3  Línea 110kV Tierra Amarilla - Atacama Kozán","H3 ",25,6.2219999999999995,0.24887999999999999,6.2249999999999996,0.249,4.8216007714563063E-4]
[null,null,110,"Tierra Amarilla 110 kV - H4 Línea 110kV Tierra Amarilla - Plantas","H4",40,4.76,0.11899999999999999,4.7609999999999992,0.11902499999999998,2.1008403361332895E-4]
[null,"Tinguiririca",154,"Tinguiririca 154 kV - A3 Línea 154kV Tinguiririca - Convento Viejo/Itahue 2","A3",40,18.251000000000001,0.45627500000000004,18.262,0.45655000000000001,6.0270670100264271E-4]
[null,null,154,"Tinguiririca 154 kV - A4 Línea 154kV Tinguiririca - Itahue 1","A4",40,18.326000000000001,0.45815,18.337,0.45842499999999997,6.0024009603837347E-4]
[null,null,154,"Tinguiririca 154 kV - A8 Línea 154kV Tinguiririca - San Fernando C1","A8",40,19.597000000000001,0.48992500000000005,19.608999999999998,0.49022499999999997,6.1233862325850387E-4]
[null,null,154,"Tinguiririca 154 kV - AX Línea 154kV Tinguiririca - San Fernando C2","AX","S/I",19.594000000000001,"N/P",19.604999999999997,"N/P",5.613963458199285E-4]
[null,null,154,"Tinguiririca 154 kV - A9 Línea 154kV Tinguiririca - Rancagua 1/Alto Jahuel 1","A9","S/I",17.971000000000004,"F/I",17.980999999999998,"F/I",5.5645206165457991E-4]
[null,null,154,"Tinguiririca 154 kV - A10 Línea 154kV Tinguiririca - Rancagua 2/Alto Jahuel 2","A10","S/I",17.970000000000002,"F/I",17.980999999999998,"F/I",6.1213132999419465E-4]
[null,null,154,"Tinguiririca 154 kV - AT1 Transformador AT1 300MVA 220/154/69kV","AT1",40,10.577,0.26442500000000002,10.583,0.264575,5.6726860168291834E-4]
[null,"Torquemada",110,"Torquemada 110 kV - H1 Línea 110kV Loncura - Torquemada C1","H1",40,18.29,0.45724999999999999,19.362000000000002,0.48405000000000004,5.8611262985237986E-2]
[null,null,110,"Torquemada 110 kV - H2 Línea 110kV Loncura - Torquemada C2","H2",40,18.29,0.45724999999999999,19.362000000000002,0.48405000000000004,5.8611262985237986E-2]
[null,null,110,"Torquemada 110 kV - H11 Línea 110kV Torquemada - Miraflores 1","H11",40,18.599,0.46497500000000003,20.379000000000001,0.50947500000000001,9.5704070111296363E-2]
[null,null,110,"Torquemada 110 kV - H12 Línea 110kV Torquemada - Miraflores 2","H12",40,18.599,0.46497500000000003,20.379000000000001,0.50947500000000001,9.5704070111296363E-2]
[null,null,110,"Torquemada 110 kV - HR Acoplador","HR",40,22.344999999999999,0.55862499999999993,24.215,0.605375,8.3687625867084406E-2]
[null,null,110,"Torquemada 110 kV - H3 Línea 110kV Torquemada - Con Con 1","H3",40,20.463999999999999,0.51159999999999994,22.286999999999999,0.55717499999999998,8.9083268178264299E-2]
[null,null,110,"Torquemada 110 kV - H4 Línea 110kV Torquemada - Con Con 2","H4",40,20.463999999999999,0.51159999999999994,22.286999999999999,0.55717499999999998,8.9083268178264299E-2]
[null,null,110,"Torquemada 110 kV - H5 Línea 110kV Torquemada - Central Colmito","H5","S/I",20.896999999999998,"F/I",22.766999999999999,"F/I",8.9486529166866113E-2]
[null,null,110,"Torquemada 110 kV - H7 Línea 110kV Torquemada - Mauco 1","H7",40,21.477,0.53692499999999999,23.347000000000001,0.58367500000000005,8.7069888718163665E-2]
[null,null,110,"Torquemada 110 kV - H8 Línea 110kV Torquemada - Mauco 2","H8",40,21.477,0.53692499999999999,23.347000000000001,0.58367500000000005,8.7069888718163665E-2]
[null,"Totoralillo",110,"Totoralillo 110 kV - HT Transformador TR 33MVA 115/66kV","HT",40,8.3490000000000002,0.20872499999999999,8.363999999999999,0.20909999999999998,1.7966223499818891E-3]
[null,null,110,"Totoralillo 110 kV - H2 Línea 110kV Totoralillo - Aconcagua/Los Maquis 2","H2",40,4.6589999999999998,0.116475,4.665,0.11662500000000001,1.2878300064391988E-3]
[null,null,110,"Totoralillo 110 kV - H2A Línea 110kV Totoralillo - Nueva San Rafael","H2A",40,4.8320000000000007,0.12080000000000002,4.8379999999999992,0.12094999999999997,1.2417218543043151E-3]
[null,"Travesía",110,"Travesía 110 kV - H3 Línea 110kV Travesía - Punta Padrones/ EB2","H3",40,4.4669999999999996,0.111675,4.468,0.11169999999999999,2.2386389075449608E-4]
[null,null,110,"Travesía 110 kV - H2 Transformador TR1 110/23kV","H2",40,5.0149999999999997,0.12537499999999999,5.016,0.12540000000000001,1.9940179461621816E-4]
[null,"Uribe",110,"Uribe 110 kV - H2 Línea 110kV Uribe - Esmeralda/Tap Uribe","H2","S/I",6.6369999999999996,"F/I",6.6420000000000003,"F/I",7.5335241826138038E-4]
[null,null,110,"Uribe 110 kV - H3 Línea 110kV Uribe - Uribe Solar","H3","S/I",6.6349999999999998,"F/I",6.64,"F/I",7.5357950263751222E-4]
[null,null,110,"Uribe 110 kV - HT1 Transformador TR1 110/23kV","HT1","S/I",7.0220000000000002,"F/I",7.0259999999999998,"F/I",5.6963827969233258E-4]
[null,"Uribe Solar",110,"Uribe Solar 110 kV - H1 Línea 110kV Uribe Solar - Uribe","H1",40,4.9480000000000004,0.1237,4.9509999999999996,0.123775,6.0630557801116109E-4]
[null,"Valle de los vientos",110,"Valle de los vientos 110 kV - HT1 Transformador TR01 50/65MVA 110/23kV","HT1","S/I",4.9059999999999997,"F/I",4.9369999999999994,"F/I",6.3187933143089474E-3]
[null,null,110,"Valle de los vientos 110 kV - HT2 Transformador TR02 50/65MVA 110/23kV","HT2","S/I",4.9059999999999997,"F/I",4.9369999999999994,"F/I",6.3187933143089474E-3]
[null,null,110,"Valle de los vientos 110 kV - HL1 Línea 110kV Valle de los vientos - Calama","HL1","S/I",4.5330000000000004,"F/I",4.5670000000000002,"F/I",7.5005515111404818E-3]
[null,"Vallenar",110,"Vallenar 110 kV - HT1 Transformador TR01 y TR02","HT1",40,4.415,0.110375,4.415,0.110375,0]
[null,"Valparaíso",110,"Valparaíso 110 kV - HT1 Transformador TR1 25MVA 110/12kV","HT1",40,16.837,0.42092499999999999,17.074000000000002,0.42685000000000006,1.4076141830492479E-2]
[null,null,110,"Valparaíso 110 kV - HT2 Transformador TR2 25MVA 110/12kV","HT2",40,16.837,0.42092499999999999,17.074000000000002,0.42685000000000006,1.4076141830492479E-2]
[null,null,110,"Valparaíso 110 kV - HT3 Transformador TR3 25MVA 110/12kV","HT3",40,16.837,0.42092499999999999,17.074000000000002,0.42685000000000006,1.4076141830492479E-2]
[null,"Ventanas",110,"Ventanas 110 kV - HS1 Acoplador","HS1",40,31.651,0.79127499999999995,40.271999999999998,1.0067999999999999,0.27237686013080153]
[null,null,110,"Ventanas 110 kV - HS2 Acoplador","HS2",40,31.651,0.79127499999999995,40.271999999999998,1.0067999999999999,0.27237686013080153]
[null,null,110,"Ventanas 110 kV - HR Acoplador","HR",40,31.651,0.79127499999999995,40.271999999999998,1.0067999999999999,0.27237686013080153]
[null,null,110,"Ventanas 110 kV - H1 Línea 110kV Ventanas - San Pedro/Codelco Div. Ventanas C2","H1",40,28.704000000000001,0.71760000000000002,37.317,0.932925,0.30006270903010029]
[null,null,110,"Ventanas 110 kV - H2 Línea 110kV Ventanas - San Pedro/Codelco Div. Ventanas C1","H2",40,28.704000000000001,0.71760000000000002,37.317,0.932925,0.30006270903010029]
[null,null,110,"Ventanas 110 kV - H3 Línea 110kV Loncura - Ventanas C1","H3",40,28.613,0.71532499999999999,37.301000000000002,0.93252500000000005,0.30363820640967404]
[null,null,110,"Ventanas 110 kV - H4 Línea 110kV Loncura - Ventanas C2","H4",40,28.613,0.71532499999999999,37.301000000000002,0.93252500000000005,0.30363820640967404]
[null,null,110,"Ventanas 110 kV - H5 Línea 110kV Ventanas - Quintero (Chilquinta)","H5",40,31.651,0.79127499999999995,40.271999999999998,1.0067999999999999,0.27237686013080153]
[null,null,110,"Ventanas 110 kV - HX Línea 110kV Ventanas - El Bato","HX","S/I",31.651,"N/P",40.271999999999998,"N/P",0.27237686013080153]
[null,null,110,"Ventanas 110 kV - H6 Línea 110kV Ventanas - GNL Quintero","H6",40,28.341000000000001,0.70852500000000007,37.295000000000002,0.93237500000000006,0.31593804029497902]
[null,null,110,"Ventanas 110 kV - HT1 Transformador 3 devanado","HT1",40,21.183999999999997,0.52959999999999996,29.388999999999999,0.73472499999999996,0.38732061933534756]
[null,null,110,"Ventanas 110 kV - HTP Transformador TRP 20MVA 110/4,16kV","HTP","S/I",31.456,"F/I",40.034999999999997,"F/I",0.2727301627670396]
[null,null,110,"Ventanas 110 kV - HT4 Transformador T4 20MVA 110/4,16kV","HT4",40,31.456,0.78639999999999999,40.034999999999997,1.000875,0.2727301627670396]
[null,null,110,"Ventanas 110 kV - HT Aguas abajo paño HTP y HT4","HT",40,31.262,0.78154999999999997,39.798000000000002,0.99495,0.27304714989444057]
[null,null,110,"Ventanas 110 kV - HT1A Transformador TR1A 22,5MVA 110/13kV","HT1A",40,30.832000000000001,0.77080000000000004,38.137999999999998,0.95344999999999991,0.23696159833938757]
[null,null,110,"Ventanas 110 kV - HT1B Transformador TR1B 22,5MVA 110/13kV","HT1B",40,30.832000000000001,0.77080000000000004,38.15,0.95374999999999999,0.23735080435910735]
[null,null,110,"Ventanas 110 kV - HT2A Transformador TR2A 22,5MVA 110/18kV","HT2A",40,29.68,0.74199999999999999,35.314,0.88285000000000002,0.18982479784366579]
[null,null,110,"Ventanas 110 kV - HT2B Transformador TR2B 22,5MVA 110/18kV","HT2B",40,29.68,0.74199999999999999,35.314,0.88285000000000002,0.18982479784366579]
[null,"Vicuña",110,"Vicuña 110 kV - HT Transformador TR1 10/13MVA","HT",40,2.097,5.2424999999999999E-2,2.097,5.2424999999999999E-2,0]
[null,null,110,"Vicuña 110 kV - H2 Línea 110kV Vicuña - El Indio","H2",40,2.097,5.2424999999999999E-2,2.097,5.2424999999999999E-2,0]
[null,"Vitacura",110,"Vitacura 110 kV - HT1 Transformador TR1 50MVA 110/12,5kV","HT1",40,28.138999999999999,0.70347499999999996,28.215,0.70537499999999997,2.7008777852802345E-3]
[null,null,110,"Vitacura 110 kV - HT2 Transformador TR2 50MVA 110/12,5kV","HT2",40,28.138999999999999,0.70347499999999996,28.215,0.70537499999999997,2.7008777852802345E-3]
[null,null,110,"Vitacura 110 kV - HT3 Transformador TR3 50MVA 110/12,5kV","HT3",31.5,28.138999999999999,0.89330158730158726,28.215,0.89571428571428569,2.7008777852802345E-3]
[null,null,110,"Vitacura 110 kV - H4 Transformador TR4 50MVA 110/12,5kV","H4",31.5,28.138999999999999,0.89330158730158726,28.215,0.89571428571428569,2.7008777852802345E-3]
[null,null,110,"Vitacura 110 kV - HS1 Acoplador","HS1",40,28.138999999999999,0.70347499999999996,28.215,0.70537499999999997,2.7008777852802345E-3]
[null,null,110,"Vitacura 110 kV - H1 Línea 110kV Vitacura - Los Almendros/El Salto1","H1",40,14.07,0.35175000000000001,14.108000000000001,0.35270000000000001,2.7007818052594353E-3]
[null,null,110,"Vitacura 110 kV - H2 Línea 110kV Vitacura - Los Almendros/El Salto2","H2",40,14.069999999999999,0.35174999999999995,14.108000000000001,0.35270000000000001,2.7007818052595619E-3]
[null,"Yerbas Buenas",154,"Yerbas Buenas 154 kV - A1 Transformador T1 20MVA 154/13,2kV","A1",31.5,6.89,0.21873015873015872,6.8940000000000001,0.21885714285714286,5.8055152394781537E-4]
[null,"Yungay",110,"Yungay 110 kV -  En Barra",null,null,6.2389999999999999,"N/A",6.24,"N/A",1.6028209648987561E-4]
[null,"CD Combarbalá",110,"CD Combarbalá 110 kV - HTX Transformador Combarbalá 110/13,8 kV","HTX","S/I",2.7389999999999999,"N/P",2.7389999999999999,"N/P",0]
[null,"Alto Maipo",110,"Alto Maipo 110 kV - HTX1 Transformador U1 160 MVA 220/12 kV","HTX1","S/I",17.011000000000003,"N/P",17.021000000000001,"N/P",5.8785491740626702E-4]
[null,null,110,"Alto Maipo 110 kV - HTX2 Transformador U2 160 MVA 220/12 kV","HTX2","S/I",17.011000000000003,"N/P",17.021000000000001,"N/P",5.8785491740626702E-4]
[null,null,110,"Alto Maipo 110 kV - HX1 Línea 110 kV Alto Maipo - Maitenes","HX1","S/I",13.266999999999999,"N/P",13.273,"N/P",4.5224994346877424E-4]
[null,null,110,"Alto Maipo 110 kV - HX2 Línea 110 kV Alto Maipo - Tap La Laja C2","HX2","S/I",16.153000000000002,"N/P",16.16,"N/P",4.3335603293492825E-4]
[null,null,110,"Alto Maipo 110 kV - HX3 Línea 110 kV Alto Maipo - Tap La Laja C1","HX3","S/I",16.153000000000002,"N/P",16.16,"N/P",4.3335603293492825E-4]
[null,"Pueblo Seco",154,"Pueblo Seco 154 kV - HX1 Línea 154 kV Charrua - Pueblo Seco","HX1","S/I",5.7910000000000004,"N/P",5.7969999999999997,"N/P",1.0360904852355964E-3]
[null,null,154,"Pueblo Seco 154 kV - HX2 Línea 154 kV Pueblo Seco - Monterrico","HX2","S/I",5.7799999999999994,"N/P",5.7869999999999999,"N/P",1.2110726643599589E-3]
[null,null,154,"Pueblo Seco 154 kV - HTX Transformador 20MVA 154/23kV","HTX","S/I",7.8929999999999998,"N/P",7.9009999999999998,"N/P",1.0135563157227933E-3]
[null,"La Ruca",110,"La Ruca 110 kV - HX1 Línea El Peñón - La Ruca 110 kV C1","HX1","S/I",3.5750000000000002,"N/P",3.5759999999999996,"N/P",2.7972027972012468E-4]
[null,null,110,"La Ruca 110 kV - HX2 Línea El Peñón - La Ruca 110 kV C2","HX2","S/I",3.5620000000000003,"N/P",3.5619999999999994,"N/P",-2.4934823686134903E-16]
[null,null,110,"La Ruca 110 kV - HX3 Línea La Ruca - Ovalle 110 kV C1","HX3","S/I",4.7110000000000003,"N/P",4.7119999999999997,"N/P",2.1226915729132789E-4]
[null,null,110,"La Ruca 110 kV - HX4 Línea La Ruca - Ovalle 110 kV C2","HX4","S/I",4.7060000000000004,"N/P",4.7069999999999999,"N/P",2.124946876326914E-4]
[null,"Nueva Panquehue",110,"Nueva Panquehue 110 kV - HX1 Línea 110kV Fundición Chagres - Nueva Panquehue","HX1","S/I",10.48,"N/P",10.541999999999998,"N/P",5.9160305343509169E-3]
[null,null,110,"Nueva Panquehue 110 kV - HX2 Línea 110kV Tap Chagres - Nueva Panquehue","HX2","S/I",8.7920000000000016,"N/P",8.8419999999999987,"N/P",5.6869881710642795E-3]
[null,null,110,"Nueva Panquehue 110 kV - HX3 Línea 110kV Nueva Panquehue - Tap San Felipe C1","HX3","S/I",14.709,"N/P",14.810999999999998,"N/P",6.9345298796654117E-3]
[null,null,110,"Nueva Panquehue 110 kV - HX4 Línea 110kV Nueva Panquehue - Tap San Felipe C2","HX4","S/I",14.709,"N/P",14.810999999999998,"N/P",6.9345298796654117E-3]
[null,null,110,"Nueva Panquehue 110 kV - HTX Transformador 30MVA 110/13,8kV","HTX","S/I",16.23,"N/P",16.335999999999999,"N/P",6.5311152187306279E-3]
[null,"Río Aconcagua",110,"Río Aconcagua 110 kV - HX1 Línea 110 kV  Esperanza (HASA) - Río Aconcagua C1","HX1","S/I",21.045999999999999,"N/P",21.286000000000001,"N/P",1.1403592131521523E-2]
[null,null,110,"Río Aconcagua 110 kV - HX2 Línea 110 kV  Esperanza (HASA) - Río Aconcagua C2","HX2","S/I",21.045999999999999,"N/P",21.286000000000001,"N/P",1.1403592131521523E-2]
[null,null,110,"Río Aconcagua 110 kV - HX3 Línea 110 kV Fundición Chagres - Río Aconcagua C1","HX3","S/I",25.413999999999998,"N/P",25.753,"N/P",1.3339104430628874E-2]
[null,null,110,"Río Aconcagua 110 kV - HX4 Línea 110 kV Fundición Chagres - Río Aconcagua C2","HX4","S/I",25.452999999999999,"N/P",25.792000000000002,"N/P",1.3318665776136494E-2]
[null,null,110,"Río Aconcagua 110 kV - HTX Transformador 350MVA 220/110/13.2 kV","HTX","S/I",13.814,"N/P",14.011000000000001,"N/P",1.4260894744462209E-2]
[null,"Nueva San Rafael",110,"Nueva San Rafael 110 kV - HX1 Línea 110kV Nueva San Rafael - San Rafael C1","HX1","S/I",10.146000000000001,"N/P",10.172000000000001,"N/P",2.5625862408830869E-3]
[null,null,110,"Nueva San Rafael 110 kV - HX2 Línea 110kV Nueva San Rafael - San Rafael C2","HX2","S/I",10.146000000000001,"N/P",10.172000000000001,"N/P",2.5625862408830869E-3]
[null,null,110,"Nueva San Rafael 110 kV - HX3 Línea 110kV Nueva San Rafael - Tap San Felipe C1","HX3","S/I",7.3410000000000011,"N/P",7.3560000000000008,"N/P",2.0433183489987302E-3]
[null,null,110,"Nueva San Rafael 110 kV - HX4 Línea 110kV Nueva San Rafael - Tap San Felipe C2","HX4","S/I",7.3410000000000011,"N/P",7.3560000000000008,"N/P",2.0433183489987302E-3]
[null,null,110,"Nueva San Rafael 110 kV - HX5 Línea 110kV Nueva San Rafael - Tap Los Maquis","HX5","S/I",7.8560000000000008,"N/P",7.8790000000000004,"N/P",2.9276985743380453E-3]
[null,null,110,"Nueva San Rafael 110 kV - HX6 Línea 110kV Nueva San Rafael - Totoralillo","HX6","S/I",7.8370000000000006,"N/P",7.8600000000000012,"N/P",2.9347964782442991E-3]
[null,"Guardiamarina",110,"Guardiamarina 110 kV - HX1 Línea 110kV Guardiamarina - Tap Off Desalant","HX1","S/I",6.2990000000000004,"N/P",6.3040000000000003,"N/P",7.9377678996664445E-4]
[null,null,110,"Guardiamarina 110 kV - HX2 Línea 110kV Guardiamarina - Antofagasta","HX2","S/I",4.8070000000000004,"N/P",4.8109999999999999,"N/P",8.3211982525474495E-4]
[null,null,110,"Guardiamarina 110 kV - HX3 Línea 110kV Guardiamarina - Esmeralda","HX3","S/I",5.4480000000000004,"N/P",5.452,"N/P",7.3421439060197488E-4]
[null,null,110,"Guardiamarina 110 kV - HX4 Línea 110kV Guardiamarina - La Portada","HX4","S/I",8.2469999999999999,"N/P",8.2539999999999996,"N/P",8.4879350066686954E-4]
[null,null,110,"Guardiamarina 110 kV - HTX1 Transformador 30MVA 110/23kV","HTX1","S/I",8.2680000000000007,"N/P",8.2750000000000004,"N/P",8.4663763909042968E-4]
[null,null,110,"Guardiamarina 110 kV - HTX2 Transformador 50MVA 110/13,8kV","HTX2","S/I",8.2680000000000007,"N/P",8.2750000000000004,"N/P",8.4663763909042968E-4]
[null,"La Pólvora",110,"La Pólvora 110 kV - HTX Transformador 150MVA 220/110/23kV","HTX","S/I",14.219000000000001,"N/P",14.486000000000001,"N/P",1.8777691820803112E-2]
[null,null,110,"La Pólvora 110 kV - HX1 Línea 110kV La Pólvora - Tap Placeres C1","HX1","S/I",13.615,"N/P",13.738,"N/P",9.0341535071611703E-3]
[null,null,110,"La Pólvora 110 kV - HX2 Línea 110kV La Pólvora - Tap Placeres C2","HX2","S/I",13.615,"N/P",13.738,"N/P",9.0341535071611703E-3]
[null,null,110,"La Pólvora 110 kV - HX3 Línea 110kV La Pólvora - Central Laguna verde C1","HX3","S/I",17.861000000000001,"N/P",18.163,"N/P",1.6908347796875851E-2]
[null,null,110,"La Pólvora 110 kV - HX4 Línea 110kV La Pólvora - Central Laguna Verde C2","HX4","S/I",17.861000000000001,"N/P",18.163,"N/P",1.6908347796875851E-2]
[null,null,110,"La Pólvora 110 kV - HX5 Línea 110kV La Pólvora - Playa Ancha C1","HX5","S/i",19.056000000000001,"N/P",19.338999999999999,"N/P",1.4850965575146815E-2]
[null,null,110,"La Pólvora 110 kV - HX6 Línea 110kV La Pólvora - Playa Ancha C2","HX6","S/I",19.056000000000001,"N/P",19.338999999999999,"N/P",1.4850965575146815E-2]
[null,null,110,"La Pólvora 110 kV - HX7 Línea 110kV La Pólvora - Valparaíso C1","HX7","S/I",19.056000000000001,"N/P",19.338999999999999,"N/P",1.4850965575146815E-2]
[null,null,110,"La Pólvora 110 kV - HX8 Línea 110kV La Pólvora - Valparaíso C2","HX8","S/I",19.056000000000001,"N/P",19.338999999999999,"N/P",1.4850965575146815E-2]
[null,"Nueva La Negra",110,"Nueva La Negra 110 kV - HTX Transformador 120MVA 220/110kV","HTX","S/I",5.4640000000000004,"N/P",5.468,"N/P",7.3206442166902624E-4]
[null,null,110,"Nueva La Negra 110 kV - HT1 Transformador TR1 110/23kV","HT1","S/I",9.2000000000000011,"F/I",9.2090000000000014,"F/I",9.7826086956525433E-4]
[null,null,110,"Nueva La Negra 110 kV - HT2 Transformador TR2 110/23kV","HT2","S/I",9.2189999999999994,"F/I",9.2279999999999998,"F/I",9.7624471200784702E-4]
[null,null,110,"Nueva La Negra 110 kV - HX1 Línea 110kV Nueva La Negra - Antofagasta","HX1","S/I",6.702,"N/P",6.706999999999999,"N/P",7.4604595643076768E-4]
[null,null,110,"Nueva La Negra 110 kV - HX3 Línea 110kV Nueva La Negra - Alto Norte","HX3","S/I",8.0220000000000002,"N/P",8.0279999999999987,"N/P",7.4794315631992656E-4]
[null,"Loncura",110,"Loncura 110 kV - HTX Transformador 20MVA 110/12kV","HTX","S/I",22.138000000000002,"N/P",26.466999999999999,"N/P",0.19554611979401917]
[null,null,110,"Loncura 110 kV - HX1 Línea 110kV Loncura - Ventanas C1","HX1","S/I",15.157000000000002,"N/P",17.387999999999998,"N/P",0.14719271623672206]
[null,null,110,"Loncura 110 kV - HX2 Línea 110kV Loncura - Ventanas C2","HX2","S/I",15.157000000000002,"N/P",17.387999999999998,"N/P",0.14719271623672206]
[null,null,110,"Loncura 110 kV - HX3 Línea 110kV Loncura - Torquemada C1","HX3","S/I",18.038000000000004,"N/P",22.302999999999997,"N/P",0.23644528218205968]
[null,null,110,"Loncura 110 kV - HX4 Línea 110kV Loncura - Torquemada C2","HX4","S/I",18.038000000000004,"N/P",22.302999999999997,"N/P",0.23644528218205968]
[null,"Ilque",110,"Ilque 110 kV - HX1 Línea 110kV Ilique - Calbuco","HX1","S/I",3.23,"N/P",3.23,"N/P",0]
[null,null,110,"Ilque 110 kV - HX2 Línea 110kV Ilique - El Empalme","HX2","S/I",3.23,"N/P",3.23,"N/P",0]
[null,"Damascal",110,"Damascal 110 kV - HX1 Transformador 30MVA 110/23kV","HX1","S/I",3.694,"N/P",3.694,"N/P",0]
[null,null,110,"Damascal 110 kV - HX2 Línea 110kV Damascal - Vicuña","HX2","S/I",3.694,"N/P",3.694,"N/P",0]
[null,null,110,"Damascal 110 kV - HX3 Línea 110kV Damascal - Pan de Azúcar","HX3","S/I",3.694,"N/P",3.694,"N/P",0]
[null,"Litueche",110,"Litueche 110 kV - HX1 Línea 110kV Litueche - Quelentaro","HX1","S/I",4.5949999999999998,"N/P",4.5970000000000004,"N/P",4.3525571273137496E-4]
[null,null,110,"Litueche 110 kV - HX2 Línea 110kV Litueche - Portezuelo","HX2","S/I",4.59,"N/P",4.5919999999999996,"N/P",4.3572984749450539E-4]
[null,"Codegua",110,"Codegua 110 kV - HTX Transformador 100MVA 110/66kV","HTX","S/I",12.798,"N/P",12.805999999999999,"N/P",6.2509767151110477E-4]
[null,null,110,"Codegua 110 kV - HX1 Línea 110kV Codegua - Alto Jahuel C1","HX1","S/I",11.327,"N/P",11.334,"N/P",6.1799240752182156E-4]
[null,null,110,"Codegua 110 kV - HX2 Línea 110kV Codegua - Alto Jahuel C2","HX2","S/I",11.327,"N/P",11.334,"N/P",6.1799240752182156E-4]
[null,null,110,"Codegua 110 kV - HX3 Línea 110kV Codegua - Sauzal C1","HX3","S/I",11.270999999999999,"N/P",11.279,"N/P",7.0978617691428412E-4]
[null,null,110,"Codegua 110 kV - HX4 Línea 110kV Codegua - Sauzal C2","HX4","S/I",11.270999999999999,"N/P",11.279,"N/P",7.0978617691428412E-4]
[null,"Trupán",154,"Trupán 154 kV - HX1 Línea 154kV Trupán - Abanico","HX1","S/I",3.2710000000000004,"N/P",3.2719999999999998,"N/P",3.0571690614474034E-4]
[null,null,154,"Trupán 154 kV - HX2 Línea 154kV Trupán - Charrúa","HX2","S/I",3.016,"N/P",3.0169999999999999,"N/P",3.3156498673736403E-4]
[null,null,154,"Trupán 154 kV - HTX Transformador 20MVA 154/13.8kV","HTX","S/I",5.2279999999999998,"N/P",5.2289999999999992,"N/P",1.9127773527150837E-4]
[null,"Alfalfal",110,"Alfalfal 110 kV - HX Línea 110kV Alfalfal - Central Maitenes","HX","S/I",9.6349999999999998,"N/P",9.6389999999999993,"N/P",4.1515308770104405E-4]
[null,null,110,"Alfalfal 110 kV - HTX Transformador 200MVA 220/110715MkV","HTX","S/I",9.5609999999999999,"N/P",9.5640000000000001,"N/P",3.1377470975840538E-4]