## CPF Mensual
Desempeño Control Primario de Frecuencia SEN
Mes: | 2020-10-01
Unidad | Respuesta CPF (Fact_CPF) | Disponibilidad (Fdis_CPF) | Desempeño (DCPF) | Factor de Desempeño (Fd_CPF) | Cuenta con equipo registrador validado
HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
HE ANGOSTURA U3 | 97% | 100% | 97% | 100% | SI
HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
HE ANTUCO U2 | No Participó | 0.00224% | 0.00224% | 0% | SI
HE CANUTILLAR U1 | 98% | 100% | 98% | 100% | SI
HE CANUTILLAR U2 | 98% | 100% | 98% | 100% | SI
HE CIPRESES U1 | 99% | 98.54% | 97.56% | 100% | SI
HE CIPRESES U2 | 67% | 99.08% | 66.38% | 0% | SI
HE CIPRESES U3 | 96% | 96.51% | 92.65% | 93% | SI
HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
HE PANGUE U1 | 96% | 48.33% | 46.4% | 0% | SI
HE PANGUE U2 | No Participó | 0.00224% | 0.00224% | 0% | SI
HE PEHUENCHE U1 | 96% | 100% | 96% | 100% | SI
HE PEHUENCHE U2 | 95% | 100% | 95% | 95% | SI
HE RALCO U1 | 93% | 100% | 93% | 93% | SI
HE RALCO U2 | 93% | 99.41% | 92.45% | 92% | SI
HE RAPEL U1 | 100% | 95.39% | 95.39% | 100% | SI
HE RAPEL U2 | 89% | 99.46% | 88.52% | 89% | SI
HE RAPEL U3 | 98% | 99.46% | 97.47% | 100% | SI
HE RAPEL U4 | 99% | 99.46% | 98.46% | 100% | SI
HE RAPEL U5 | No Participó | 99.46% | 99.46% | 100% | SI
TER ANDINA U1 | 80% | 0.05376% | 0.04301% | 0% | SI
TER ANGAMOS U1 | 67% | 98.21% | 65.8% | 0% | SI
TER ANGAMOS U2 | No Verificable | 99.68% | 0% | 0% | NO
TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
TER ATACAMA CC1-TG2 | No Verificable | 99.77% | 0% | 0% | NO
TER ATACAMA CC2-TG1 | No Verificable | 88.3% | 0% | 0% | NO
TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
TER COCHRANE U1 | No Verificable | 99.6% | 0% | 0% | NO
TER COCHRANE U2 | 82% | 97.03% | 79.57% | 80% | SI
TER GUACOLDA U3 | 91% | 99.3% | 90.36% | 90% | SI
TER GUACOLDA U4 | 92% | 100% | 92% | 92% | SI
TER HORNITOS U1 | 100% | 87.44% | 87.44% | 87% | SI
TER IEM U1 | 85% | 100% | 85% | 85% | SI
TER KELAR CC1-TG1 | 97% | 98.73% | 95.77% | 100% | SI
TER KELAR CC1-TG2 | 97% | 98.87% | 95.9% | 100% | SI
TER MEJILLONES CTM1 | 60% | 73.1% | 43.86% | 0% | SI
TER MEJILLONES CTM2 | 39% | 31.41% | 12.25% | 0% | SI
TER MEJILLONES CTM3-TG | 90% | 99.45% | 89.5% | 90% | SI
TER NORGENER U1 | 74% | 100% | 74% | 0% | SI
TER NORGENER U2 | 55% | 100% | 55% | 0% | SI
TER QUINTERO U1 | 70% | 98.9% | 69.23% | 0% | SI
TER QUINTERO U2 | 65% | 100% | 65% | 0% | SI
TER TALTAL U1 | 58% | 100% | 58% | 0% | SI
TER TALTAL U2 | No Verificable (1) | 99.75% | 0% | 0% | SI
TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
TER TOCOPILLA TG3 | No Verificable | 0.00224% | 0% | 0% | NO
TER TOCOPILLA U14 | 91% | 46.42% | 42.25% | 0% | SI
TER TOCOPILLA U15 | 53% | 100% | 53% | 0% | SI
TER TOCOPILLA U16-TG-TV | 89% | 92.82% | 82.61% | 83% | SI
(1) Los registros no tienen información suficiente para la evaluación confiable (defectuosos)

## CPF Horario
Desempeño Control Primario de Frecuencia SEN
Mes: | 2020-10-01
Fecha | Hora | Unidad | Respuesta CPF (Fact_CPF) | Disponibilidad (Fdis_CPF) | Desempeño (DCPF) | Factor de Desempeño (Fd_CPF) | Cuenta con equipo registrador validado
2020-10-01 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 0 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 1 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 11 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 13 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 14 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 15 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 12 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 20 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 21 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 10 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 20 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 21 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 2 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 2 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | HE COLBÚN U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE PANGUE U1 | 66% | 100% | 66% | 0% | SI
2020-10-01 | 1 | HE PANGUE U1 | 75% | 100% | 75% | 75% | SI
2020-10-01 | 2 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 4 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE PANGUE U1 | 50% | 100% | 50% | 0% | SI
2020-10-01 | 7 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 10 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 11 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 12 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 13 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 17 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 19 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 20 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 0 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 2 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 4 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 5 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 6 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 7 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 8 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 10 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 11 | HE PEHUENCHE U1 | 50% | 100% | 50% | 0% | SI
2020-10-01 | 12 | HE PEHUENCHE U1 | 67% | 100% | 67% | 0% | SI
2020-10-01 | 13 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 16 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 19 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 22 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 23 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 2 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 4 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 5 | HE PEHUENCHE U2 | 67% | 100% | 67% | 0% | SI
2020-10-01 | 6 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 8 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 10 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 11 | HE PEHUENCHE U2 | 67% | 100% | 67% | 0% | SI
2020-10-01 | 12 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 13 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 14 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 15 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 21 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 22 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 1 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 2 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 3 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 4 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 5 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 6 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 7 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 8 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 9 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 10 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 11 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 12 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 13 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 14 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 15 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 16 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 17 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 18 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 19 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 20 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 21 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 22 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 23 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 0 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 1 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 2 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 3 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 4 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 5 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 6 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 7 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 8 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 9 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 10 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 11 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 12 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 13 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 14 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 15 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 17 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 18 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 19 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 20 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 21 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 22 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 23 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE RAPEL U4 | 75% | 100% | 75% | 75% | SI
2020-10-01 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | TER ANDINA U1 | 80% | 13.33% | 10.67% | 0% | SI
2020-10-01 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 0 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 1 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 2 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 3 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 4 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 5 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 6 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 7 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 8 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 9 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-01 | 10 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 11 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 12 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 13 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 14 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 15 | TER COCHRANE U2 | 75% | 100% | 75% | 75% | SI
2020-10-01 | 16 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-01 | 17 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 18 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 19 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 20 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 21 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-01 | 22 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 23 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 0 | TER GUACOLDA U3 | 40% | 100% | 40% | 0% | SI
2020-10-01 | 1 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-01 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 3 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 4 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 8 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 9 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 10 | TER GUACOLDA U3 | 80% | 100% | 80% | 80% | SI
2020-10-01 | 11 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | TER GUACOLDA U3 | 0% | 100% | 0% | 0% | SI
2020-10-01 | 14 | TER GUACOLDA U3 | 80% | 100% | 80% | 80% | SI
2020-10-01 | 15 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 19 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 21 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 22 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 23 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 0 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 1 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 2 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 3 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 4 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 5 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 6 | TER GUACOLDA U4 | 34% | 100% | 34% | 0% | SI
2020-10-01 | 7 | TER GUACOLDA U4 | 66% | 100% | 66% | 0% | SI
2020-10-01 | 8 | TER GUACOLDA U4 | 25% | 100% | 25% | 0% | SI
2020-10-01 | 9 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | TER GUACOLDA U4 | 40% | 100% | 40% | 0% | SI
2020-10-01 | 11 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | TER GUACOLDA U4 | 33% | 100% | 33% | 0% | SI
2020-10-01 | 14 | TER GUACOLDA U4 | 60% | 100% | 60% | 0% | SI
2020-10-01 | 15 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 16 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 20 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 21 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 22 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 23 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 0 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | TER HORNITOS U1 | 80% | 100% | 80% | 80% | SI
2020-10-01 | 3 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | TER HORNITOS U1 | No Participó | 11.67% | 11.67% | 0% | SI
2020-10-01 | 8 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 9 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 10 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 11 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 12 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 13 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 14 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 15 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 16 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 17 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 18 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 19 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 20 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 21 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 22 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 23 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | TER IEM U1 | 60% | 100% | 60% | 0% | SI
2020-10-01 | 3 | TER IEM U1 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 4 | TER IEM U1 | 67% | 100% | 67% | 0% | SI
2020-10-01 | 5 | TER IEM U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 6 | TER IEM U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 7 | TER IEM U1 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 8 | TER IEM U1 | 33% | 100% | 33% | 0% | SI
2020-10-01 | 9 | TER IEM U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 10 | TER IEM U1 | 40% | 100% | 40% | 0% | SI
2020-10-01 | 11 | TER IEM U1 | 50% | 100% | 50% | 0% | SI
2020-10-01 | 12 | TER IEM U1 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 13 | TER IEM U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 14 | TER IEM U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 15 | TER IEM U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER IEM U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER IEM U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER IEM U1 | 67% | 100% | 67% | 0% | SI
2020-10-01 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 4 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 5 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 6 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 7 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 8 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 9 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 1 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-01 | 2 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-01 | 3 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER MEJILLONES CTM3-TG | 50% | 100% | 50% | 0% | SI
2020-10-01 | 13 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-01 | 14 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-01 | 15 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-01 | 19 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-01 | 20 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-01 | 21 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-01 | 22 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-01 | 23 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-01 | 0 | TER NORGENER U1 | 40% | 100% | 40% | 0% | SI
2020-10-01 | 1 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-01 | 2 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-01 | 3 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-01 | 4 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-01 | 5 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-01 | 6 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-01 | 7 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 8 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 9 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-01 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 19 | TER NORGENER U1 | 0% | 100% | 0% | 0% | SI
2020-10-01 | 20 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 21 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-01 | 22 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-01 | 23 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-01 | 0 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-01 | 1 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-01 | 2 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-01 | 3 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-01 | 4 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-01 | 5 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-01 | 6 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-01 | 7 | TER NORGENER U2 | 34% | 100% | 34% | 0% | SI
2020-10-01 | 8 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-01 | 9 | TER NORGENER U2 | 25% | 100% | 25% | 0% | SI
2020-10-01 | 10 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-01 | 11 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-01 | 12 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-01 | 13 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 14 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-01 | 15 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-01 | 16 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-01 | 17 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER NORGENER U2 | 34% | 100% | 34% | 0% | SI
2020-10-01 | 19 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-01 | 20 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-01 | 21 | TER NORGENER U2 | 34% | 100% | 34% | 0% | SI
2020-10-01 | 22 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-01 | 23 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-01 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-01 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-01 | 0 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-01 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 38.33% | 38.33% | 0% | SI
2020-10-01 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-01 | 19 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 20 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 21 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-01 | 22 | TER TOCOPILLA U16-TG-TV | 75% | 100% | 75% | 75% | SI
2020-10-01 | 23 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 0 | HE CANUTILLAR U1 | 80% | 100% | 80% | 80% | SI
2020-10-02 | 1 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 20 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 21 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 10 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 20 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 21 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 2 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE PANGUE U1 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 1 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 2 | HE PANGUE U1 | 75% | 100% | 75% | 75% | SI
2020-10-02 | 3 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 5 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 6 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 7 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 9 | HE PANGUE U1 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 10 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 11 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 12 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE PANGUE U1 | 66% | 100% | 66% | 0% | SI
2020-10-02 | 15 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 16 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 19 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 20 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 22 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 0 | HE PEHUENCHE U1 | 80% | 100% | 80% | 80% | SI
2020-10-02 | 1 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 2 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 3 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 4 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 5 | HE PEHUENCHE U1 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 6 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 7 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 8 | HE PEHUENCHE U1 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 13 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 14 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 17 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE PEHUENCHE U1 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 22 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 2 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 4 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 6 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 8 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 9 | HE PEHUENCHE U2 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 10 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 13 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 14 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE PEHUENCHE U2 | 60% | 100% | 60% | 0% | SI
2020-10-02 | 17 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 18 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE PEHUENCHE U2 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 22 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 1 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 2 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 3 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 4 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 5 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 6 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 7 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 8 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 9 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 10 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 11 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 12 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 13 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 14 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 15 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 16 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 17 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 18 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 19 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 20 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 21 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 22 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 23 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 0 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 1 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 2 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 3 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 4 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 5 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 6 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 7 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 8 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 9 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 10 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 11 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 12 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 13 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 14 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 15 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 17 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 18 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 19 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 20 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 21 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 22 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 23 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 0 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 1 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 2 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 3 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 4 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 5 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 6 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-02 | 7 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 8 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 9 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 10 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 11 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 12 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-02 | 13 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-02 | 14 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-02 | 15 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 16 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 17 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 18 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 19 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-02 | 20 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 21 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 22 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 0 | TER GUACOLDA U3 | 80% | 100% | 80% | 80% | SI
2020-10-02 | 1 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 16 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 18 | TER GUACOLDA U3 | 75% | 100% | 75% | 75% | SI
2020-10-02 | 19 | TER GUACOLDA U3 | 50% | 100% | 50% | 0% | SI
2020-10-02 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 21 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 22 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 23 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 0 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 1 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 2 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 3 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 4 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 5 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 6 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 7 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 8 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 9 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 10 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 11 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 12 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 13 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 14 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 16 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 17 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 18 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 20 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 21 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 22 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 23 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 0 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 1 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 2 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 3 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 4 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 5 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 6 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 7 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 8 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 9 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 10 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 11 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 12 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 13 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 14 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 15 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 16 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 17 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 18 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 19 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 20 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 21 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 22 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 23 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-02 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | TER IEM U1 | 80% | 100% | 80% | 80% | SI
2020-10-02 | 8 | TER IEM U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 9 | TER IEM U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER IEM U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 11 | TER IEM U1 | 66% | 100% | 66% | 0% | SI
2020-10-02 | 12 | TER IEM U1 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 13 | TER IEM U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER IEM U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER IEM U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 16 | TER IEM U1 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 17 | TER IEM U1 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 18 | TER IEM U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 1 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 2 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 3 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 4 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 5 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 6 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 7 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 8 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 9 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 11 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 12 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 13 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 16 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 17 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 18 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 19 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 20 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 21 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-02 | 22 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 23 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-02 | 0 | TER NORGENER U1 | 40% | 100% | 40% | 0% | SI
2020-10-02 | 1 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-02 | 2 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 3 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 4 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-02 | 5 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 6 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 7 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-02 | 8 | TER NORGENER U1 | 0% | 100% | 0% | 0% | SI
2020-10-02 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER NORGENER U1 | 49% | 100% | 49% | 0% | SI
2020-10-02 | 11 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-02 | 12 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 19 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 20 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 21 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-02 | 22 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-02 | 23 | TER NORGENER U1 | 34% | 100% | 34% | 0% | SI
2020-10-02 | 0 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-02 | 1 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-02 | 2 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-02 | 3 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 4 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-02 | 5 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-02 | 6 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-02 | 7 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-02 | 8 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-02 | 9 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-02 | 10 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-02 | 11 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 12 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-02 | 13 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-02 | 15 | TER NORGENER U2 | 49% | 100% | 49% | 0% | SI
2020-10-02 | 16 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 17 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-02 | 18 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-02 | 19 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 20 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-02 | 21 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-02 | 22 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-02 | 23 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-02 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | TER TALTAL U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 21 | TER TALTAL U1 | 83% | 100% | 83% | 83% | SI
2020-10-02 | 22 | TER TALTAL U1 | 67% | 100% | 67% | 0% | SI
2020-10-02 | 23 | TER TALTAL U1 | 17% | 100% | 17% | 0% | SI
2020-10-02 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-02 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-02 | 0 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 0 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 1 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 2 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 3 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 4 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 5 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-02 | 6 | TER TOCOPILLA U16-TG-TV | 80% | 100% | 80% | 80% | SI
2020-10-02 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-02 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE CANUTILLAR U2 | 80% | 100% | 80% | 80% | SI
2020-10-03 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 20 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 21 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 10 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 20 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 21 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 1 | HE PANGUE U1 | 75% | 100% | 75% | 75% | SI
2020-10-03 | 2 | HE PANGUE U1 | 75% | 100% | 75% | 75% | SI
2020-10-03 | 3 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE PANGUE U1 | 67% | 100% | 67% | 0% | SI
2020-10-03 | 8 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 10 | HE PANGUE U1 | 66% | 100% | 66% | 0% | SI
2020-10-03 | 11 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 13 | HE PANGUE U1 | 75% | 100% | 75% | 75% | SI
2020-10-03 | 14 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 15 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 16 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 18 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 19 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 20 | HE PANGUE U1 | 17% | 100% | 17% | 0% | SI
2020-10-03 | 21 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 22 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 0 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 3 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 5 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 7 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 14 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 15 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE PEHUENCHE U1 | 50% | 100% | 50% | 0% | SI
2020-10-03 | 20 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 21 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 22 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 2 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 3 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 7 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 12 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 14 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 15 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 18 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE PEHUENCHE U2 | 50% | 100% | 50% | 0% | SI
2020-10-03 | 20 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 21 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 22 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 0 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 1 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 2 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 3 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 4 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 5 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 6 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 7 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 8 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 9 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 10 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 11 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 12 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 13 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 14 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 15 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 16 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 17 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 18 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 19 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 20 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 21 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 22 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 23 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 0 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 1 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 2 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 3 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 4 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 5 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 6 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 7 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 8 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 9 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 10 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 11 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 12 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 13 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 14 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 15 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 17 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 18 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 19 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 20 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 21 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 22 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 23 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 0 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 1 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 2 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 3 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 4 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 5 | TER COCHRANE U2 | 17% | 100% | 17% | 0% | SI
2020-10-03 | 6 | TER COCHRANE U2 | 75% | 100% | 75% | 75% | SI
2020-10-03 | 7 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-03 | 8 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-03 | 9 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-03 | 10 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 11 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-03 | 12 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-03 | 13 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-03 | 14 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 15 | TER COCHRANE U2 | 60% | 100% | 60% | 0% | SI
2020-10-03 | 16 | TER COCHRANE U2 | 0% | 100% | 0% | 0% | SI
2020-10-03 | 17 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 18 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 19 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 20 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 21 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 22 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 23 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 0 | TER GUACOLDA U3 | 80% | 100% | 80% | 80% | SI
2020-10-03 | 1 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 21 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 22 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 23 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 0 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 1 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 2 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 3 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 4 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 5 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 6 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 8 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 9 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 10 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 11 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 12 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 13 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 14 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 16 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 18 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 19 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 20 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 21 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 22 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 23 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 0 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 1 | TER HORNITOS U1 | No Participó | 6.667% | 6.667% | 0% | SI
2020-10-03 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 9 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 10 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 11 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER IEM U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 4 | TER IEM U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 5 | TER IEM U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER IEM U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 8 | TER IEM U1 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 9 | TER IEM U1 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 10 | TER IEM U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER IEM U1 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 12 | TER IEM U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER IEM U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER IEM U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER IEM U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER IEM U1 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 17 | TER IEM U1 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 18 | TER IEM U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 19 | TER IEM U1 | 17% | 100% | 17% | 0% | SI
2020-10-03 | 20 | TER IEM U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 21 | TER IEM U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 22 | TER IEM U1 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 23 | TER IEM U1 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | TER KELAR CC1-TG1 | 75% | 100% | 75% | 75% | SI
2020-10-03 | 2 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER KELAR CC1-TG1 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 4 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 5 | TER KELAR CC1-TG1 | 17% | 100% | 17% | 0% | SI
2020-10-03 | 6 | TER KELAR CC1-TG1 | 67% | 100% | 67% | 0% | SI
2020-10-03 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER KELAR CC1-TG2 | No Participó | 28.33% | 28.33% | 0% | SI
2020-10-03 | 18 | TER KELAR CC1-TG2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 19 | TER KELAR CC1-TG2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 20 | TER KELAR CC1-TG2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 21 | TER KELAR CC1-TG2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 22 | TER KELAR CC1-TG2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 23 | TER KELAR CC1-TG2 | No Participó | 0% | 0% | 0% | SI
2020-10-03 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-03 | 1 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-03 | 2 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-03 | 4 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-03 | 5 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-03 | 6 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-03 | 8 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-03 | 9 | TER MEJILLONES CTM3-TG | 80% | 100% | 80% | 80% | SI
2020-10-03 | 10 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 12 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 13 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-03 | 14 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-03 | 15 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 16 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-03 | 18 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-03 | 19 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-03 | 20 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-03 | 21 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-03 | 22 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-03 | 23 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-03 | 0 | TER NORGENER U1 | 60% | 100% | 60% | 0% | SI
2020-10-03 | 1 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-03 | 2 | TER NORGENER U1 | 66% | 100% | 66% | 0% | SI
2020-10-03 | 3 | TER NORGENER U1 | 40% | 100% | 40% | 0% | SI
2020-10-03 | 4 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-03 | 5 | TER NORGENER U1 | 40% | 100% | 40% | 0% | SI
2020-10-03 | 6 | TER NORGENER U1 | 20% | 100% | 20% | 0% | SI
2020-10-03 | 7 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-03 | 8 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-03 | 19 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-03 | 20 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 21 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 22 | TER NORGENER U1 | 40% | 100% | 40% | 0% | SI
2020-10-03 | 23 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-03 | 0 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-03 | 1 | TER NORGENER U2 | 25% | 100% | 25% | 0% | SI
2020-10-03 | 2 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-03 | 3 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 4 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-03 | 5 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-03 | 6 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-03 | 7 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-03 | 8 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-03 | 9 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-03 | 10 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-03 | 11 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-03 | 12 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-03 | 13 | TER NORGENER U2 | 80% | 100% | 80% | 80% | SI
2020-10-03 | 14 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-03 | 15 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 16 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 17 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-03 | 18 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-03 | 19 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-03 | 20 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-03 | 21 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-03 | 22 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-03 | 23 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-03 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-03 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-03 | 0 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-03 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 21 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 22 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 0 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 9 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 12 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 21 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE CANUTILLAR U2 | 60% | 100% | 60% | 0% | SI
2020-10-04 | 1 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 6 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 12 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 6 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 12 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 14 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 20 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 21 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 5 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 9 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 15 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 20 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 21 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 1 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 1 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 8 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 9 | HE PANGUE U1 | 25% | 100% | 25% | 0% | SI
2020-10-04 | 10 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 12 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 13 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 14 | HE PANGUE U1 | 75% | 100% | 75% | 75% | SI
2020-10-04 | 15 | HE PANGUE U1 | 75% | 100% | 75% | 75% | SI
2020-10-04 | 16 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 17 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 18 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 19 | HE PANGUE U1 | 50% | 100% | 50% | 0% | SI
2020-10-04 | 20 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 21 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 22 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 23 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 0 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 1 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 2 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 3 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 6 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 7 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 8 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 12 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 13 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 15 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 20 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 21 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 22 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 23 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 0 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 1 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 21 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 22 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 23 | HE PEHUENCHE U2 | 66% | 100% | 66% | 0% | SI
2020-10-04 | 0 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 1 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 2 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 3 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 4 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 5 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 6 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 7 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 8 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 9 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 10 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 11 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 12 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 13 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 14 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 15 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 16 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 17 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 18 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 19 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 20 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 21 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 22 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 23 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 0 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 1 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 2 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 3 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 4 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 5 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 6 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 7 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 8 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 9 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 10 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 11 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 12 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 13 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 14 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 15 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 17 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 18 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 19 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 22 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 23 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 0 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 2 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 3 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 4 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 5 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 6 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-04 | 7 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-04 | 8 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 9 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 10 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 11 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 12 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 13 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 14 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-04 | 15 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 16 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-04 | 17 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 18 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 19 | TER COCHRANE U2 | 33% | 100% | 33% | 0% | SI
2020-10-04 | 20 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 21 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 0 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 1 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-04 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 8 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-04 | 12 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 13 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 17 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 18 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 19 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 20 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 21 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 23 | TER GUACOLDA U3 | 50% | 100% | 50% | 0% | SI
2020-10-04 | 0 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 1 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 2 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-04 | 3 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 4 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 5 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-04 | 7 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 8 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 9 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 12 | TER GUACOLDA U4 | 0% | 100% | 0% | 0% | SI
2020-10-04 | 13 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 14 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER GUACOLDA U4 | 80% | 100% | 80% | 80% | SI
2020-10-04 | 17 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 18 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 19 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 20 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 21 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 8 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 11 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 12 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 13 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 14 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 15 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 16 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 17 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 18 | TER HORNITOS U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 19 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | TER IEM U1 | 60% | 100% | 60% | 0% | SI
2020-10-04 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 1 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 2 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 5 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 8 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 9 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 12 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 13 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 14 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 17 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 18 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 19 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 20 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 21 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 22 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 23 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 0 | TER KELAR CC1-TG2 | No Participó | 0% | 0% | 0% | SI
2020-10-04 | 1 | TER KELAR CC1-TG2 | No Participó | 28.33% | 28.33% | 0% | SI
2020-10-04 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER KELAR CC1-TG2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 5 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 8 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 9 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER KELAR CC1-TG2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 12 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 13 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 14 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 17 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 18 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 19 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 20 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 21 | TER KELAR CC1-TG2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 22 | TER KELAR CC1-TG2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 23 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 1 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 2 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-04 | 5 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-04 | 8 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-04 | 9 | TER MEJILLONES CTM3-TG | 67% | 100% | 67% | 0% | SI
2020-10-04 | 10 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-04 | 11 | TER MEJILLONES CTM3-TG | 67% | 100% | 67% | 0% | SI
2020-10-04 | 12 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 13 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-04 | 14 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-04 | 15 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 16 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-04 | 17 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 18 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-04 | 19 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-04 | 20 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-04 | 21 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-04 | 22 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-04 | 0 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 1 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 2 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-04 | 3 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 4 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-04 | 5 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-04 | 6 | TER NORGENER U1 | 80% | 100% | 80% | 80% | SI
2020-10-04 | 7 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-04 | 8 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-04 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 17 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 18 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 19 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-04 | 20 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-04 | 21 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER NORGENER U1 | 60% | 100% | 60% | 0% | SI
2020-10-04 | 0 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-04 | 1 | TER NORGENER U2 | 34% | 100% | 34% | 0% | SI
2020-10-04 | 2 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 3 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-04 | 4 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-04 | 5 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-04 | 6 | TER NORGENER U2 | 34% | 100% | 34% | 0% | SI
2020-10-04 | 7 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-04 | 8 | TER NORGENER U2 | 25% | 100% | 25% | 0% | SI
2020-10-04 | 9 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 10 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 11 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-04 | 12 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 13 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 14 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-04 | 15 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 16 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-04 | 17 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 18 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-04 | 19 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-04 | 20 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-04 | 21 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-04 | 22 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-04 | 23 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-04 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-04 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-04 | 0 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-04 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 2 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 6 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 10 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE PANGUE U1 | 75% | 100% | 75% | 75% | SI
2020-10-05 | 1 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 2 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 3 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 4 | HE PANGUE U1 | 60% | 100% | 60% | 0% | SI
2020-10-05 | 5 | HE PANGUE U1 | 60% | 100% | 60% | 0% | SI
2020-10-05 | 6 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 7 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 8 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 10 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 11 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 12 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 13 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 14 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 15 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 16 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 19 | HE PANGUE U1 | 75% | 100% | 75% | 75% | SI
2020-10-05 | 20 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 0 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 2 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 3 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 5 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 7 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 10 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 11 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 12 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 13 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 16 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 21 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 2 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 3 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 5 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 6 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 7 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 8 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 23 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 1 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 2 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 3 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 4 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 8 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 9 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 10 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 11 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 12 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 13 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 14 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 15 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 16 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 17 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 18 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 19 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 20 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 21 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 22 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 23 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 0 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 4 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 5 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 6 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 7 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 13 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 14 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 15 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 17 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 18 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 19 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 20 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 21 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 22 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 23 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-05 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 0 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-05 | 1 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 2 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-05 | 3 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 4 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 5 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 6 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 7 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 8 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 9 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-05 | 10 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-05 | 11 | TER COCHRANE U2 | 33% | 100% | 33% | 0% | SI
2020-10-05 | 12 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 13 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-05 | 14 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-05 | 15 | TER COCHRANE U2 | 33% | 100% | 33% | 0% | SI
2020-10-05 | 16 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 17 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 18 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-05 | 19 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 20 | TER COCHRANE U2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER COCHRANE U2 | 40% | 100% | 40% | 0% | SI
2020-10-05 | 23 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-05 | 0 | TER GUACOLDA U3 | 80% | 100% | 80% | 80% | SI
2020-10-05 | 1 | TER GUACOLDA U3 | 50% | 100% | 50% | 0% | SI
2020-10-05 | 2 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 3 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 7 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 10 | TER GUACOLDA U3 | 75% | 100% | 75% | 75% | SI
2020-10-05 | 11 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER GUACOLDA U3 | 66% | 100% | 66% | 0% | SI
2020-10-05 | 15 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER GUACOLDA U3 | 75% | 100% | 75% | 75% | SI
2020-10-05 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-05 | 23 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 1 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 2 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 3 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 4 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 5 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 6 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 7 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 8 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 9 | TER GUACOLDA U4 | 25% | 100% | 25% | 0% | SI
2020-10-05 | 10 | TER GUACOLDA U4 | 66% | 100% | 66% | 0% | SI
2020-10-05 | 11 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 12 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 13 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 14 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER GUACOLDA U4 | 75% | 100% | 75% | 75% | SI
2020-10-05 | 17 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 9 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 10 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 11 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 16 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 17 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 18 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 1 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 2 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 3 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 4 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 7 | TER KELAR CC1-TG1 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 8 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 9 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 10 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 11 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 12 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 13 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER KELAR CC1-TG1 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 17 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 1 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 2 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 3 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 4 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER KELAR CC1-TG2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 7 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 8 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 9 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 10 | TER KELAR CC1-TG2 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 11 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 12 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 13 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 17 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-05 | 1 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-05 | 2 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-05 | 3 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-05 | 4 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-05 | 7 | TER MEJILLONES CTM3-TG | 80% | 100% | 80% | 80% | SI
2020-10-05 | 8 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-05 | 9 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-05 | 10 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 11 | TER MEJILLONES CTM3-TG | 80% | 100% | 80% | 80% | SI
2020-10-05 | 12 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 13 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 15 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 16 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-05 | 17 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER MEJILLONES CTM3-TG | 33% | 100% | 33% | 0% | SI
2020-10-05 | 19 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 1 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-05 | 2 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-05 | 3 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-05 | 4 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 5 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-05 | 6 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-05 | 7 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-05 | 8 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-05 | 9 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-05 | 10 | TER NORGENER U1 | 25% | 100% | 25% | 0% | SI
2020-10-05 | 11 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-05 | 12 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-05 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-05 | 21 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-05 | 22 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-05 | 23 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-05 | 0 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-05 | 1 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-05 | 2 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-05 | 3 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-05 | 4 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-05 | 5 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 6 | TER NORGENER U2 | 25% | 100% | 25% | 0% | SI
2020-10-05 | 7 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 8 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-05 | 9 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-05 | 10 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-05 | 11 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-05 | 12 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-05 | 13 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 14 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-05 | 15 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 16 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-05 | 17 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-05 | 18 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-05 | 19 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-05 | 20 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-05 | 21 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-05 | 22 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-05 | 23 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-05 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-05 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-05 | 0 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-05 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE ANGOSTURA U2 | 50% | 100% | 50% | 0% | SI
2020-10-06 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE CANUTILLAR U1 | 67% | 100% | 67% | 0% | SI
2020-10-06 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 8 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 10 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 20 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 21 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 8 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 10 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 20 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 21 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE PANGUE U1 | 80% | 100% | 80% | 80% | SI
2020-10-06 | 1 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 4 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 6 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 9 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 10 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 11 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 12 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 13 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 22 | HE PANGUE U1 | 66% | 100% | 66% | 0% | SI
2020-10-06 | 23 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 0 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 5 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 15 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 20 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 20 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE PEHUENCHE U2 | 75% | 100% | 75% | 75% | SI
2020-10-06 | 23 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 1 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 2 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 3 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 4 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 5 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 6 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 7 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 8 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 9 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 10 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 11 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 12 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 13 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 14 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 15 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 16 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 17 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 18 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 19 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 20 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 21 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 22 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 23 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 0 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 1 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 2 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 3 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 4 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 5 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 6 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 7 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 8 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 9 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 10 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 11 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 12 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 13 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 14 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 15 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 17 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 18 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 19 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 20 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 21 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 22 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 23 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-06 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 10 | TER COCHRANE U1 | No Verificable | 25% | 0% | 0% | NO
2020-10-06 | 11 | TER COCHRANE U1 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 12 | TER COCHRANE U1 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 13 | TER COCHRANE U1 | No Verificable | 78.33% | 0% | 0% | NO
2020-10-06 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 0 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-06 | 5 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 6 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 7 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-06 | 8 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 9 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-06 | 10 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-06 | 11 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-06 | 12 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-06 | 13 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-06 | 14 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 15 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-06 | 16 | TER COCHRANE U2 | 33% | 100% | 33% | 0% | SI
2020-10-06 | 17 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-06 | 18 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-06 | 19 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-06 | 0 | TER GUACOLDA U3 | 60% | 100% | 60% | 0% | SI
2020-10-06 | 1 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 22 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 1 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 2 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 6 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 7 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 8 | TER GUACOLDA U4 | 66% | 100% | 66% | 0% | SI
2020-10-06 | 9 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-06 | 10 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 11 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER GUACOLDA U4 | 49% | 100% | 49% | 0% | SI
2020-10-06 | 15 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 16 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 17 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 18 | TER GUACOLDA U4 | 66% | 100% | 66% | 0% | SI
2020-10-06 | 19 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 20 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 23 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 18 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 3 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 18 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER MEJILLONES CTM2 | 80% | 100% | 80% | 80% | SI
2020-10-06 | 21 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER MEJILLONES CTM3-TG | 20% | 100% | 20% | 0% | SI
2020-10-06 | 13 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-06 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER MEJILLONES CTM3-TG | 66% | 100% | 66% | 0% | SI
2020-10-06 | 18 | TER MEJILLONES CTM3-TG | 67% | 100% | 67% | 0% | SI
2020-10-06 | 19 | TER MEJILLONES CTM3-TG | 67% | 100% | 67% | 0% | SI
2020-10-06 | 20 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER NORGENER U1 | 20% | 100% | 20% | 0% | SI
2020-10-06 | 2 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-06 | 3 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-06 | 4 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-06 | 5 | TER NORGENER U1 | 66% | 100% | 66% | 0% | SI
2020-10-06 | 6 | TER NORGENER U1 | 20% | 100% | 20% | 0% | SI
2020-10-06 | 7 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-06 | 8 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 9 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 10 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-06 | 21 | TER NORGENER U1 | 40% | 100% | 40% | 0% | SI
2020-10-06 | 22 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-06 | 23 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-06 | 0 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-06 | 1 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-06 | 2 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-06 | 3 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-06 | 4 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-06 | 5 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-06 | 6 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-06 | 7 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-06 | 8 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-06 | 9 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-06 | 10 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-06 | 11 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-06 | 12 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-06 | 13 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 14 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-06 | 15 | TER NORGENER U2 | 49% | 100% | 49% | 0% | SI
2020-10-06 | 16 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-06 | 17 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 18 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-06 | 19 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-06 | 20 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-06 | 21 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-06 | 22 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-06 | 23 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-06 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-06 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-06 | 0 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-06 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 16 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-07 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 20 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 10 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 11 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 12 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 13 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 14 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 15 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 16 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 9 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 20 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 5 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 9 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-07 | 12 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 13 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 14 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 15 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 16 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE PANGUE U1 | 49% | 100% | 49% | 0% | SI
2020-10-07 | 20 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-07 | 22 | HE PANGUE U1 | 60% | 100% | 60% | 0% | SI
2020-10-07 | 23 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 0 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 1 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE PEHUENCHE U1 | 80% | 100% | 80% | 80% | SI
2020-10-07 | 7 | HE PEHUENCHE U1 | 80% | 100% | 80% | 80% | SI
2020-10-07 | 8 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE PEHUENCHE U1 | 67% | 100% | 67% | 0% | SI
2020-10-07 | 12 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 13 | HE PEHUENCHE U1 | 80% | 100% | 80% | 80% | SI
2020-10-07 | 14 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 16 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-07 | 17 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 21 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE PEHUENCHE U2 | 66% | 100% | 66% | 0% | SI
2020-10-07 | 12 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 13 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 14 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-07 | 15 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 16 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 17 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 19 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 21 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 22 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 1 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 2 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 3 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 4 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 5 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 6 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 7 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 8 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 9 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 10 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 11 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 12 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 13 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 14 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 15 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 16 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 17 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 18 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 19 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 20 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 21 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 22 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 23 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 0 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 1 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 2 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 3 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 4 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 5 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 6 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 7 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 8 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 9 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 10 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 11 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 12 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 13 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 14 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 15 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 17 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 18 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 19 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 20 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 22 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 23 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 0 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-07 | 1 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-07 | 2 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 3 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 4 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 5 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 6 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 7 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 8 | TER COCHRANE U2 | No Verificable | 21.67% | 0% | 0% | SI
2020-10-07 | 9 | TER COCHRANE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 10 | TER COCHRANE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 11 | TER COCHRANE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 12 | TER COCHRANE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 13 | TER COCHRANE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 14 | TER COCHRANE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 15 | TER COCHRANE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 16 | TER COCHRANE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 17 | TER COCHRANE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 18 | TER COCHRANE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 19 | TER COCHRANE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 20 | TER COCHRANE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 21 | TER COCHRANE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 22 | TER COCHRANE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 23 | TER COCHRANE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-07 | 0 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 1 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 5 | TER GUACOLDA U3 | 34% | 100% | 34% | 0% | SI
2020-10-07 | 6 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 7 | TER GUACOLDA U3 | 0% | 100% | 0% | 0% | SI
2020-10-07 | 8 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 21 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 22 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-07 | 1 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER GUACOLDA U4 | 75% | 100% | 75% | 75% | SI
2020-10-07 | 5 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 6 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 7 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 8 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER GUACOLDA U4 | 80% | 100% | 80% | 80% | SI
2020-10-07 | 10 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-07 | 16 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-07 | 17 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-07 | 18 | TER GUACOLDA U4 | 49% | 100% | 49% | 0% | SI
2020-10-07 | 19 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-07 | 20 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-07 | 21 | TER GUACOLDA U4 | 49% | 100% | 49% | 0% | SI
2020-10-07 | 22 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-07 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 1 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 5 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 6 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 7 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 8 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 14 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 17 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER KELAR CC1-TG1 | 83% | 100% | 83% | 83% | SI
2020-10-07 | 19 | TER KELAR CC1-TG1 | 75% | 100% | 75% | 75% | SI
2020-10-07 | 20 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 21 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 22 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 20 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 21 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 22 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER MEJILLONES CTM2 | 20% | 100% | 20% | 0% | SI
2020-10-07 | 1 | TER MEJILLONES CTM2 | 67% | 100% | 67% | 0% | SI
2020-10-07 | 2 | TER MEJILLONES CTM2 | 50% | 100% | 50% | 0% | SI
2020-10-07 | 3 | TER MEJILLONES CTM2 | 67% | 100% | 67% | 0% | SI
2020-10-07 | 4 | TER MEJILLONES CTM2 | 80% | 100% | 80% | 80% | SI
2020-10-07 | 5 | TER MEJILLONES CTM2 | 25% | 100% | 25% | 0% | SI
2020-10-07 | 6 | TER MEJILLONES CTM2 | 34% | 100% | 34% | 0% | SI
2020-10-07 | 7 | TER MEJILLONES CTM2 | 50% | 100% | 50% | 0% | SI
2020-10-07 | 8 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | TER MEJILLONES CTM2 | 0% | 100% | 0% | 0% | SI
2020-10-07 | 20 | TER MEJILLONES CTM2 | 67% | 100% | 67% | 0% | SI
2020-10-07 | 21 | TER MEJILLONES CTM2 | 33% | 100% | 33% | 0% | SI
2020-10-07 | 22 | TER MEJILLONES CTM2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 23 | TER MEJILLONES CTM2 | 50% | 73.33% | 36.67% | 0% | SI
2020-10-07 | 0 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-07 | 1 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-07 | 5 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-07 | 6 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-07 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | TER MEJILLONES CTM3-TG | 67% | 100% | 67% | 0% | SI
2020-10-07 | 22 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER NORGENER U1 | 60% | 100% | 60% | 0% | SI
2020-10-07 | 1 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-07 | 2 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-07 | 3 | TER NORGENER U1 | 20% | 100% | 20% | 0% | SI
2020-10-07 | 4 | TER NORGENER U1 | 80% | 100% | 80% | 80% | SI
2020-10-07 | 5 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-07 | 6 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-07 | 7 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-07 | 8 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-07 | 9 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-07 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 19 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 20 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-07 | 21 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-07 | 1 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-07 | 2 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-07 | 3 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-07 | 4 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-07 | 5 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-07 | 6 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 7 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-07 | 8 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-07 | 9 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-07 | 10 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-07 | 11 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-07 | 12 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-07 | 13 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 14 | TER NORGENER U2 | 25% | 100% | 25% | 0% | SI
2020-10-07 | 15 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-07 | 16 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 17 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-07 | 19 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-07 | 20 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-07 | 21 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-07 | 22 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-07 | 23 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-07 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 20 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 21 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 22 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 21 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-07 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-07 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-07 | 0 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-07 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 20 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | HE ANGOSTURA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 13 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 15 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 9 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 12 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 15 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 8 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 15 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 18 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 20 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 21 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 10 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 20 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 21 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 2 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 4 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 9 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 10 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 11 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 12 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 13 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 14 | HE PANGUE U1 | 75% | 100% | 75% | 75% | SI
2020-10-08 | 15 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 16 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 17 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE PANGUE U1 | 75% | 100% | 75% | 75% | SI
2020-10-08 | 19 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE PANGUE U1 | 75% | 100% | 75% | 75% | SI
2020-10-08 | 22 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 23 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 0 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 3 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 4 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 6 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 7 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 8 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 12 | HE PEHUENCHE U1 | 67% | 100% | 67% | 0% | SI
2020-10-08 | 13 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 15 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 16 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 17 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE PEHUENCHE U1 | 67% | 100% | 67% | 0% | SI
2020-10-08 | 22 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 0 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 3 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 4 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 12 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 13 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 14 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 15 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 16 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 17 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 20 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 1 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 2 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 3 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 4 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 5 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 6 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 7 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 8 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 9 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 10 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 11 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 12 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 13 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 18 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 19 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 20 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 21 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 22 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 23 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 0 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 1 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 2 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 3 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 4 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 5 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 6 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 7 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 8 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 9 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 10 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 11 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 12 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 13 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 14 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 15 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 17 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 18 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 19 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 20 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 21 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 22 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 23 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 56.67% | 0% | 0% | NO
2020-10-08 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 75% | 0% | 0% | NO
2020-10-08 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 95% | 0% | 0% | NO
2020-10-08 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 0 | TER COCHRANE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 1 | TER COCHRANE U2 | 60% | 0% | 0% | 0% | SI
2020-10-08 | 2 | TER COCHRANE U2 | 67% | 0% | 0% | 0% | SI
2020-10-08 | 3 | TER COCHRANE U2 | No Verificable | 0% | 0% | 0% | SI
2020-10-08 | 4 | TER COCHRANE U2 | No Verificable | 0% | 0% | 0% | SI
2020-10-08 | 5 | TER COCHRANE U2 | 50% | 0% | 0% | 0% | SI
2020-10-08 | 6 | TER COCHRANE U2 | 83% | 71.67% | 59.48% | 0% | SI
2020-10-08 | 7 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 8 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 9 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-08 | 10 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 11 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-08 | 12 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 13 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 14 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 15 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 16 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 17 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 18 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-08 | 19 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 20 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 21 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 22 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 23 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 0 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 15 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 16 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 18 | TER GUACOLDA U3 | 60% | 100% | 60% | 0% | SI
2020-10-08 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 21 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 22 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 23 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 0 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-08 | 2 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 3 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 4 | TER GUACOLDA U4 | 75% | 100% | 75% | 75% | SI
2020-10-08 | 5 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 6 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 7 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 8 | TER GUACOLDA U4 | 66% | 100% | 66% | 0% | SI
2020-10-08 | 9 | TER GUACOLDA U4 | 0% | 100% | 0% | 0% | SI
2020-10-08 | 10 | TER GUACOLDA U4 | 80% | 100% | 80% | 80% | SI
2020-10-08 | 11 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 12 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-08 | 13 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 14 | TER GUACOLDA U4 | 75% | 100% | 75% | 75% | SI
2020-10-08 | 15 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 16 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 17 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 18 | TER GUACOLDA U4 | 25% | 100% | 25% | 0% | SI
2020-10-08 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 20 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-08 | 21 | TER GUACOLDA U4 | 80% | 100% | 80% | 80% | SI
2020-10-08 | 22 | TER GUACOLDA U4 | 60% | 100% | 60% | 0% | SI
2020-10-08 | 23 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 8 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 14 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 15 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 16 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 17 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER KELAR CC1-TG1 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER MEJILLONES CTM1 | No Participó | 18.33% | 18.33% | 0% | SI
2020-10-08 | 3 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 4 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 5 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 6 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 7 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 8 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 9 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 10 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 11 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 12 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 13 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 14 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 15 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 16 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 17 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 18 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 19 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 20 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 21 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 22 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 23 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 0 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER MEJILLONES CTM2 | 25% | 100% | 25% | 0% | SI
2020-10-08 | 3 | TER MEJILLONES CTM2 | 40% | 100% | 40% | 0% | SI
2020-10-08 | 4 | TER MEJILLONES CTM2 | 34% | 100% | 34% | 0% | SI
2020-10-08 | 5 | TER MEJILLONES CTM2 | 33% | 100% | 33% | 0% | SI
2020-10-08 | 6 | TER MEJILLONES CTM2 | 25% | 100% | 25% | 0% | SI
2020-10-08 | 7 | TER MEJILLONES CTM2 | 0% | 100% | 0% | 0% | SI
2020-10-08 | 8 | TER MEJILLONES CTM2 | 34% | 100% | 34% | 0% | SI
2020-10-08 | 9 | TER MEJILLONES CTM2 | 0% | 100% | 0% | 0% | SI
2020-10-08 | 10 | TER MEJILLONES CTM2 | 50% | 100% | 50% | 0% | SI
2020-10-08 | 11 | TER MEJILLONES CTM2 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 12 | TER MEJILLONES CTM2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 13 | TER MEJILLONES CTM2 | 67% | 100% | 67% | 0% | SI
2020-10-08 | 14 | TER MEJILLONES CTM2 | 40% | 100% | 40% | 0% | SI
2020-10-08 | 15 | TER MEJILLONES CTM2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 16 | TER MEJILLONES CTM2 | 75% | 100% | 75% | 75% | SI
2020-10-08 | 17 | TER MEJILLONES CTM2 | 50% | 100% | 50% | 0% | SI
2020-10-08 | 18 | TER MEJILLONES CTM2 | 34% | 100% | 34% | 0% | SI
2020-10-08 | 19 | TER MEJILLONES CTM2 | 50% | 100% | 50% | 0% | SI
2020-10-08 | 20 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 1 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-08 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-08 | 6 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-08 | 7 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-08 | 8 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-08 | 9 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 10 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-08 | 11 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 12 | TER MEJILLONES CTM3-TG | 66% | 100% | 66% | 0% | SI
2020-10-08 | 13 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-08 | 14 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-08 | 15 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 16 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-08 | 17 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-08 | 18 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-08 | 19 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-08 | 20 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-08 | 21 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-08 | 22 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-08 | 23 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-08 | 0 | TER NORGENER U1 | 66% | 100% | 66% | 0% | SI
2020-10-08 | 1 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-08 | 2 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-08 | 3 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-08 | 4 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 5 | TER NORGENER U1 | 75% | 100% | 75% | 75% | SI
2020-10-08 | 6 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 7 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-08 | 8 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 10 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 13 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 14 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 15 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 16 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 19 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-08 | 20 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-08 | 21 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-08 | 22 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 23 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 0 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-08 | 1 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-08 | 2 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-08 | 3 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 4 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-08 | 5 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-08 | 6 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-08 | 7 | TER NORGENER U2 | 25% | 100% | 25% | 0% | SI
2020-10-08 | 8 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-08 | 9 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-08 | 10 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-08 | 11 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-08 | 12 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 13 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 14 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-08 | 15 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 16 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-08 | 17 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-08 | 18 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 19 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-08 | 20 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-08 | 21 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-08 | 22 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-08 | 23 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-08 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 10 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 11 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 12 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 13 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 14 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 15 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 16 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 17 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 18 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 19 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 20 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 21 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 22 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 23 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-08 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-08 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-08 | 0 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-08 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 45% | 45% | 0% | SI
2020-10-08 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-08 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 28.33% | 28.33% | 0% | SI
2020-10-09 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 0 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 1 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 2 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 3 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 4 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 1 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 2 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 3 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 19 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 10 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 19 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 3 | HE PANGUE U1 | 67% | 100% | 67% | 0% | SI
2020-10-09 | 4 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 5 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 9 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 10 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 11 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 12 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 14 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 18 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 21 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 22 | HE PANGUE U1 | 60% | 100% | 60% | 0% | SI
2020-10-09 | 23 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 0 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 2 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 3 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 4 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 6 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 10 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 13 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 14 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 19 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 20 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 21 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 22 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 0 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 8 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 10 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 13 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 14 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 15 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 17 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 18 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 1 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 2 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 3 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 4 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 5 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 6 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 7 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 8 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 9 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 10 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 11 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 12 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 13 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 14 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 15 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 16 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 17 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 18 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 19 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 20 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 21 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 22 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 23 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 0 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 1 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 2 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 3 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 4 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 5 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 6 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 7 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 8 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 9 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 10 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 11 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 12 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 13 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 14 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 15 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 17 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 18 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 19 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 20 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 21 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 22 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 23 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 0 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 1 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 2 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 3 | TER COCHRANE U2 | 20% | 100% | 20% | 0% | SI
2020-10-09 | 4 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 5 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 8 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 9 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 10 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 11 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 12 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 13 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 14 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 15 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 16 | TER COCHRANE U2 | 0% | 100% | 0% | 0% | SI
2020-10-09 | 17 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 18 | TER COCHRANE U2 | 75% | 100% | 75% | 75% | SI
2020-10-09 | 19 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | TER COCHRANE U2 | 34% | 100% | 34% | 0% | SI
2020-10-09 | 21 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 1 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 2 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 15 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 16 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 18 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-09 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 20 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 21 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 22 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 1 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 2 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 3 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 4 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 5 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 6 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 7 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 8 | TER GUACOLDA U4 | 75% | 100% | 75% | 75% | SI
2020-10-09 | 9 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 10 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 11 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 12 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-09 | 13 | TER GUACOLDA U4 | 33% | 100% | 33% | 0% | SI
2020-10-09 | 14 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 15 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 16 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 17 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 18 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 19 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 20 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 21 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 22 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 23 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 20 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 21 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 22 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 20 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 21 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 22 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 1 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 2 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 3 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 4 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 5 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 6 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 7 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 8 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 9 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 10 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 11 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 12 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 13 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 14 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 15 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 16 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 17 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 18 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 19 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 20 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 21 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 22 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 23 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 0 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | TER MEJILLONES CTM2 | 40% | 100% | 40% | 0% | SI
2020-10-09 | 6 | TER MEJILLONES CTM2 | 0% | 100% | 0% | 0% | SI
2020-10-09 | 7 | TER MEJILLONES CTM2 | 0% | 100% | 0% | 0% | SI
2020-10-09 | 8 | TER MEJILLONES CTM2 | 33% | 100% | 33% | 0% | SI
2020-10-09 | 9 | TER MEJILLONES CTM2 | 40% | 100% | 40% | 0% | SI
2020-10-09 | 10 | TER MEJILLONES CTM2 | 0% | 100% | 0% | 0% | SI
2020-10-09 | 11 | TER MEJILLONES CTM2 | 0% | 100% | 0% | 0% | SI
2020-10-09 | 12 | TER MEJILLONES CTM2 | 0% | 100% | 0% | 0% | SI
2020-10-09 | 13 | TER MEJILLONES CTM2 | 0% | 100% | 0% | 0% | SI
2020-10-09 | 14 | TER MEJILLONES CTM2 | 0% | 100% | 0% | 0% | SI
2020-10-09 | 15 | TER MEJILLONES CTM2 | 80% | 100% | 80% | 80% | SI
2020-10-09 | 16 | TER MEJILLONES CTM2 | 50% | 100% | 50% | 0% | SI
2020-10-09 | 17 | TER MEJILLONES CTM2 | 60% | 100% | 60% | 0% | SI
2020-10-09 | 18 | TER MEJILLONES CTM2 | 34% | 100% | 34% | 0% | SI
2020-10-09 | 19 | TER MEJILLONES CTM2 | 50% | 100% | 50% | 0% | SI
2020-10-09 | 20 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 1 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 2 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 3 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 4 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 5 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 6 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 7 | TER MEJILLONES CTM3-TG | 80% | 100% | 80% | 80% | SI
2020-10-09 | 8 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 9 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 10 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 11 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 12 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 13 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 14 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 15 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 16 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 17 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 18 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 19 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 20 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 21 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 22 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER NORGENER U1 | 34% | 100% | 34% | 0% | SI
2020-10-09 | 1 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-09 | 2 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-09 | 3 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-09 | 4 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-09 | 5 | TER NORGENER U1 | 34% | 100% | 34% | 0% | SI
2020-10-09 | 6 | TER NORGENER U1 | 20% | 100% | 20% | 0% | SI
2020-10-09 | 7 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-09 | 8 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-09 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-09 | 18 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 19 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-09 | 20 | TER NORGENER U1 | 0% | 100% | 0% | 0% | SI
2020-10-09 | 21 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-09 | 22 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-09 | 23 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER NORGENER U2 | 34% | 100% | 34% | 0% | SI
2020-10-09 | 1 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-09 | 2 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-09 | 3 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-09 | 4 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-09 | 5 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-09 | 6 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-09 | 7 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-09 | 8 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-09 | 9 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 10 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-09 | 11 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-09 | 12 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-09 | 13 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-09 | 14 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-09 | 15 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-09 | 16 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-09 | 17 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-09 | 18 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-09 | 19 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-09 | 20 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-09 | 21 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 10 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 11 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | TER TALTAL U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 2 | TER TALTAL U1 | 20% | 100% | 20% | 0% | SI
2020-10-09 | 3 | TER TALTAL U1 | 75% | 100% | 75% | 75% | SI
2020-10-09 | 4 | TER TALTAL U1 | 40% | 100% | 40% | 0% | SI
2020-10-09 | 5 | TER TALTAL U1 | 33% | 100% | 33% | 0% | SI
2020-10-09 | 6 | TER TALTAL U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-09 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-09 | 0 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 19 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 20 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 21 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 22 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 0 | TER TOCOPILLA U15 | 60% | 100% | 60% | 0% | SI
2020-10-09 | 1 | TER TOCOPILLA U15 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 2 | TER TOCOPILLA U15 | 50% | 100% | 50% | 0% | SI
2020-10-09 | 3 | TER TOCOPILLA U15 | 83% | 100% | 83% | 83% | SI
2020-10-09 | 4 | TER TOCOPILLA U15 | 66% | 100% | 66% | 0% | SI
2020-10-09 | 5 | TER TOCOPILLA U15 | 50% | 100% | 50% | 0% | SI
2020-10-09 | 6 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 7 | TER TOCOPILLA U15 | 67% | 100% | 67% | 0% | SI
2020-10-09 | 8 | TER TOCOPILLA U15 | 75% | 100% | 75% | 75% | SI
2020-10-09 | 9 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 10 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-09 | 11 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-09 | 12 | TER TOCOPILLA U15 | 25% | 100% | 25% | 0% | SI
2020-10-09 | 13 | TER TOCOPILLA U15 | 17% | 100% | 17% | 0% | SI
2020-10-09 | 14 | TER TOCOPILLA U15 | 17% | 100% | 17% | 0% | SI
2020-10-09 | 15 | TER TOCOPILLA U15 | 66% | 100% | 66% | 0% | SI
2020-10-09 | 16 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-09 | 17 | TER TOCOPILLA U15 | 20% | 100% | 20% | 0% | SI
2020-10-09 | 18 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-09 | 19 | TER TOCOPILLA U15 | 33% | 100% | 33% | 0% | SI
2020-10-09 | 20 | TER TOCOPILLA U15 | 33% | 100% | 33% | 0% | SI
2020-10-09 | 21 | TER TOCOPILLA U15 | 50% | 100% | 50% | 0% | SI
2020-10-09 | 22 | TER TOCOPILLA U15 | 67% | 100% | 67% | 0% | SI
2020-10-09 | 23 | TER TOCOPILLA U15 | 25% | 100% | 25% | 0% | SI
2020-10-09 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 66.67% | 66.67% | 0% | SI
2020-10-09 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-09 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 95% | 95% | 95% | SI
2020-10-09 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-09 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE PANGUE U1 | 80% | 100% | 80% | 80% | SI
2020-10-10 | 1 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE PANGUE U1 | 67% | 100% | 67% | 0% | SI
2020-10-10 | 3 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 6 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 7 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 8 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 9 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 13 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 14 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 15 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 16 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 19 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 20 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE PANGUE U1 | 67% | 100% | 67% | 0% | SI
2020-10-10 | 22 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 23 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 0 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 3 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 4 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 11 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 12 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 13 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 14 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 15 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 16 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 17 | HE PEHUENCHE U1 | 40% | 100% | 40% | 0% | SI
2020-10-10 | 18 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 19 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 23 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 12 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 15 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE PEHUENCHE U2 | 80% | 100% | 80% | 80% | SI
2020-10-10 | 18 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 1 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 2 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 3 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 4 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 5 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 6 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 7 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 8 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 9 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 10 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 11 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 12 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 13 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 14 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 15 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 16 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 17 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 18 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 19 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 20 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 21 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 22 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 23 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 0 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 1 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 2 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 3 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 4 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 5 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 6 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 7 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 8 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 9 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 10 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 11 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 12 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 13 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 14 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 15 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 17 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 18 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 19 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 20 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 21 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 22 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 23 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 0 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | TER COCHRANE U2 | 40% | 100% | 40% | 0% | SI
2020-10-10 | 9 | TER COCHRANE U2 | 33% | 100% | 33% | 0% | SI
2020-10-10 | 10 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-10 | 11 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 12 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-10 | 13 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 14 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 15 | TER COCHRANE U2 | 75% | 100% | 75% | 75% | SI
2020-10-10 | 16 | TER COCHRANE U2 | 60% | 100% | 60% | 0% | SI
2020-10-10 | 17 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 18 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 19 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 11 | TER GUACOLDA U3 | 75% | 100% | 75% | 75% | SI
2020-10-10 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 15 | TER GUACOLDA U3 | 75% | 100% | 75% | 75% | SI
2020-10-10 | 16 | TER GUACOLDA U3 | 17% | 100% | 17% | 0% | SI
2020-10-10 | 17 | TER GUACOLDA U3 | 50% | 100% | 50% | 0% | SI
2020-10-10 | 18 | TER GUACOLDA U3 | 0% | 100% | 0% | 0% | SI
2020-10-10 | 19 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 20 | TER GUACOLDA U3 | 0% | 100% | 0% | 0% | SI
2020-10-10 | 21 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 22 | TER GUACOLDA U3 | 50% | 100% | 50% | 0% | SI
2020-10-10 | 23 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 0 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 2 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 3 | TER GUACOLDA U4 | 80% | 100% | 80% | 80% | SI
2020-10-10 | 4 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 5 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 6 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 7 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 8 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 9 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 10 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 11 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-10 | 12 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-10 | 13 | TER GUACOLDA U4 | 0% | 100% | 0% | 0% | SI
2020-10-10 | 14 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-10 | 15 | TER GUACOLDA U4 | 49% | 100% | 49% | 0% | SI
2020-10-10 | 16 | TER GUACOLDA U4 | 80% | 100% | 80% | 80% | SI
2020-10-10 | 17 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 18 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 20 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 21 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 22 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 23 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 9 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 10 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 11 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER KELAR CC1-TG1 | 67% | 100% | 67% | 0% | SI
2020-10-10 | 8 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 9 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 10 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 11 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 12 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 13 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 14 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 15 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 16 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 17 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 18 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 23 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 0 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 1 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 2 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 3 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 4 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 5 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 6 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 7 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 8 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 9 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 10 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 11 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 12 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 13 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 14 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 15 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 16 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 17 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 18 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 19 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 20 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 21 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 22 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 23 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 0 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER MEJILLONES CTM2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | TER MEJILLONES CTM2 | 25% | 100% | 25% | 0% | SI
2020-10-10 | 9 | TER MEJILLONES CTM2 | 0% | 100% | 0% | 0% | SI
2020-10-10 | 10 | TER MEJILLONES CTM2 | 25% | 100% | 25% | 0% | SI
2020-10-10 | 11 | TER MEJILLONES CTM2 | 0% | 100% | 0% | 0% | SI
2020-10-10 | 12 | TER MEJILLONES CTM2 | 75% | 100% | 75% | 75% | SI
2020-10-10 | 13 | TER MEJILLONES CTM2 | 0% | 100% | 0% | 0% | SI
2020-10-10 | 14 | TER MEJILLONES CTM2 | 17% | 100% | 17% | 0% | SI
2020-10-10 | 15 | TER MEJILLONES CTM2 | 20% | 100% | 20% | 0% | SI
2020-10-10 | 16 | TER MEJILLONES CTM2 | 25% | 100% | 25% | 0% | SI
2020-10-10 | 17 | TER MEJILLONES CTM2 | 0% | 95% | 0% | 0% | SI
2020-10-10 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-10 | 0 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | TER MEJILLONES CTM3-TG | 0% | 100% | 0% | 0% | SI
2020-10-10 | 20 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 21 | TER MEJILLONES CTM3-TG | 80% | 100% | 80% | 80% | SI
2020-10-10 | 22 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 23 | TER MEJILLONES CTM3-TG | 0% | 100% | 0% | 0% | SI
2020-10-10 | 0 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER NORGENER U1 | 80% | 100% | 80% | 80% | SI
2020-10-10 | 8 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 11 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 14 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 16 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 19 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-10 | 8 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 9 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-10 | 10 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-10 | 11 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-10 | 12 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-10 | 13 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-10 | 14 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 15 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 16 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 17 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 18 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 19 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | TER NORGENER U2 | 80% | 100% | 80% | 80% | SI
2020-10-10 | 22 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-10 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-10 | 0 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 1 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 2 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 3 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 4 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 5 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 6 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 7 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 8 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | TER TOCOPILLA U14 | 80% | 100% | 80% | 80% | SI
2020-10-10 | 20 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 21 | TER TOCOPILLA U14 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 22 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 23 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-10 | 0 | TER TOCOPILLA U15 | 75% | 100% | 75% | 75% | SI
2020-10-10 | 1 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-10 | 2 | TER TOCOPILLA U15 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 3 | TER TOCOPILLA U15 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 4 | TER TOCOPILLA U15 | 80% | 100% | 80% | 80% | SI
2020-10-10 | 5 | TER TOCOPILLA U15 | 75% | 100% | 75% | 75% | SI
2020-10-10 | 6 | TER TOCOPILLA U15 | 80% | 100% | 80% | 80% | SI
2020-10-10 | 7 | TER TOCOPILLA U15 | 60% | 100% | 60% | 0% | SI
2020-10-10 | 8 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-10 | 9 | TER TOCOPILLA U15 | 60% | 100% | 60% | 0% | SI
2020-10-10 | 10 | TER TOCOPILLA U15 | 33% | 100% | 33% | 0% | SI
2020-10-10 | 11 | TER TOCOPILLA U15 | 66% | 100% | 66% | 0% | SI
2020-10-10 | 12 | TER TOCOPILLA U15 | 34% | 100% | 34% | 0% | SI
2020-10-10 | 13 | TER TOCOPILLA U15 | 66% | 100% | 66% | 0% | SI
2020-10-10 | 14 | TER TOCOPILLA U15 | 33% | 100% | 33% | 0% | SI
2020-10-10 | 15 | TER TOCOPILLA U15 | 60% | 100% | 60% | 0% | SI
2020-10-10 | 16 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-10 | 17 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 18 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-10 | 19 | TER TOCOPILLA U15 | 67% | 100% | 67% | 0% | SI
2020-10-10 | 20 | TER TOCOPILLA U15 | 40% | 100% | 40% | 0% | SI
2020-10-10 | 21 | TER TOCOPILLA U15 | 83% | 100% | 83% | 83% | SI
2020-10-10 | 22 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 23 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-10 | 0 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 1 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 2 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 3 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 4 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 5 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 6 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 7 | TER TOCOPILLA U16-TG-TV | 100% | 100% | 100% | 100% | SI
2020-10-10 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-10 | 19 | TER TOCOPILLA U16-TG-TV | 0% | 100% | 0% | 0% | SI
2020-10-10 | 20 | TER TOCOPILLA U16-TG-TV | 34% | 100% | 34% | 0% | SI
2020-10-10 | 21 | TER TOCOPILLA U16-TG-TV | 100% | 100% | 100% | 100% | SI
2020-10-10 | 22 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-10 | 23 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE ANGOSTURA U3 | 66% | 100% | 66% | 0% | SI
2020-10-11 | 10 | HE ANGOSTURA U3 | 40% | 100% | 40% | 0% | SI
2020-10-11 | 11 | HE ANGOSTURA U3 | 50% | 100% | 50% | 0% | SI
2020-10-11 | 12 | HE ANGOSTURA U3 | 0% | 100% | 0% | 0% | SI
2020-10-11 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 0 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 13 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 23 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 0 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 13 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 16 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 10 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 13 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 16 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE COLBÚN U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE COLBÚN U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 1 | HE PANGUE U1 | 75% | 100% | 75% | 75% | SI
2020-10-11 | 2 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 3 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 4 | HE PANGUE U1 | 75% | 100% | 75% | 75% | SI
2020-10-11 | 5 | HE PANGUE U1 | 50% | 100% | 50% | 0% | SI
2020-10-11 | 6 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 7 | HE PANGUE U1 | 60% | 100% | 60% | 0% | SI
2020-10-11 | 8 | HE PANGUE U1 | 80% | 100% | 80% | 80% | SI
2020-10-11 | 9 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 11 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 12 | HE PANGUE U1 | 80% | 100% | 80% | 80% | SI
2020-10-11 | 13 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 14 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 15 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 17 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 18 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 19 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 20 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 21 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 22 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 23 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 0 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 2 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 3 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 4 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 5 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 6 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 12 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 13 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 14 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 15 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 16 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 17 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE PEHUENCHE U1 | 67% | 100% | 67% | 0% | SI
2020-10-11 | 23 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 3 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 4 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 5 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 6 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 7 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE PEHUENCHE U2 | 80% | 100% | 80% | 80% | SI
2020-10-11 | 12 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 13 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 14 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 15 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 16 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 17 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 1 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 2 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 3 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 4 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 5 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 6 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 7 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 8 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 9 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 10 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 11 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 12 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 13 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 14 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 15 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 16 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 17 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 18 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 19 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 20 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 21 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 22 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 23 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 0 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 1 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 2 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 3 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 4 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 5 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 6 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 7 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 8 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 9 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 10 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 11 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 12 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 13 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 14 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 15 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 17 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 18 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 19 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 20 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 21 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 22 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 23 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 96.67% | 0% | 0% | NO
2020-10-11 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 0 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-11 | 8 | TER COCHRANE U2 | 75% | 100% | 75% | 75% | SI
2020-10-11 | 9 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 10 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 11 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 12 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-11 | 13 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 14 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 15 | TER COCHRANE U2 | 66% | 100% | 66% | 0% | SI
2020-10-11 | 16 | TER COCHRANE U2 | 60% | 100% | 60% | 0% | SI
2020-10-11 | 17 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 18 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-11 | 19 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | TER GUACOLDA U3 | 0% | 100% | 0% | 0% | SI
2020-10-11 | 1 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 2 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 3 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 15 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-11 | 16 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 17 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-11 | 18 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 19 | TER GUACOLDA U3 | 80% | 100% | 80% | 80% | SI
2020-10-11 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 21 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 22 | TER GUACOLDA U3 | 75% | 100% | 75% | 75% | SI
2020-10-11 | 23 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 0 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 1 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 2 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 3 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 4 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 5 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 6 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-11 | 7 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 8 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 9 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 10 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 11 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 12 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 13 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 14 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 15 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 16 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 17 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 18 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 19 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 20 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 21 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-11 | 22 | TER GUACOLDA U4 | 34% | 100% | 34% | 0% | SI
2020-10-11 | 23 | TER GUACOLDA U4 | 40% | 100% | 40% | 0% | SI
2020-10-11 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 18 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 1 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 2 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 3 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 4 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 5 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 6 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 20 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 21 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 22 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 23 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 1 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 2 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 3 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 4 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 5 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 6 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 7 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 8 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 9 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 10 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 11 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 12 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 13 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 14 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 15 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 16 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 17 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 18 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 19 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 20 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 21 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 22 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 23 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 0 | TER MEJILLONES CTM3-TG | 33% | 100% | 33% | 0% | SI
2020-10-11 | 1 | TER MEJILLONES CTM3-TG | 67% | 100% | 67% | 0% | SI
2020-10-11 | 2 | TER MEJILLONES CTM3-TG | 80% | 100% | 80% | 80% | SI
2020-10-11 | 3 | TER MEJILLONES CTM3-TG | 50% | 100% | 50% | 0% | SI
2020-10-11 | 4 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 5 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-11 | 6 | TER MEJILLONES CTM3-TG | 50% | 100% | 50% | 0% | SI
2020-10-11 | 7 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | TER MEJILLONES CTM3-TG | 25% | 100% | 25% | 0% | SI
2020-10-11 | 0 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 8 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 18 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 19 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-11 | 20 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 21 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-11 | 22 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | TER NORGENER U2 | 25% | 100% | 25% | 0% | SI
2020-10-11 | 4 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-11 | 7 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 8 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-11 | 9 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 10 | TER NORGENER U2 | 25% | 100% | 25% | 0% | SI
2020-10-11 | 11 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 12 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-11 | 13 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 14 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 15 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 16 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 17 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 18 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 19 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-11 | 21 | TER NORGENER U2 | 80% | 100% | 80% | 80% | SI
2020-10-11 | 22 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 13 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 14 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 15 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 16 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 17 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 18 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 19 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 21 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 22 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-11 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-11 | 0 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 1 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 2 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 3 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 4 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 5 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-11 | 6 | TER TOCOPILLA U14 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 7 | TER TOCOPILLA U14 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 8 | TER TOCOPILLA U14 | 80% | 91.67% | 73.33% | 0% | SI
2020-10-11 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-11 | 23 | TER TOCOPILLA U14 | No Participó | 25% | 25% | 0% | SI
2020-10-11 | 0 | TER TOCOPILLA U15 | 60% | 100% | 60% | 0% | SI
2020-10-11 | 1 | TER TOCOPILLA U15 | 66% | 100% | 66% | 0% | SI
2020-10-11 | 2 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 3 | TER TOCOPILLA U15 | 17% | 100% | 17% | 0% | SI
2020-10-11 | 4 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 5 | TER TOCOPILLA U15 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 6 | TER TOCOPILLA U15 | 25% | 100% | 25% | 0% | SI
2020-10-11 | 7 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 8 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 9 | TER TOCOPILLA U15 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 10 | TER TOCOPILLA U15 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 11 | TER TOCOPILLA U15 | 80% | 100% | 80% | 80% | SI
2020-10-11 | 12 | TER TOCOPILLA U15 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 13 | TER TOCOPILLA U15 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 14 | TER TOCOPILLA U15 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 15 | TER TOCOPILLA U15 | 83% | 100% | 83% | 83% | SI
2020-10-11 | 16 | TER TOCOPILLA U15 | 67% | 100% | 67% | 0% | SI
2020-10-11 | 17 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 18 | TER TOCOPILLA U15 | 33% | 100% | 33% | 0% | SI
2020-10-11 | 19 | TER TOCOPILLA U15 | 50% | 100% | 50% | 0% | SI
2020-10-11 | 20 | TER TOCOPILLA U15 | 50% | 100% | 50% | 0% | SI
2020-10-11 | 21 | TER TOCOPILLA U15 | 50% | 100% | 50% | 0% | SI
2020-10-11 | 22 | TER TOCOPILLA U15 | 60% | 100% | 60% | 0% | SI
2020-10-11 | 23 | TER TOCOPILLA U15 | 66% | 100% | 66% | 0% | SI
2020-10-11 | 0 | TER TOCOPILLA U16-TG-TV | 100% | 100% | 100% | 100% | SI
2020-10-11 | 1 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 2 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 3 | TER TOCOPILLA U16-TG-TV | 66% | 100% | 66% | 0% | SI
2020-10-11 | 4 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 5 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 6 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 7 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-11 | 19 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 20 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 21 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-11 | 22 | TER TOCOPILLA U16-TG-TV | 50% | 100% | 50% | 0% | SI
2020-10-11 | 23 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 0 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 4 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 14 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 0 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 19 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 19 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE COLBÚN U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | HE PANGUE U1 | 0% | 100% | 0% | 0% | SI
2020-10-12 | 1 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 2 | HE PANGUE U1 | 80% | 100% | 80% | 80% | SI
2020-10-12 | 3 | HE PANGUE U1 | 60% | 100% | 60% | 0% | SI
2020-10-12 | 4 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 6 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 7 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE PANGUE U1 | 67% | 100% | 67% | 0% | SI
2020-10-12 | 10 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 15 | HE PANGUE U1 | 51% | 100% | 51% | 0% | SI
2020-10-12 | 16 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 17 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 19 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 20 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 23 | HE PANGUE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 0 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 1 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 2 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 3 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 4 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 5 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 6 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 7 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 10 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE PEHUENCHE U1 | 67% | 100% | 67% | 0% | SI
2020-10-12 | 12 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 14 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 15 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 16 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 18 | HE PEHUENCHE U1 | 50% | 100% | 50% | 0% | SI
2020-10-12 | 19 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 20 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 21 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 22 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 23 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 0 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 4 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 6 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 7 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 10 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE PEHUENCHE U2 | 67% | 100% | 67% | 0% | SI
2020-10-12 | 12 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 13 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 14 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 15 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 16 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 17 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 22 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 23 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 0 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 1 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 2 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 3 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 4 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 5 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 6 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 7 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 8 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 9 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 10 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 11 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 12 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 13 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 14 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 15 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 16 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 17 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 18 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 19 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 20 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 21 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 22 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 23 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 0 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 1 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 2 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 3 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 4 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 5 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 6 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 7 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 8 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 9 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 10 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 11 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 12 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 13 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 14 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 15 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 17 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 18 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 19 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 20 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 21 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 22 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 23 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 0 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | TER COCHRANE U2 | 60% | 100% | 60% | 0% | SI
2020-10-12 | 8 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-12 | 9 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 10 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 11 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-12 | 12 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 13 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-12 | 14 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 15 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 16 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-12 | 17 | TER COCHRANE U2 | 0% | 100% | 0% | 0% | SI
2020-10-12 | 18 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-12 | 19 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | TER GUACOLDA U3 | 80% | 100% | 80% | 80% | SI
2020-10-12 | 1 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 3 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 4 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 13 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 15 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 16 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 19 | TER GUACOLDA U3 | 66% | 100% | 66% | 0% | SI
2020-10-12 | 20 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 21 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER GUACOLDA U3 | 25% | 100% | 25% | 0% | SI
2020-10-12 | 0 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | TER GUACOLDA U4 | 80% | 100% | 80% | 80% | SI
2020-10-12 | 5 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 6 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 7 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 8 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 9 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 10 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 11 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 12 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 13 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 14 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 15 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 16 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 17 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 18 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 20 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 21 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 23 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-12 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 1 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 2 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 3 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 4 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 5 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 6 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 20 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 21 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 22 | TER KELAR CC1-TG1 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 23 | TER KELAR CC1-TG1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 20 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 21 | TER KELAR CC1-TG2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 22 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER KELAR CC1-TG2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 0 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 1 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 2 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 3 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 4 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 5 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 6 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 7 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 8 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 9 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 10 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 11 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 12 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 13 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 14 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 15 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 16 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 17 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 18 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 19 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 20 | TER MEJILLONES CTM1 | No Participó | 65% | 65% | 0% | SI
2020-10-12 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-12 | 0 | TER MEJILLONES CTM3-TG | 0% | 100% | 0% | 0% | SI
2020-10-12 | 1 | TER MEJILLONES CTM3-TG | 0% | 100% | 0% | 0% | SI
2020-10-12 | 2 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 3 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 4 | TER MEJILLONES CTM3-TG | 75% | 100% | 75% | 75% | SI
2020-10-12 | 5 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-12 | 6 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 7 | TER MEJILLONES CTM3-TG | 80% | 100% | 80% | 80% | SI
2020-10-12 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | TER MEJILLONES CTM3-TG | 60% | 100% | 60% | 0% | SI
2020-10-12 | 21 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 0 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | TER NORGENER U1 | 60% | 100% | 60% | 0% | SI
2020-10-12 | 8 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 16 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-12 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 18 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 19 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-12 | 8 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-12 | 9 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-12 | 10 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 11 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 12 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 13 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 14 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 15 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-12 | 16 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 17 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-12 | 18 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-12 | 19 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 13 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 14 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 15 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 16 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 17 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 20 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-12 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-12 | 0 | TER TOCOPILLA U14 | 60% | 100% | 60% | 0% | SI
2020-10-12 | 1 | TER TOCOPILLA U14 | 50% | 100% | 50% | 0% | SI
2020-10-12 | 2 | TER TOCOPILLA U14 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 3 | TER TOCOPILLA U14 | 67% | 100% | 67% | 0% | SI
2020-10-12 | 4 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 5 | TER TOCOPILLA U14 | 67% | 100% | 67% | 0% | SI
2020-10-12 | 6 | TER TOCOPILLA U14 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 7 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 8 | TER TOCOPILLA U14 | 50% | 100% | 50% | 0% | SI
2020-10-12 | 9 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 10 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 11 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 12 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 13 | TER TOCOPILLA U14 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 14 | TER TOCOPILLA U14 | 67% | 100% | 67% | 0% | SI
2020-10-12 | 15 | TER TOCOPILLA U14 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 16 | TER TOCOPILLA U14 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 17 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 18 | TER TOCOPILLA U14 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 19 | TER TOCOPILLA U14 | 67% | 100% | 67% | 0% | SI
2020-10-12 | 20 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 21 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER TOCOPILLA U14 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 23 | TER TOCOPILLA U14 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 0 | TER TOCOPILLA U15 | 80% | 100% | 80% | 80% | SI
2020-10-12 | 1 | TER TOCOPILLA U15 | 80% | 100% | 80% | 80% | SI
2020-10-12 | 2 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-12 | 3 | TER TOCOPILLA U15 | 50% | 100% | 50% | 0% | SI
2020-10-12 | 4 | TER TOCOPILLA U15 | 40% | 100% | 40% | 0% | SI
2020-10-12 | 5 | TER TOCOPILLA U15 | 60% | 100% | 60% | 0% | SI
2020-10-12 | 6 | TER TOCOPILLA U15 | 83% | 100% | 83% | 83% | SI
2020-10-12 | 7 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-12 | 8 | TER TOCOPILLA U15 | 40% | 100% | 40% | 0% | SI
2020-10-12 | 9 | TER TOCOPILLA U15 | 60% | 100% | 60% | 0% | SI
2020-10-12 | 10 | TER TOCOPILLA U15 | 25% | 100% | 25% | 0% | SI
2020-10-12 | 11 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-12 | 12 | TER TOCOPILLA U15 | 67% | 100% | 67% | 0% | SI
2020-10-12 | 13 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 14 | TER TOCOPILLA U15 | 67% | 100% | 67% | 0% | SI
2020-10-12 | 15 | TER TOCOPILLA U15 | 33% | 100% | 33% | 0% | SI
2020-10-12 | 16 | TER TOCOPILLA U15 | 34% | 100% | 34% | 0% | SI
2020-10-12 | 17 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-12 | 18 | TER TOCOPILLA U15 | 34% | 100% | 34% | 0% | SI
2020-10-12 | 19 | TER TOCOPILLA U15 | 17% | 100% | 17% | 0% | SI
2020-10-12 | 20 | TER TOCOPILLA U15 | 33% | 100% | 33% | 0% | SI
2020-10-12 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 0 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 1 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 2 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 3 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 4 | TER TOCOPILLA U16-TG-TV | 67% | 100% | 67% | 0% | SI
2020-10-12 | 5 | TER TOCOPILLA U16-TG-TV | 83% | 100% | 83% | 83% | SI
2020-10-12 | 6 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-12 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-12 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 3 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE CANUTILLAR U2 | 75% | 100% | 75% | 75% | SI
2020-10-13 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE PANGUE U1 | 75% | 100% | 75% | 75% | SI
2020-10-13 | 1 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 0 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE PEHUENCHE U2 | 80% | 100% | 80% | 80% | SI
2020-10-13 | 2 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 3 | HE PEHUENCHE U2 | 66% | 100% | 66% | 0% | SI
2020-10-13 | 4 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE PEHUENCHE U2 | 80% | 100% | 80% | 80% | SI
2020-10-13 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 1 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 11 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 17 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE RALCO U1 | 80% | 100% | 80% | 80% | SI
2020-10-13 | 19 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 0 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 20 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 21 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 22 | HE RALCO U2 | 80% | 100% | 80% | 80% | SI
2020-10-13 | 23 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 0 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 8 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 9 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 10 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 11 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-13 | 12 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-13 | 13 | TER COCHRANE U2 | 75% | 100% | 75% | 75% | SI
2020-10-13 | 14 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-13 | 15 | TER COCHRANE U2 | 75% | 100% | 75% | 75% | SI
2020-10-13 | 16 | TER COCHRANE U2 | 33% | 100% | 33% | 0% | SI
2020-10-13 | 17 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 18 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-13 | 19 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 21 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-13 | 22 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-13 | 23 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 0 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 10 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 11 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 12 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-13 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 14 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 15 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 16 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 17 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 18 | TER GUACOLDA U3 | 75% | 100% | 75% | 75% | SI
2020-10-13 | 19 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 21 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 22 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 23 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 0 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 1 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 2 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 3 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 4 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 5 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 6 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 7 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 8 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 9 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 10 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 11 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 12 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 13 | TER GUACOLDA U4 | 75% | 100% | 75% | 75% | SI
2020-10-13 | 14 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 15 | TER GUACOLDA U4 | 75% | 100% | 75% | 75% | SI
2020-10-13 | 16 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-13 | 17 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 18 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 20 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 21 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 22 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 23 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 10 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 11 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 12 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 13 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 14 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 15 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 16 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 17 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 18 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 0 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-13 | 7 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-13 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | TER MEJILLONES CTM3-TG | 80% | 100% | 80% | 80% | SI
2020-10-13 | 20 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-13 | 21 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-13 | 22 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-13 | 23 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-13 | 0 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | TER NORGENER U1 | 60% | 100% | 60% | 0% | SI
2020-10-13 | 8 | TER NORGENER U1 | 66% | 100% | 66% | 0% | SI
2020-10-13 | 9 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-13 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 11 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-13 | 12 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 13 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 14 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-13 | 15 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-13 | 16 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 18 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-13 | 19 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-13 | 20 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-13 | 21 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-13 | 22 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-13 | 23 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-13 | 0 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-13 | 7 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-13 | 8 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-13 | 9 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-13 | 10 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 11 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-13 | 12 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-13 | 13 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 14 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-13 | 15 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-13 | 16 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 17 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 18 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-13 | 19 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-13 | 20 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-13 | 21 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-13 | 23 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-13 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 9 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 10 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 11 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 12 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 13 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 14 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 15 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 16 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 17 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 18 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 19 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 20 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 21 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 22 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 21 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-13 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-13 | 0 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER TOCOPILLA U14 | 100% | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER TOCOPILLA U14 | No Participó | 93.33% | 93.33% | 93% | SI
2020-10-13 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 0 | TER TOCOPILLA U15 | 60% | 100% | 60% | 0% | SI
2020-10-13 | 1 | TER TOCOPILLA U15 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 2 | TER TOCOPILLA U15 | 67% | 100% | 67% | 0% | SI
2020-10-13 | 3 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 4 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 5 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 6 | TER TOCOPILLA U15 | 67% | 100% | 67% | 0% | SI
2020-10-13 | 7 | TER TOCOPILLA U15 | 20% | 100% | 20% | 0% | SI
2020-10-13 | 8 | TER TOCOPILLA U15 | 75% | 100% | 75% | 75% | SI
2020-10-13 | 9 | TER TOCOPILLA U15 | 17% | 100% | 17% | 0% | SI
2020-10-13 | 10 | TER TOCOPILLA U15 | 80% | 100% | 80% | 80% | SI
2020-10-13 | 11 | TER TOCOPILLA U15 | 60% | 100% | 60% | 0% | SI
2020-10-13 | 12 | TER TOCOPILLA U15 | 40% | 100% | 40% | 0% | SI
2020-10-13 | 13 | TER TOCOPILLA U15 | 66% | 100% | 66% | 0% | SI
2020-10-13 | 14 | TER TOCOPILLA U15 | 75% | 100% | 75% | 75% | SI
2020-10-13 | 15 | TER TOCOPILLA U15 | 33% | 100% | 33% | 0% | SI
2020-10-13 | 16 | TER TOCOPILLA U15 | 25% | 100% | 25% | 0% | SI
2020-10-13 | 17 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-13 | 18 | TER TOCOPILLA U15 | 17% | 100% | 17% | 0% | SI
2020-10-13 | 19 | TER TOCOPILLA U15 | 50% | 100% | 50% | 0% | SI
2020-10-13 | 20 | TER TOCOPILLA U15 | 67% | 100% | 67% | 0% | SI
2020-10-13 | 21 | TER TOCOPILLA U15 | 25% | 100% | 25% | 0% | SI
2020-10-13 | 22 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-13 | 23 | TER TOCOPILLA U15 | 83% | 100% | 83% | 83% | SI
2020-10-13 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-13 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 83.33% | 83.33% | 83% | SI
2020-10-13 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-13 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 13.33% | 13.33% | 0% | SI
2020-10-14 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE CANUTILLAR U1 | 67% | 100% | 67% | 0% | SI
2020-10-14 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 10 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 17 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 0 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE PEHUENCHE U1 | 50% | 100% | 50% | 0% | SI
2020-10-14 | 16 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE PEHUENCHE U1 | 0% | 100% | 0% | 0% | SI
2020-10-14 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE PEHUENCHE U2 | 80% | 100% | 80% | 80% | SI
2020-10-14 | 8 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE RALCO U1 | 80% | 100% | 80% | 80% | SI
2020-10-14 | 1 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 2 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 4 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 6 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 8 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 14 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 15 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 17 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 19 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 21 | HE RALCO U1 | 33% | 100% | 33% | 0% | SI
2020-10-14 | 22 | HE RALCO U1 | 80% | 100% | 80% | 80% | SI
2020-10-14 | 23 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE RALCO U2 | 80% | 100% | 80% | 80% | SI
2020-10-14 | 1 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 2 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 14 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 0 | TER COCHRANE U2 | 60% | 100% | 60% | 0% | SI
2020-10-14 | 1 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 2 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-14 | 3 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 4 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 5 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-14 | 6 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 7 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 8 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-14 | 9 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 10 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-14 | 11 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 12 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 13 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 14 | TER COCHRANE U2 | 33% | 100% | 33% | 0% | SI
2020-10-14 | 15 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-14 | 16 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-14 | 17 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 18 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 19 | TER COCHRANE U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 20 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-14 | 21 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-14 | 22 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 23 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 0 | TER GUACOLDA U3 | 80% | 100% | 80% | 80% | SI
2020-10-14 | 1 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 3 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 6 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 8 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 9 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 10 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 13 | TER GUACOLDA U3 | 20% | 100% | 20% | 0% | SI
2020-10-14 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 15 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 16 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 17 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 19 | TER GUACOLDA U3 | 75% | 100% | 75% | 75% | SI
2020-10-14 | 20 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 21 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 22 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 23 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 0 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 1 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 2 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 3 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 4 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 5 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 6 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 7 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 8 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 9 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 10 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-14 | 11 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-14 | 12 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-14 | 13 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 14 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 15 | TER GUACOLDA U4 | 75% | 100% | 75% | 75% | SI
2020-10-14 | 16 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 17 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 18 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 20 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 21 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 22 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 23 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 9 | TER HORNITOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 10 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 11 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 12 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 13 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 14 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 15 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 16 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 17 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 18 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | TER MEJILLONES CTM1 | 75% | 100% | 75% | 75% | SI
2020-10-14 | 1 | TER MEJILLONES CTM1 | 60% | 100% | 60% | 0% | SI
2020-10-14 | 2 | TER MEJILLONES CTM1 | 50% | 0% | 0% | 0% | SI
2020-10-14 | 3 | TER MEJILLONES CTM1 | No Participó | 31.67% | 31.67% | 0% | SI
2020-10-14 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | TER MEJILLONES CTM1 | No Participó | 73.33% | 73.33% | 0% | SI
2020-10-14 | 15 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 16 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 17 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 18 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 19 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 20 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 21 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 22 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 23 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 0 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-14 | 1 | TER MEJILLONES CTM3-TG | 66% | 100% | 66% | 0% | SI
2020-10-14 | 2 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-14 | 3 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-14 | 4 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-14 | 5 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-14 | 6 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-14 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | TER MEJILLONES CTM3-TG | No Participó | 91.67% | 91.67% | 92% | SI
2020-10-14 | 17 | TER MEJILLONES CTM3-TG | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 18 | TER MEJILLONES CTM3-TG | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 19 | TER MEJILLONES CTM3-TG | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 20 | TER MEJILLONES CTM3-TG | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 21 | TER MEJILLONES CTM3-TG | No Participó | 98.33% | 98.33% | 100% | SI
2020-10-14 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-14 | 0 | TER NORGENER U1 | 60% | 100% | 60% | 0% | SI
2020-10-14 | 1 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-14 | 2 | TER NORGENER U1 | 0% | 100% | 0% | 0% | SI
2020-10-14 | 3 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-14 | 4 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-14 | 5 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-14 | 6 | TER NORGENER U1 | 60% | 100% | 60% | 0% | SI
2020-10-14 | 7 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 8 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 9 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 11 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 18 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-14 | 19 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-14 | 20 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-14 | 21 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-14 | 22 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-14 | 23 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-14 | 0 | TER NORGENER U2 | 34% | 100% | 34% | 0% | SI
2020-10-14 | 1 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-14 | 2 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-14 | 3 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-14 | 4 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-14 | 5 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-14 | 6 | TER NORGENER U2 | 80% | 100% | 80% | 80% | SI
2020-10-14 | 7 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-14 | 8 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 9 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 10 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-14 | 11 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-14 | 12 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 13 | TER NORGENER U2 | 25% | 100% | 25% | 0% | SI
2020-10-14 | 14 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-14 | 15 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 16 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-14 | 17 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-14 | 18 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-14 | 19 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 20 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-14 | 21 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-14 | 22 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-14 | 23 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-14 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 17 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 18 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 19 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 20 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 21 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 22 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 23 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 17 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 18 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 19 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 20 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 21 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 22 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 23 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-14 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-14 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 0 | TER TOCOPILLA U15 | 66% | 100% | 66% | 0% | SI
2020-10-14 | 1 | TER TOCOPILLA U15 | 60% | 100% | 60% | 0% | SI
2020-10-14 | 2 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-14 | 3 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 4 | TER TOCOPILLA U15 | 66% | 100% | 66% | 0% | SI
2020-10-14 | 5 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 6 | TER TOCOPILLA U15 | 50% | 100% | 50% | 0% | SI
2020-10-14 | 7 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-14 | 8 | TER TOCOPILLA U15 | 20% | 100% | 20% | 0% | SI
2020-10-14 | 9 | TER TOCOPILLA U15 | 20% | 100% | 20% | 0% | SI
2020-10-14 | 10 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-14 | 11 | TER TOCOPILLA U15 | 50% | 100% | 50% | 0% | SI
2020-10-14 | 12 | TER TOCOPILLA U15 | 25% | 100% | 25% | 0% | SI
2020-10-14 | 13 | TER TOCOPILLA U15 | 50% | 100% | 50% | 0% | SI
2020-10-14 | 14 | TER TOCOPILLA U15 | 25% | 100% | 25% | 0% | SI
2020-10-14 | 15 | TER TOCOPILLA U15 | 40% | 100% | 40% | 0% | SI
2020-10-14 | 16 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-14 | 17 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-14 | 18 | TER TOCOPILLA U15 | 25% | 100% | 25% | 0% | SI
2020-10-14 | 19 | TER TOCOPILLA U15 | 66% | 100% | 66% | 0% | SI
2020-10-14 | 20 | TER TOCOPILLA U15 | 17% | 100% | 17% | 0% | SI
2020-10-14 | 21 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-14 | 22 | TER TOCOPILLA U15 | 50% | 100% | 50% | 0% | SI
2020-10-14 | 23 | TER TOCOPILLA U15 | 17% | 100% | 17% | 0% | SI
2020-10-14 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-14 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 91.67% | 91.67% | 92% | SI
2020-10-14 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-14 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 88.33% | 88.33% | 88% | SI
2020-10-14 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 73.33% | 73.33% | 0% | SI
2020-10-14 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 1.667% | 1.667% | 0% | SI
2020-10-15 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE ANGOSTURA U3 | 80% | 100% | 80% | 80% | SI
2020-10-15 | 10 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE CANUTILLAR U1 | 67% | 100% | 67% | 0% | SI
2020-10-15 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 9 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 12 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE PANGUE U1 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 8 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE PANGUE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE PANGUE U1 | 100% | 70% | 70% | 0% | SI
2020-10-15 | 23 | HE PANGUE U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 0 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE PEHUENCHE U1 | 75% | 100% | 75% | 75% | SI
2020-10-15 | 10 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 12 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 13 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 14 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE PEHUENCHE U2 | 75% | 100% | 75% | 75% | SI
2020-10-15 | 10 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE RALCO U1 | 75% | 100% | 75% | 75% | SI
2020-10-15 | 1 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 4 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 5 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 6 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE RALCO U1 | 80% | 100% | 80% | 80% | SI
2020-10-15 | 22 | HE RALCO U1 | 67% | 100% | 67% | 0% | SI
2020-10-15 | 23 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 7 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 11 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 14 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 16 | HE RALCO U2 | 50% | 100% | 50% | 0% | SI
2020-10-15 | 17 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 20 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE RALCO U2 | 50% | 100% | 50% | 0% | SI
2020-10-15 | 23 | HE RALCO U2 | 66% | 100% | 66% | 0% | SI
2020-10-15 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 0 | TER COCHRANE U2 | 60% | 100% | 60% | 0% | SI
2020-10-15 | 1 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 2 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 3 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-15 | 4 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 5 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 6 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-15 | 7 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 8 | TER COCHRANE U2 | 60% | 100% | 60% | 0% | SI
2020-10-15 | 9 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 10 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 11 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-15 | 12 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 13 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 14 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 15 | TER COCHRANE U2 | 33% | 100% | 33% | 0% | SI
2020-10-15 | 16 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 17 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 18 | TER COCHRANE U2 | 25% | 100% | 25% | 0% | SI
2020-10-15 | 19 | TER COCHRANE U2 | 33% | 100% | 33% | 0% | SI
2020-10-15 | 20 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-15 | 21 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | TER COCHRANE U2 | 60% | 100% | 60% | 0% | SI
2020-10-15 | 23 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 0 | TER GUACOLDA U3 | 60% | 100% | 60% | 0% | SI
2020-10-15 | 1 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 2 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-15 | 3 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 4 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 7 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 8 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 9 | TER GUACOLDA U3 | 75% | 100% | 75% | 75% | SI
2020-10-15 | 10 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 11 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 12 | TER GUACOLDA U3 | 50% | 100% | 50% | 0% | SI
2020-10-15 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 15 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 16 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 20 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 21 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 22 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 23 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 0 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 1 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 2 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 3 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 4 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 5 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 6 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-15 | 7 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-15 | 8 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 9 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 10 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 11 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 12 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 13 | TER GUACOLDA U4 | 33% | 100% | 33% | 0% | SI
2020-10-15 | 14 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-15 | 15 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 16 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 17 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 18 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 20 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 21 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 22 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 23 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 9 | TER HORNITOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 10 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 11 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 12 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 13 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 14 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 17 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 18 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | TER KELAR CC1-TG2 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 23 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 0 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 1 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 2 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 3 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 4 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 5 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 6 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 7 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 8 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 9 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 10 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 11 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 12 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 13 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 14 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 15 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 16 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 17 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 18 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 19 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 20 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 21 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 22 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 23 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 0 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 1 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 2 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 3 | TER MEJILLONES CTM3-TG | 75% | 100% | 75% | 75% | SI
2020-10-15 | 4 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 5 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 6 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 7 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 8 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-15 | 9 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 10 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 11 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 12 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 13 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 14 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 15 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 16 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 17 | TER MEJILLONES CTM3-TG | 67% | 100% | 67% | 0% | SI
2020-10-15 | 18 | TER MEJILLONES CTM3-TG | 67% | 100% | 67% | 0% | SI
2020-10-15 | 19 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 20 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 21 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 22 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-15 | 23 | TER MEJILLONES CTM3-TG | 66% | 100% | 66% | 0% | SI
2020-10-15 | 0 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 1 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-15 | 2 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-15 | 3 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-15 | 4 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-15 | 5 | TER NORGENER U1 | 0% | 100% | 0% | 0% | SI
2020-10-15 | 6 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 7 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 8 | TER NORGENER U1 | 75% | 100% | 75% | 75% | SI
2020-10-15 | 9 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 10 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-15 | 11 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-15 | 12 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-15 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 14 | TER NORGENER U1 | 75% | 100% | 75% | 75% | SI
2020-10-15 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 16 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-15 | 18 | TER NORGENER U1 | 60% | 100% | 60% | 0% | SI
2020-10-15 | 19 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-15 | 20 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-15 | 21 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-15 | 22 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-15 | 23 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-15 | 0 | TER NORGENER U2 | 34% | 100% | 34% | 0% | SI
2020-10-15 | 1 | TER NORGENER U2 | 80% | 100% | 80% | 80% | SI
2020-10-15 | 2 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-15 | 3 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-15 | 4 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-15 | 5 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-15 | 6 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 7 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-15 | 8 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-15 | 9 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 10 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-15 | 13 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-15 | 14 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-15 | 15 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-15 | 16 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-15 | 17 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-15 | 18 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-15 | 19 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-15 | 20 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-15 | 21 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-15 | 22 | TER NORGENER U2 | 25% | 100% | 25% | 0% | SI
2020-10-15 | 23 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-15 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 18 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 19 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 20 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 21 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 22 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 23 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 19 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 20 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 21 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-15 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-15 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-15 | 0 | TER TOCOPILLA U15 | 40% | 100% | 40% | 0% | SI
2020-10-15 | 1 | TER TOCOPILLA U15 | 33% | 100% | 33% | 0% | SI
2020-10-15 | 2 | TER TOCOPILLA U15 | 33% | 100% | 33% | 0% | SI
2020-10-15 | 3 | TER TOCOPILLA U15 | 40% | 100% | 40% | 0% | SI
2020-10-15 | 4 | TER TOCOPILLA U15 | 0% | 100% | 0% | 0% | SI
2020-10-15 | 5 | TER TOCOPILLA U15 | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-15 | 0 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 1 | TER TOCOPILLA U16-TG-TV | 50% | 100% | 50% | 0% | SI
2020-10-15 | 2 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 3 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 4 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 5 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 6 | TER TOCOPILLA U16-TG-TV | 75% | 100% | 75% | 75% | SI
2020-10-15 | 7 | TER TOCOPILLA U16-TG-TV | 50% | 100% | 50% | 0% | SI
2020-10-15 | 8 | TER TOCOPILLA U16-TG-TV | 75% | 100% | 75% | 75% | SI
2020-10-15 | 9 | TER TOCOPILLA U16-TG-TV | 50% | 100% | 50% | 0% | SI
2020-10-15 | 10 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 11 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 12 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 13 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 14 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 15 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 16 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 17 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 18 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 19 | TER TOCOPILLA U16-TG-TV | 0% | 100% | 0% | 0% | SI
2020-10-15 | 20 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 21 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-15 | 22 | TER TOCOPILLA U16-TG-TV | 83% | 100% | 83% | 83% | SI
2020-10-15 | 23 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE ANGOSTURA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 20 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 21 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 10 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 20 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 21 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE PANGUE U1 | No Participó | 85% | 85% | 85% | SI
2020-10-16 | 1 | HE PANGUE U1 | 66% | 0% | 0% | 0% | SI
2020-10-16 | 2 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 3 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 4 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 5 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 6 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 7 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-16 | 8 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 9 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 10 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 11 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 12 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 13 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 14 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 15 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 16 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 17 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 18 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 19 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 20 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 21 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 22 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 23 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-16 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 0 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE PEHUENCHE U1 | 80% | 100% | 80% | 80% | SI
2020-10-16 | 10 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 16 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 17 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 18 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 8 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE RALCO U1 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 23 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE RALCO U2 | 40% | 100% | 40% | 0% | SI
2020-10-16 | 1 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 19 | TER ANDINA U1 | No Participó | 25% | 25% | 0% | SI
2020-10-16 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 0 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 1 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-16 | 2 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-16 | 3 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 4 | TER COCHRANE U2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 5 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 6 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 7 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-16 | 8 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-16 | 9 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-16 | 10 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-16 | 11 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-16 | 12 | TER COCHRANE U2 | 40% | 100% | 40% | 0% | SI
2020-10-16 | 13 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 14 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 15 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 16 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 17 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 18 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 19 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 20 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-16 | 21 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 22 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 23 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 0 | TER GUACOLDA U3 | 80% | 100% | 80% | 80% | SI
2020-10-16 | 1 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 2 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 3 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 6 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 7 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 8 | TER GUACOLDA U3 | 50% | 100% | 50% | 0% | SI
2020-10-16 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 12 | TER GUACOLDA U3 | 40% | 100% | 40% | 0% | SI
2020-10-16 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 14 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 15 | TER GUACOLDA U3 | 50% | 100% | 50% | 0% | SI
2020-10-16 | 16 | TER GUACOLDA U3 | 75% | 100% | 75% | 75% | SI
2020-10-16 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 18 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 19 | TER GUACOLDA U3 | 75% | 100% | 75% | 75% | SI
2020-10-16 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 21 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 22 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 23 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 0 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 1 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 2 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 3 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 4 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 5 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 6 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 7 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 8 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 9 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 10 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 11 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 12 | TER GUACOLDA U4 | 20% | 100% | 20% | 0% | SI
2020-10-16 | 13 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 14 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 15 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 16 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 17 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 18 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 20 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 21 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 22 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 23 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 9 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 10 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 11 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 12 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 13 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 14 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 15 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 16 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 17 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 18 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 1 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 2 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 3 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 4 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 5 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 6 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 7 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 8 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 9 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 10 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 11 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 12 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 13 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 14 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 15 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 16 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 17 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 18 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 19 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 20 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 21 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 22 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 23 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 0 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 1 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 2 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 3 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 4 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 5 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 6 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 7 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 8 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 9 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 10 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 11 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 12 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 13 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 14 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 15 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 16 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 17 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 18 | TER MEJILLONES CTM3-TG | 80% | 100% | 80% | 80% | SI
2020-10-16 | 19 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 20 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 21 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 22 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 23 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-16 | 0 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-16 | 1 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 2 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-16 | 3 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-16 | 4 | TER NORGENER U1 | 60% | 100% | 60% | 0% | SI
2020-10-16 | 5 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-16 | 6 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-16 | 7 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 8 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-16 | 18 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 19 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-16 | 20 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 21 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 22 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 23 | TER NORGENER U1 | 66% | 100% | 66% | 0% | SI
2020-10-16 | 0 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-16 | 1 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-16 | 2 | TER NORGENER U2 | 80% | 100% | 80% | 80% | SI
2020-10-16 | 3 | TER NORGENER U2 | 34% | 100% | 34% | 0% | SI
2020-10-16 | 4 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-16 | 5 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-16 | 6 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-16 | 7 | TER NORGENER U2 | 25% | 100% | 25% | 0% | SI
2020-10-16 | 8 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-16 | 9 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 10 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 11 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 12 | TER NORGENER U2 | 80% | 100% | 80% | 80% | SI
2020-10-16 | 13 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 14 | TER NORGENER U2 | 34% | 100% | 34% | 0% | SI
2020-10-16 | 15 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 16 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 17 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 18 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-16 | 19 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-16 | 20 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-16 | 21 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 22 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-16 | 23 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-16 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 5 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 6 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 7 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 8 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 9 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 10 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 11 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 12 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 13 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 14 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 15 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 16 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 17 | TER QUINTERO U1 | 0% | 100% | 0% | 0% | SI
2020-10-16 | 18 | TER QUINTERO U1 | 20% | 100% | 20% | 0% | SI
2020-10-16 | 19 | TER QUINTERO U1 | 33% | 100% | 33% | 0% | SI
2020-10-16 | 20 | TER QUINTERO U1 | 66% | 100% | 66% | 0% | SI
2020-10-16 | 21 | TER QUINTERO U1 | 66% | 100% | 66% | 0% | SI
2020-10-16 | 22 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-16 | 23 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-16 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-16 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-16 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-16 | 0 | TER TOCOPILLA U16-TG-TV | 60% | 100% | 60% | 0% | SI
2020-10-16 | 1 | TER TOCOPILLA U16-TG-TV | 83% | 100% | 83% | 83% | SI
2020-10-16 | 2 | TER TOCOPILLA U16-TG-TV | 75% | 100% | 75% | 75% | SI
2020-10-16 | 3 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 4 | TER TOCOPILLA U16-TG-TV | 75% | 100% | 75% | 75% | SI
2020-10-16 | 5 | TER TOCOPILLA U16-TG-TV | 100% | 100% | 100% | 100% | SI
2020-10-16 | 6 | TER TOCOPILLA U16-TG-TV | 75% | 100% | 75% | 75% | SI
2020-10-16 | 7 | TER TOCOPILLA U16-TG-TV | 0% | 100% | 0% | 0% | SI
2020-10-16 | 8 | TER TOCOPILLA U16-TG-TV | 40% | 100% | 40% | 0% | SI
2020-10-16 | 9 | TER TOCOPILLA U16-TG-TV | 75% | 100% | 75% | 75% | SI
2020-10-16 | 10 | TER TOCOPILLA U16-TG-TV | 100% | 100% | 100% | 100% | SI
2020-10-16 | 11 | TER TOCOPILLA U16-TG-TV | 100% | 100% | 100% | 100% | SI
2020-10-16 | 12 | TER TOCOPILLA U16-TG-TV | 75% | 100% | 75% | 75% | SI
2020-10-16 | 13 | TER TOCOPILLA U16-TG-TV | 75% | 100% | 75% | 75% | SI
2020-10-16 | 14 | TER TOCOPILLA U16-TG-TV | 60% | 100% | 60% | 0% | SI
2020-10-16 | 15 | TER TOCOPILLA U16-TG-TV | 67% | 100% | 67% | 0% | SI
2020-10-16 | 16 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 17 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 18 | TER TOCOPILLA U16-TG-TV | 75% | 100% | 75% | 75% | SI
2020-10-16 | 19 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 20 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 21 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 22 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-16 | 23 | TER TOCOPILLA U16-TG-TV | 0% | 100% | 0% | 0% | SI
2020-10-17 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 16 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 10 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 1 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 2 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 3 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 4 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 5 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 6 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 7 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 8 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 9 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 10 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 11 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-17 | 12 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-17 | 13 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-17 | 14 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 15 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 16 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 17 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-17 | 18 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 19 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 20 | HE PANGUE U1 | 80% | 0% | 0% | 0% | SI
2020-10-17 | 21 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 22 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 23 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-17 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 0 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 16 | HE PEHUENCHE U1 | 80% | 100% | 80% | 80% | SI
2020-10-17 | 17 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE PEHUENCHE U2 | 67% | 100% | 67% | 0% | SI
2020-10-17 | 10 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 13 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 17 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 18 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE RALCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE RALCO U1 | 75% | 100% | 75% | 75% | SI
2020-10-17 | 19 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 2 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 6 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 10 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 15 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 18 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 19 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 0 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-17 | 1 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-17 | 2 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-17 | 3 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-17 | 4 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 5 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 6 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-17 | 7 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 8 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 9 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 10 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 11 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-17 | 12 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-17 | 13 | TER COCHRANE U2 | 33% | 100% | 33% | 0% | SI
2020-10-17 | 14 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 15 | TER COCHRANE U2 | 49% | 100% | 49% | 0% | SI
2020-10-17 | 16 | TER COCHRANE U2 | 0% | 100% | 0% | 0% | SI
2020-10-17 | 17 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-17 | 18 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 19 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 20 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 21 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 22 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 23 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 0 | TER GUACOLDA U3 | 80% | 100% | 80% | 80% | SI
2020-10-17 | 1 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 2 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 6 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-17 | 7 | TER GUACOLDA U3 | 66% | 100% | 66% | 0% | SI
2020-10-17 | 8 | TER GUACOLDA U3 | 33% | 100% | 33% | 0% | SI
2020-10-17 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 15 | TER GUACOLDA U3 | 66% | 100% | 66% | 0% | SI
2020-10-17 | 16 | TER GUACOLDA U3 | 75% | 100% | 75% | 75% | SI
2020-10-17 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 19 | TER GUACOLDA U3 | 40% | 100% | 40% | 0% | SI
2020-10-17 | 20 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 21 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 22 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 23 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 0 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 1 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 2 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 3 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 4 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 5 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 6 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-17 | 7 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-17 | 8 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 9 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 10 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 11 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-17 | 12 | TER GUACOLDA U4 | 17% | 100% | 17% | 0% | SI
2020-10-17 | 13 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-17 | 14 | TER GUACOLDA U4 | 33% | 100% | 33% | 0% | SI
2020-10-17 | 15 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-17 | 16 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-17 | 17 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 18 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 20 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 21 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 22 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 23 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 9 | TER HORNITOS U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 10 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 11 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 12 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 13 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 1 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 2 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 3 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 4 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 5 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 6 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 7 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 8 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 9 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 10 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 11 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 12 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 13 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 14 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 15 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 16 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 17 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 18 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 19 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 20 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 21 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 22 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 23 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 0 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-17 | 1 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-17 | 2 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-17 | 3 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-17 | 4 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-17 | 5 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-17 | 6 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-17 | 7 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-17 | 8 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-17 | 9 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-17 | 10 | TER MEJILLONES CTM3-TG | 75% | 100% | 75% | 75% | SI
2020-10-17 | 11 | TER MEJILLONES CTM3-TG | 50% | 100% | 50% | 0% | SI
2020-10-17 | 12 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-17 | 13 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-17 | 14 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 15 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-17 | 16 | TER MEJILLONES CTM3-TG | 50% | 100% | 50% | 0% | SI
2020-10-17 | 17 | TER MEJILLONES CTM3-TG | 40% | 100% | 40% | 0% | SI
2020-10-17 | 18 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-17 | 19 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-17 | 20 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-17 | 21 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-17 | 22 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-17 | 23 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-17 | 0 | TER NORGENER U1 | 80% | 100% | 80% | 80% | SI
2020-10-17 | 1 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-17 | 2 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 3 | TER NORGENER U1 | 40% | 100% | 40% | 0% | SI
2020-10-17 | 4 | TER NORGENER U1 | 0% | 100% | 0% | 0% | SI
2020-10-17 | 5 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-17 | 6 | TER NORGENER U1 | 66% | 100% | 66% | 0% | SI
2020-10-17 | 7 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-17 | 8 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 9 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 10 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-17 | 19 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 20 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-17 | 21 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 22 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-17 | 23 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-17 | 0 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-17 | 1 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-17 | 2 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-17 | 3 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-17 | 4 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-17 | 5 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-17 | 6 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-17 | 7 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-17 | 8 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 9 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-17 | 10 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-17 | 11 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-17 | 12 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 13 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-17 | 14 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-17 | 15 | TER NORGENER U2 | 25% | 100% | 25% | 0% | SI
2020-10-17 | 16 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-17 | 17 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-17 | 18 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-17 | 19 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-17 | 20 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-17 | 21 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-17 | 22 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-17 | 23 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-17 | 0 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 1 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 2 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 3 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 4 | TER QUINTERO U1 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 5 | TER QUINTERO U1 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 6 | TER QUINTERO U1 | 67% | 100% | 67% | 0% | SI
2020-10-17 | 7 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 8 | TER QUINTERO U1 | 49% | 100% | 49% | 0% | SI
2020-10-17 | 9 | TER QUINTERO U1 | 67% | 100% | 67% | 0% | SI
2020-10-17 | 10 | TER QUINTERO U1 | 67% | 100% | 67% | 0% | SI
2020-10-17 | 11 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 12 | TER QUINTERO U1 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 13 | TER QUINTERO U1 | 60% | 100% | 60% | 0% | SI
2020-10-17 | 14 | TER QUINTERO U1 | 0% | 100% | 0% | 0% | SI
2020-10-17 | 15 | TER QUINTERO U1 | 34% | 100% | 34% | 0% | SI
2020-10-17 | 16 | TER QUINTERO U1 | 60% | 100% | 60% | 0% | SI
2020-10-17 | 17 | TER QUINTERO U1 | 66% | 100% | 66% | 0% | SI
2020-10-17 | 18 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 19 | TER QUINTERO U1 | 49% | 100% | 49% | 0% | SI
2020-10-17 | 20 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 21 | TER QUINTERO U1 | 83% | 100% | 83% | 83% | SI
2020-10-17 | 22 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | TER QUINTERO U2 | 75% | 100% | 75% | 75% | SI
2020-10-17 | 10 | TER QUINTERO U2 | 50% | 100% | 50% | 0% | SI
2020-10-17 | 11 | TER QUINTERO U2 | 67% | 100% | 67% | 0% | SI
2020-10-17 | 12 | TER QUINTERO U2 | 50% | 100% | 50% | 0% | SI
2020-10-17 | 13 | TER QUINTERO U2 | 50% | 100% | 50% | 0% | SI
2020-10-17 | 14 | TER QUINTERO U2 | 75% | 100% | 75% | 75% | SI
2020-10-17 | 15 | TER QUINTERO U2 | 33% | 100% | 33% | 0% | SI
2020-10-17 | 16 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 17 | TER QUINTERO U2 | 50% | 100% | 50% | 0% | SI
2020-10-17 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-17 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-17 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 0 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 1 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 2 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 3 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 4 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 5 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 6 | TER TOCOPILLA U16-TG-TV | 50% | 100% | 50% | 0% | SI
2020-10-17 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-17 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 76.67% | 76.67% | 77% | SI
2020-10-17 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-17 | 19 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 20 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 21 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-17 | 22 | TER TOCOPILLA U16-TG-TV | 49% | 100% | 49% | 0% | SI
2020-10-17 | 23 | TER TOCOPILLA U16-TG-TV | 50% | 100% | 50% | 0% | SI
2020-10-18 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 4 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 4 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 11 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 20 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 21 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 10 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 20 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 21 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 1 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 2 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 3 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 4 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 5 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 6 | HE PANGUE U1 | 80% | 0% | 0% | 0% | SI
2020-10-18 | 7 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 8 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 9 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 10 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 11 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 12 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 13 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 14 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 15 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 16 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-18 | 17 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 18 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 19 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-18 | 20 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 21 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-18 | 22 | HE PANGUE U1 | 66% | 0% | 0% | 0% | SI
2020-10-18 | 23 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-18 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 0 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 4 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 6 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 7 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 11 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE PEHUENCHE U2 | 80% | 100% | 80% | 80% | SI
2020-10-18 | 9 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 10 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 11 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 12 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 18 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE RALCO U1 | 80% | 100% | 80% | 80% | SI
2020-10-18 | 1 | HE RALCO U1 | 33% | 100% | 33% | 0% | SI
2020-10-18 | 2 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 4 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 12 | HE RALCO U1 | 40% | 100% | 40% | 0% | SI
2020-10-18 | 13 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 14 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 15 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 17 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 18 | HE RALCO U1 | 80% | 100% | 80% | 80% | SI
2020-10-18 | 19 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE RALCO U1 | 60% | 100% | 60% | 0% | SI
2020-10-18 | 22 | HE RALCO U1 | 67% | 100% | 67% | 0% | SI
2020-10-18 | 23 | HE RALCO U1 | 80% | 100% | 80% | 80% | SI
2020-10-18 | 0 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 4 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE RALCO U2 | 60% | 100% | 60% | 0% | SI
2020-10-18 | 13 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE RALCO U2 | 66% | 100% | 66% | 0% | SI
2020-10-18 | 17 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE RALCO U2 | 75% | 100% | 75% | 75% | SI
2020-10-18 | 22 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 23 | HE RALCO U2 | 60% | 100% | 60% | 0% | SI
2020-10-18 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 0 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 1 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-18 | 2 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 3 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 4 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-18 | 5 | TER COCHRANE U2 | 60% | 100% | 60% | 0% | SI
2020-10-18 | 6 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 7 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 8 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 9 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 10 | TER COCHRANE U2 | 75% | 100% | 75% | 75% | SI
2020-10-18 | 11 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 12 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 13 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 14 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 15 | TER COCHRANE U2 | 33% | 100% | 33% | 0% | SI
2020-10-18 | 16 | TER COCHRANE U2 | 25% | 100% | 25% | 0% | SI
2020-10-18 | 17 | TER COCHRANE U2 | 40% | 100% | 40% | 0% | SI
2020-10-18 | 18 | TER COCHRANE U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER COCHRANE U2 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 20 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 21 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-18 | 22 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-18 | 23 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-18 | 0 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 1 | TER GUACOLDA U3 | 0% | 100% | 0% | 0% | SI
2020-10-18 | 2 | TER GUACOLDA U3 | 0% | 100% | 0% | 0% | SI
2020-10-18 | 3 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 15 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 16 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 21 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-18 | 22 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 23 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 0 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 1 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 2 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 3 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 4 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 5 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 6 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 7 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 8 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 9 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 10 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 11 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 12 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 13 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 14 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 15 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 16 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 17 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 18 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 20 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 21 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 22 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 23 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 8 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 1 | TER MEJILLONES CTM1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 2 | TER MEJILLONES CTM1 | No Participó | 1.667% | 1.667% | 0% | SI
2020-10-18 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 0 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-18 | 1 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-18 | 2 | TER MEJILLONES CTM3-TG | 66% | 100% | 66% | 0% | SI
2020-10-18 | 3 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 21 | TER MEJILLONES CTM3-TG | 20% | 100% | 20% | 0% | SI
2020-10-18 | 22 | TER MEJILLONES CTM3-TG | 50% | 100% | 50% | 0% | SI
2020-10-18 | 23 | TER MEJILLONES CTM3-TG | 67% | 100% | 67% | 0% | SI
2020-10-18 | 0 | TER NORGENER U1 | 40% | 100% | 40% | 0% | SI
2020-10-18 | 1 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-18 | 2 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-18 | 3 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-18 | 4 | TER NORGENER U1 | 66% | 100% | 66% | 0% | SI
2020-10-18 | 5 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-18 | 6 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-18 | 7 | TER NORGENER U1 | 34% | 100% | 34% | 0% | SI
2020-10-18 | 8 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 17 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-18 | 20 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 21 | TER NORGENER U1 | 0% | 100% | 0% | 0% | SI
2020-10-18 | 22 | TER NORGENER U1 | 0% | 100% | 0% | 0% | SI
2020-10-18 | 23 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-18 | 0 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-18 | 1 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-18 | 2 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 3 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-18 | 4 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 5 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-18 | 6 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-18 | 7 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-18 | 8 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 9 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-18 | 10 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-18 | 11 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 12 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-18 | 13 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-18 | 14 | TER NORGENER U2 | 49% | 100% | 49% | 0% | SI
2020-10-18 | 15 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 16 | TER NORGENER U2 | 80% | 100% | 80% | 80% | SI
2020-10-18 | 17 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-18 | 18 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-18 | 19 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-18 | 20 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-18 | 21 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-18 | 22 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-18 | 23 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-18 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | TER QUINTERO U1 | No Participó | 38.33% | 38.33% | 0% | SI
2020-10-18 | 3 | TER QUINTERO U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 4 | TER QUINTERO U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 5 | TER QUINTERO U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 6 | TER QUINTERO U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 7 | TER QUINTERO U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 8 | TER QUINTERO U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 9 | TER QUINTERO U1 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 10 | TER QUINTERO U1 | No Verificable | 46.67% | 0% | 0% | SI
2020-10-18 | 11 | TER QUINTERO U1 | 66% | 100% | 66% | 0% | SI
2020-10-18 | 12 | TER QUINTERO U1 | 0% | 100% | 0% | 0% | SI
2020-10-18 | 13 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 14 | TER QUINTERO U1 | 34% | 100% | 34% | 0% | SI
2020-10-18 | 15 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 16 | TER QUINTERO U1 | 75% | 100% | 75% | 75% | SI
2020-10-18 | 17 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 18 | TER QUINTERO U1 | 100% | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 20 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 21 | TER QUINTERO U1 | 25% | 100% | 25% | 0% | SI
2020-10-18 | 22 | TER QUINTERO U1 | 33% | 100% | 33% | 0% | SI
2020-10-18 | 23 | TER QUINTERO U1 | 0% | 100% | 0% | 0% | SI
2020-10-18 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 5 | TER QUINTERO U2 | 20% | 100% | 20% | 0% | SI
2020-10-18 | 6 | TER QUINTERO U2 | 34% | 100% | 34% | 0% | SI
2020-10-18 | 7 | TER QUINTERO U2 | 50% | 100% | 50% | 0% | SI
2020-10-18 | 8 | TER QUINTERO U2 | 80% | 100% | 80% | 80% | SI
2020-10-18 | 9 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 10 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 11 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 12 | TER QUINTERO U2 | 0% | 100% | 0% | 0% | SI
2020-10-18 | 13 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 14 | TER QUINTERO U2 | 0% | 100% | 0% | 0% | SI
2020-10-18 | 15 | TER QUINTERO U2 | 50% | 100% | 50% | 0% | SI
2020-10-18 | 16 | TER QUINTERO U2 | 50% | 100% | 50% | 0% | SI
2020-10-18 | 17 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 18 | TER QUINTERO U2 | 0% | 100% | 0% | 0% | SI
2020-10-18 | 19 | TER QUINTERO U2 | 0% | 100% | 0% | 0% | SI
2020-10-18 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-18 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-18 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-18 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 0 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 1 | TER TOCOPILLA U16-TG-TV | 50% | 100% | 50% | 0% | SI
2020-10-18 | 2 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 3 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 4 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 5 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 6 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-18 | 19 | TER TOCOPILLA U16-TG-TV | 50% | 100% | 50% | 0% | SI
2020-10-18 | 20 | TER TOCOPILLA U16-TG-TV | 40% | 100% | 40% | 0% | SI
2020-10-18 | 21 | TER TOCOPILLA U16-TG-TV | 0% | 100% | 0% | 0% | SI
2020-10-18 | 22 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-18 | 23 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 7 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 20 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE CANUTILLAR U1 | 66% | 100% | 66% | 0% | SI
2020-10-19 | 18 | HE CANUTILLAR U1 | 67% | 100% | 67% | 0% | SI
2020-10-19 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 20 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 21 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 10 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 1 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 2 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-19 | 3 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 4 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 5 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 6 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 7 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 8 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 9 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 10 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 11 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 12 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 13 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 14 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 15 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 16 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 17 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 18 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 19 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 20 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 21 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 22 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 23 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-19 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 0 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE RALCO U1 | 80% | 100% | 80% | 80% | SI
2020-10-19 | 1 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE RALCO U1 | 50% | 100% | 50% | 0% | SI
2020-10-19 | 4 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 5 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 13 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE RALCO U1 | 66% | 100% | 66% | 0% | SI
2020-10-19 | 18 | HE RALCO U1 | 60% | 100% | 60% | 0% | SI
2020-10-19 | 19 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE RALCO U1 | 67% | 100% | 67% | 0% | SI
2020-10-19 | 21 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 22 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 23 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE RALCO U2 | 80% | 100% | 80% | 80% | SI
2020-10-19 | 1 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 3 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 4 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 13 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 14 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE RALCO U2 | 75% | 100% | 75% | 75% | SI
2020-10-19 | 21 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE RALCO U2 | 80% | 100% | 80% | 80% | SI
2020-10-19 | 23 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 0 | TER ANGAMOS U1 | 40% | 100% | 40% | 0% | SI
2020-10-19 | 1 | TER ANGAMOS U1 | 66% | 100% | 66% | 0% | SI
2020-10-19 | 2 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-19 | 3 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 4 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-19 | 5 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 6 | TER ANGAMOS U1 | 33% | 100% | 33% | 0% | SI
2020-10-19 | 7 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 8 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-19 | 9 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-19 | 10 | TER ANGAMOS U1 | 66% | 100% | 66% | 0% | SI
2020-10-19 | 11 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 12 | TER ANGAMOS U1 | 33% | 100% | 33% | 0% | SI
2020-10-19 | 13 | TER ANGAMOS U1 | 17% | 100% | 17% | 0% | SI
2020-10-19 | 14 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 15 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-19 | 16 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 17 | TER ANGAMOS U1 | 33% | 100% | 33% | 0% | SI
2020-10-19 | 18 | TER ANGAMOS U1 | 33% | 100% | 33% | 0% | SI
2020-10-19 | 19 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 20 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 21 | TER ANGAMOS U1 | 33% | 100% | 33% | 0% | SI
2020-10-19 | 22 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-19 | 23 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-19 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 0 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 1 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 2 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-19 | 3 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 4 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 5 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-19 | 6 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 7 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 8 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 9 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-19 | 10 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 11 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-19 | 12 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-19 | 13 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-19 | 14 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 15 | TER COCHRANE U2 | 60% | 100% | 60% | 0% | SI
2020-10-19 | 16 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 17 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 18 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-19 | 19 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 20 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-19 | 21 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 22 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 23 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 0 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 1 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 3 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 15 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 16 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 18 | TER GUACOLDA U3 | 80% | 100% | 80% | 80% | SI
2020-10-19 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 21 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 22 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 23 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 0 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 5 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 6 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 7 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 8 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 9 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 10 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 11 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 12 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 13 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 14 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 15 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 16 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 17 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 18 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 19 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 20 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 21 | TER GUACOLDA U4 | 80% | 100% | 80% | 80% | SI
2020-10-19 | 22 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 23 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 3 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 9 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 10 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 0 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-19 | 1 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-19 | 2 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-19 | 3 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-19 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 21 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-19 | 22 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-19 | 23 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-19 | 0 | TER NORGENER U1 | 40% | 100% | 40% | 0% | SI
2020-10-19 | 1 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-19 | 2 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-19 | 3 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-19 | 4 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 5 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-19 | 6 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-19 | 7 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-19 | 8 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 19 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 20 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 21 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-19 | 22 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 23 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 0 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-19 | 1 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 2 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 3 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-19 | 4 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-19 | 5 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-19 | 6 | TER NORGENER U2 | 25% | 100% | 25% | 0% | SI
2020-10-19 | 7 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-19 | 8 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 9 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 10 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-19 | 11 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 12 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 13 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-19 | 14 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-19 | 15 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-19 | 16 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-19 | 17 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 18 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 19 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-19 | 20 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-19 | 21 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-19 | 22 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-19 | 23 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-19 | 0 | TER QUINTERO U1 | 49% | 100% | 49% | 0% | SI
2020-10-19 | 1 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 2 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 3 | TER QUINTERO U1 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 4 | TER QUINTERO U1 | 0% | 100% | 0% | 0% | SI
2020-10-19 | 5 | TER QUINTERO U1 | 66% | 100% | 66% | 0% | SI
2020-10-19 | 6 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 7 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 8 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 9 | TER QUINTERO U1 | 60% | 100% | 60% | 0% | SI
2020-10-19 | 10 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 11 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 12 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 13 | TER QUINTERO U1 | 75% | 100% | 75% | 75% | SI
2020-10-19 | 14 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 15 | TER QUINTERO U1 | 0% | 100% | 0% | 0% | SI
2020-10-19 | 16 | TER QUINTERO U1 | 67% | 100% | 67% | 0% | SI
2020-10-19 | 17 | TER QUINTERO U1 | 83% | 100% | 83% | 83% | SI
2020-10-19 | 18 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 19 | TER QUINTERO U1 | 75% | 100% | 75% | 75% | SI
2020-10-19 | 20 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-19 | 21 | TER QUINTERO U1 | 49% | 100% | 49% | 0% | SI
2020-10-19 | 22 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-19 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-19 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-19 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 0 | TER TOCOPILLA U16-TG-TV | 75% | 100% | 75% | 75% | SI
2020-10-19 | 1 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 2 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 3 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 4 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 5 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 6 | TER TOCOPILLA U16-TG-TV | 80% | 100% | 80% | 80% | SI
2020-10-19 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-19 | 19 | TER TOCOPILLA U16-TG-TV | 50% | 100% | 50% | 0% | SI
2020-10-19 | 20 | TER TOCOPILLA U16-TG-TV | 100% | 100% | 100% | 100% | SI
2020-10-19 | 21 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 22 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-19 | 23 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 14 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 10 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 11 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE CANUTILLAR U2 | 67% | 100% | 67% | 0% | SI
2020-10-20 | 21 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 10 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 23 | HE CIPRESES U3 | No Verificable | 85% | 0% | 0% | SI
2020-10-20 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 1 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 2 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 3 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 4 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 5 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 6 | HE PANGUE U1 | 80% | 0% | 0% | 0% | SI
2020-10-20 | 7 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-20 | 8 | HE PANGUE U1 | 50% | 0% | 0% | 0% | SI
2020-10-20 | 9 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 10 | HE PANGUE U1 | 67% | 0% | 0% | 0% | SI
2020-10-20 | 11 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 12 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 13 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 14 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 15 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 16 | HE PANGUE U1 | 80% | 0% | 0% | 0% | SI
2020-10-20 | 17 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 18 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-20 | 19 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 20 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 21 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 22 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 23 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-20 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 0 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 5 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 11 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 14 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 15 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 23 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 12 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 14 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE RALCO U1 | 80% | 100% | 80% | 80% | SI
2020-10-20 | 1 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 5 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE RALCO U1 | 80% | 100% | 80% | 80% | SI
2020-10-20 | 8 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 23 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 0 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 2 | HE RALCO U2 | 80% | 100% | 80% | 80% | SI
2020-10-20 | 3 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 5 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 6 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 7 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE RALCO U2 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 9 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 13 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 17 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE RALCO U2 | 67% | 100% | 67% | 0% | SI
2020-10-20 | 20 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE RALCO U2 | 80% | 100% | 80% | 80% | SI
2020-10-20 | 23 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE RAPEL U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 0 | TER ANGAMOS U1 | 80% | 100% | 80% | 80% | SI
2020-10-20 | 1 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 2 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 3 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 4 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 5 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 6 | TER ANGAMOS U1 | 17% | 100% | 17% | 0% | SI
2020-10-20 | 7 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 8 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 9 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 10 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-20 | 11 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 12 | TER ANGAMOS U1 | 66% | 100% | 66% | 0% | SI
2020-10-20 | 13 | TER ANGAMOS U1 | 66% | 100% | 66% | 0% | SI
2020-10-20 | 14 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 15 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 16 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 17 | TER ANGAMOS U1 | 17% | 100% | 17% | 0% | SI
2020-10-20 | 18 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | TER ANGAMOS U1 | 80% | 100% | 80% | 80% | SI
2020-10-20 | 21 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 22 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 23 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 0 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-20 | 1 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 2 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 3 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 4 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 5 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 6 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 7 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 8 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 9 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 10 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 11 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-20 | 12 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 13 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 14 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 15 | TER COCHRANE U2 | 75% | 100% | 75% | 75% | SI
2020-10-20 | 16 | TER COCHRANE U2 | 34% | 100% | 34% | 0% | SI
2020-10-20 | 17 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 18 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 19 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-20 | 21 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 22 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 23 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 0 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 1 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 8 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 9 | TER GUACOLDA U3 | 80% | 100% | 80% | 80% | SI
2020-10-20 | 10 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-20 | 11 | TER GUACOLDA U3 | 25% | 90% | 22.5% | 0% | SI
2020-10-20 | 12 | TER GUACOLDA U3 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 13 | TER GUACOLDA U3 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 14 | TER GUACOLDA U3 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 15 | TER GUACOLDA U3 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 16 | TER GUACOLDA U3 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 17 | TER GUACOLDA U3 | No Participó | 88.33% | 88.33% | 88% | SI
2020-10-20 | 18 | TER GUACOLDA U3 | 80% | 100% | 80% | 80% | SI
2020-10-20 | 19 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 20 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 21 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 22 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 23 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 0 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 1 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 2 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 3 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 4 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 5 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 6 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 7 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 8 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 9 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 10 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 11 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 12 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 13 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 14 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 15 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 16 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 17 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 18 | TER GUACOLDA U4 | 80% | 100% | 80% | 80% | SI
2020-10-20 | 19 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 20 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 21 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 22 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 23 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 8 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 9 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | TER HORNITOS U1 | No Participó | 1.667% | 1.667% | 0% | SI
2020-10-20 | 12 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 13 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 14 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 15 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 16 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 17 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 18 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 19 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 20 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 21 | TER HORNITOS U1 | No Participó | 35% | 35% | 0% | SI
2020-10-20 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 0 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-20 | 1 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-20 | 2 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-20 | 3 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-20 | 4 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 5 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-20 | 6 | TER MEJILLONES CTM3-TG | 100% | 100% | 100% | 100% | SI
2020-10-20 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 1 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 2 | TER NORGENER U1 | 66% | 100% | 66% | 0% | SI
2020-10-20 | 3 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 4 | TER NORGENER U1 | 75% | 100% | 75% | 75% | SI
2020-10-20 | 5 | TER NORGENER U1 | 75% | 100% | 75% | 75% | SI
2020-10-20 | 6 | TER NORGENER U1 | 60% | 100% | 60% | 0% | SI
2020-10-20 | 7 | TER NORGENER U1 | 0% | 100% | 0% | 0% | SI
2020-10-20 | 8 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-20 | 19 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 21 | TER NORGENER U1 | 40% | 100% | 40% | 0% | SI
2020-10-20 | 22 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-20 | 23 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 0 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-20 | 1 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-20 | 2 | TER NORGENER U2 | 34% | 100% | 34% | 0% | SI
2020-10-20 | 3 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-20 | 4 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 5 | TER NORGENER U2 | 34% | 100% | 34% | 0% | SI
2020-10-20 | 6 | TER NORGENER U2 | 25% | 100% | 25% | 0% | SI
2020-10-20 | 7 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-20 | 8 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 9 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-20 | 10 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-20 | 11 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-20 | 12 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 13 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 14 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 15 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 16 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-20 | 17 | TER NORGENER U2 | 34% | 100% | 34% | 0% | SI
2020-10-20 | 18 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 19 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-20 | 21 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 22 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-20 | 23 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-20 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | TER QUINTERO U1 | 0% | 100% | 0% | 0% | SI
2020-10-20 | 9 | TER QUINTERO U1 | 33% | 100% | 33% | 0% | SI
2020-10-20 | 10 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 11 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 12 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 13 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 14 | TER QUINTERO U1 | 75% | 100% | 75% | 75% | SI
2020-10-20 | 15 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 16 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 17 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 18 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-20 | 19 | TER QUINTERO U1 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 20 | TER QUINTERO U1 | 83% | 100% | 83% | 83% | SI
2020-10-20 | 21 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 22 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-20 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-20 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-20 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 0 | TER TOCOPILLA U16-TG-TV | 75% | 100% | 75% | 75% | SI
2020-10-20 | 1 | TER TOCOPILLA U16-TG-TV | 100% | 100% | 100% | 100% | SI
2020-10-20 | 2 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 3 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 4 | TER TOCOPILLA U16-TG-TV | 75% | 100% | 75% | 75% | SI
2020-10-20 | 5 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 6 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 7 | TER TOCOPILLA U16-TG-TV | 66% | 100% | 66% | 0% | SI
2020-10-20 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-20 | 20 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 21 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 22 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-20 | 23 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 1 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE ANGOSTURA U2 | 66% | 100% | 66% | 0% | SI
2020-10-21 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 0 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 3 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 11 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 12 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 16 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 17 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 18 | HE CANUTILLAR U1 | 60% | 100% | 60% | 0% | SI
2020-10-21 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 4 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 13 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 20 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 21 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 1 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 2 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 3 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 4 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 5 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 6 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 7 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 8 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 9 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 10 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 11 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 12 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 13 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 14 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 15 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 16 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 17 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 18 | HE CIPRESES U3 | No Participó | 1.667% | 1.667% | 0% | SI
2020-10-21 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 20 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 21 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 0 | HE COLBÚN U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 1 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 2 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 3 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 4 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 5 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 6 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 7 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 8 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 9 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 10 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 11 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 12 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 13 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 14 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 15 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 16 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 17 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 18 | HE PANGUE U1 | 75% | 0% | 0% | 0% | SI
2020-10-21 | 19 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 20 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 21 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 22 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-21 | 23 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-21 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 0 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 1 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 3 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 4 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 5 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 6 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 7 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 8 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 14 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 17 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 11 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 12 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 1 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 2 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 3 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 7 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 8 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE RALCO U1 | 80% | 100% | 80% | 80% | SI
2020-10-21 | 10 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE RALCO U1 | 60% | 100% | 60% | 0% | SI
2020-10-21 | 21 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 22 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 23 | HE RALCO U1 | 66% | 100% | 66% | 0% | SI
2020-10-21 | 0 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 1 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE RALCO U2 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 3 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 4 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 5 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 7 | HE RALCO U2 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 8 | HE RALCO U2 | 66% | 100% | 66% | 0% | SI
2020-10-21 | 9 | HE RALCO U2 | 80% | 100% | 80% | 80% | SI
2020-10-21 | 10 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE RALCO U2 | 80% | 100% | 80% | 80% | SI
2020-10-21 | 13 | HE RALCO U2 | 66% | 100% | 66% | 0% | SI
2020-10-21 | 14 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 17 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 23 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 1 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 1 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE RAPEL U4 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 6 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 0 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 1 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 2 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 3 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 4 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 5 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 6 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 7 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 8 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 9 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 10 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 11 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 12 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 13 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 14 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 15 | TER ANGAMOS U1 | 0% | 100% | 0% | 0% | SI
2020-10-21 | 16 | TER ANGAMOS U1 | 34% | 100% | 34% | 0% | SI
2020-10-21 | 17 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 18 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 19 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 20 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 21 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 22 | TER ANGAMOS U1 | 17% | 100% | 17% | 0% | SI
2020-10-21 | 23 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 0 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 1 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 2 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 3 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 4 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 5 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 6 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 7 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 8 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 9 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 10 | TER COCHRANE U2 | 75% | 100% | 75% | 75% | SI
2020-10-21 | 11 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 12 | TER COCHRANE U2 | 25% | 100% | 25% | 0% | SI
2020-10-21 | 13 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 14 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 15 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 16 | TER COCHRANE U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 17 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 18 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 19 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 20 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 21 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 22 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 23 | TER COCHRANE U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 0 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 1 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 2 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 7 | TER GUACOLDA U3 | 75% | 100% | 75% | 75% | SI
2020-10-21 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 9 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 11 | TER GUACOLDA U3 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 12 | TER GUACOLDA U3 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 13 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 14 | TER GUACOLDA U3 | 75% | 100% | 75% | 75% | SI
2020-10-21 | 15 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 16 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 21 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 22 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 23 | TER GUACOLDA U3 | 40% | 100% | 40% | 0% | SI
2020-10-21 | 0 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 1 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 2 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 3 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 4 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 5 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 6 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 7 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 8 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 9 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 10 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 11 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 12 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 13 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 14 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 15 | TER GUACOLDA U4 | 25% | 100% | 25% | 0% | SI
2020-10-21 | 16 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 17 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 18 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 20 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 21 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 22 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 23 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 9 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 10 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 11 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 12 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 13 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 0 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 21 | TER MEJILLONES CTM3-TG | 75% | 100% | 75% | 75% | SI
2020-10-21 | 22 | TER MEJILLONES CTM3-TG | 50% | 100% | 50% | 0% | SI
2020-10-21 | 23 | TER MEJILLONES CTM3-TG | 0% | 100% | 0% | 0% | SI
2020-10-21 | 0 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 1 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 2 | TER NORGENER U1 | 75% | 100% | 75% | 75% | SI
2020-10-21 | 3 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 4 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 5 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 6 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 7 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 8 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 13 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 15 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 18 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 19 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 20 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 21 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 22 | TER NORGENER U1 | 75% | 100% | 75% | 75% | SI
2020-10-21 | 23 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-21 | 0 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 1 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-21 | 2 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 3 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 4 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 5 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-21 | 6 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 7 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-21 | 8 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-21 | 9 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 10 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-21 | 11 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 12 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-21 | 13 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-21 | 14 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-21 | 15 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-21 | 16 | TER NORGENER U2 | 80% | 100% | 80% | 80% | SI
2020-10-21 | 17 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 18 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-21 | 19 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 20 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-21 | 21 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-21 | 22 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-21 | 23 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-21 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-21 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-21 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-21 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 20 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 21 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-21 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-21 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 0 | HE CANUTILLAR U1 | 80% | 100% | 80% | 80% | SI
2020-10-22 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 3 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 11 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 12 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE CANUTILLAR U1 | 75% | 100% | 75% | 75% | SI
2020-10-22 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE CANUTILLAR U1 | 80% | 100% | 80% | 80% | SI
2020-10-22 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE CANUTILLAR U2 | 66% | 100% | 66% | 0% | SI
2020-10-22 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 10 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE CIPRESES U1 | No Participó | 20% | 20% | 0% | SI
2020-10-22 | 12 | HE CIPRESES U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 13 | HE CIPRESES U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 14 | HE CIPRESES U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 15 | HE CIPRESES U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 16 | HE CIPRESES U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 17 | HE CIPRESES U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 18 | HE CIPRESES U1 | No Participó | 93.33% | 93.33% | 93% | SI
2020-10-22 | 19 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE CIPRESES U2 | No Participó | 20% | 20% | 0% | SI
2020-10-22 | 12 | HE CIPRESES U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 13 | HE CIPRESES U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 14 | HE CIPRESES U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 15 | HE CIPRESES U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 16 | HE CIPRESES U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 17 | HE CIPRESES U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 18 | HE CIPRESES U2 | No Participó | 93.33% | 93.33% | 93% | SI
2020-10-22 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 10 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE CIPRESES U3 | No Participó | 20% | 20% | 0% | SI
2020-10-22 | 12 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 13 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 14 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 15 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 16 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 17 | HE CIPRESES U3 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 18 | HE CIPRESES U3 | No Participó | 93.33% | 93.33% | 93% | SI
2020-10-22 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE COLBÚN U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE COLBÚN U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-22 | 1 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-22 | 2 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-22 | 3 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-22 | 4 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-22 | 5 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-22 | 6 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-22 | 7 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-22 | 8 | HE PANGUE U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 9 | HE PANGUE U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 10 | HE PANGUE U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 11 | HE PANGUE U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 12 | HE PANGUE U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 13 | HE PANGUE U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 14 | HE PANGUE U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 15 | HE PANGUE U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 16 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-22 | 17 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-22 | 18 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-22 | 19 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-22 | 20 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-22 | 21 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-22 | 22 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-22 | 23 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-22 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 0 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 1 | HE PEHUENCHE U1 | 60% | 100% | 60% | 0% | SI
2020-10-22 | 2 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 3 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 4 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 5 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 6 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 4 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 9 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 11 | HE RALCO U1 | 67% | 100% | 67% | 0% | SI
2020-10-22 | 12 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 13 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 14 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE RALCO U1 | 80% | 100% | 80% | 80% | SI
2020-10-22 | 19 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 20 | HE RALCO U1 | 80% | 100% | 80% | 80% | SI
2020-10-22 | 21 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 2 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 3 | HE RALCO U2 | 80% | 100% | 80% | 80% | SI
2020-10-22 | 4 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 6 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 7 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 11 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 12 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 13 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 14 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 15 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 18 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE RALCO U2 | 40% | 100% | 40% | 0% | SI
2020-10-22 | 20 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE RAPEL U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE RAPEL U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 0 | TER ANGAMOS U1 | 60% | 100% | 60% | 0% | SI
2020-10-22 | 1 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 2 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-22 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 9 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-22 | 10 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-22 | 11 | TER ANGAMOS U1 | 80% | 100% | 80% | 80% | SI
2020-10-22 | 12 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-22 | 13 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 14 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 15 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-22 | 16 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 17 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-22 | 18 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 19 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 20 | TER ANGAMOS U1 | 66% | 100% | 66% | 0% | SI
2020-10-22 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | TER ANGAMOS U1 | 49% | 100% | 49% | 0% | SI
2020-10-22 | 23 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-22 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 0 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 1 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 2 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 3 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-22 | 4 | TER COCHRANE U2 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 5 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 6 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-22 | 7 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 8 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 9 | TER COCHRANE U2 | 60% | 100% | 60% | 0% | SI
2020-10-22 | 10 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 11 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 12 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-22 | 13 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 14 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 15 | TER COCHRANE U2 | 25% | 100% | 25% | 0% | SI
2020-10-22 | 16 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 17 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 18 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-22 | 19 | TER COCHRANE U2 | 75% | 100% | 75% | 75% | SI
2020-10-22 | 20 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 21 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 22 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 23 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 0 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 1 | TER GUACOLDA U3 | 50% | 100% | 50% | 0% | SI
2020-10-22 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 3 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 4 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-22 | 5 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-22 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 7 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-22 | 8 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-22 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 15 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 16 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 20 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 21 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 22 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 23 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 0 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 1 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 2 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 3 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 4 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 5 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 6 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 7 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 8 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 9 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 10 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 11 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 12 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 13 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 14 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 15 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 16 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 17 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 18 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 20 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 21 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 22 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 23 | TER GUACOLDA U4 | 75% | 100% | 75% | 75% | SI
2020-10-22 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 10 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 11 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 12 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 13 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | TER KELAR CC1-TG1 | No Participó | 23.33% | 23.33% | 0% | SI
2020-10-22 | 16 | TER KELAR CC1-TG1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 17 | TER KELAR CC1-TG1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 18 | TER KELAR CC1-TG1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 19 | TER KELAR CC1-TG1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 20 | TER KELAR CC1-TG1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 21 | TER KELAR CC1-TG1 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 22 | TER KELAR CC1-TG1 | No Participó | 58.33% | 58.33% | 0% | SI
2020-10-22 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 0 | TER MEJILLONES CTM3-TG | 75% | 100% | 75% | 75% | SI
2020-10-22 | 1 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 2 | TER MEJILLONES CTM3-TG | 20% | 100% | 20% | 0% | SI
2020-10-22 | 3 | TER MEJILLONES CTM3-TG | 33% | 100% | 33% | 0% | SI
2020-10-22 | 4 | TER MEJILLONES CTM3-TG | 60% | 100% | 60% | 0% | SI
2020-10-22 | 5 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 6 | TER MEJILLONES CTM3-TG | 20% | 100% | 20% | 0% | SI
2020-10-22 | 7 | TER MEJILLONES CTM3-TG | 0% | 100% | 0% | 0% | SI
2020-10-22 | 8 | TER MEJILLONES CTM3-TG | 0% | 100% | 0% | 0% | SI
2020-10-22 | 9 | TER MEJILLONES CTM3-TG | 50% | 100% | 50% | 0% | SI
2020-10-22 | 10 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 11 | TER MEJILLONES CTM3-TG | 60% | 100% | 60% | 0% | SI
2020-10-22 | 12 | TER MEJILLONES CTM3-TG | 40% | 100% | 40% | 0% | SI
2020-10-22 | 13 | TER MEJILLONES CTM3-TG | 67% | 100% | 67% | 0% | SI
2020-10-22 | 14 | TER MEJILLONES CTM3-TG | 83% | 100% | 83% | 83% | SI
2020-10-22 | 15 | TER MEJILLONES CTM3-TG | 67% | 100% | 67% | 0% | SI
2020-10-22 | 16 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 17 | TER MEJILLONES CTM3-TG | 60% | 100% | 60% | 0% | SI
2020-10-22 | 18 | TER MEJILLONES CTM3-TG | 34% | 100% | 34% | 0% | SI
2020-10-22 | 19 | TER MEJILLONES CTM3-TG | 0% | 100% | 0% | 0% | SI
2020-10-22 | 20 | TER MEJILLONES CTM3-TG | 25% | 100% | 25% | 0% | SI
2020-10-22 | 21 | TER MEJILLONES CTM3-TG | 60% | 100% | 60% | 0% | SI
2020-10-22 | 22 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 23 | TER MEJILLONES CTM3-TG | 25% | 100% | 25% | 0% | SI
2020-10-22 | 0 | TER NORGENER U1 | 75% | 100% | 75% | 75% | SI
2020-10-22 | 1 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-22 | 2 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-22 | 3 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-22 | 4 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-22 | 5 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-22 | 6 | TER NORGENER U1 | 40% | 100% | 40% | 0% | SI
2020-10-22 | 7 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-22 | 8 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 10 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | TER NORGENER U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 17 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-22 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-22 | 19 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-22 | 20 | TER NORGENER U1 | 20% | 100% | 20% | 0% | SI
2020-10-22 | 21 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-22 | 22 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-22 | 23 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 0 | TER NORGENER U2 | 80% | 100% | 80% | 80% | SI
2020-10-22 | 1 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-22 | 2 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-22 | 3 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-22 | 4 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-22 | 5 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-22 | 6 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-22 | 7 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-22 | 8 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-22 | 9 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 10 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 11 | TER NORGENER U2 | 80% | 100% | 80% | 80% | SI
2020-10-22 | 12 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-22 | 13 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 14 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-22 | 15 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 16 | TER NORGENER U2 | 80% | 100% | 80% | 80% | SI
2020-10-22 | 17 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 18 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-22 | 19 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-22 | 20 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-22 | 21 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-22 | 22 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-22 | 23 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-22 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-22 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-22 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-22 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-22 | 0 | TER TOCOPILLA U16-TG-TV | 75% | 100% | 75% | 75% | SI
2020-10-22 | 1 | TER TOCOPILLA U16-TG-TV | 66% | 100% | 66% | 0% | SI
2020-10-22 | 2 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 3 | TER TOCOPILLA U16-TG-TV | 100% | 100% | 100% | 100% | SI
2020-10-22 | 4 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 5 | TER TOCOPILLA U16-TG-TV | 0% | 100% | 0% | 0% | SI
2020-10-22 | 6 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 7 | TER TOCOPILLA U16-TG-TV | 100% | 100% | 100% | 100% | SI
2020-10-22 | 8 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 9 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 10 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 11 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 12 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 13 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 14 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 15 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 16 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 17 | TER TOCOPILLA U16-TG-TV | 0% | 100% | 0% | 0% | SI
2020-10-22 | 18 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 19 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 20 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 21 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 22 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-22 | 23 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE CANUTILLAR U1 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 12 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 13 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 19 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 10 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 1 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 2 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 3 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 4 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 5 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 6 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 7 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 8 | HE PANGUE U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 9 | HE PANGUE U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 10 | HE PANGUE U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 11 | HE PANGUE U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 12 | HE PANGUE U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 13 | HE PANGUE U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 14 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 15 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 16 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 17 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 18 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 19 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 20 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 21 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 22 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 23 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-23 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 0 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 15 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 17 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 2 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 4 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 5 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 6 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 7 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 8 | HE RALCO U1 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 9 | HE RALCO U1 | 60% | 100% | 60% | 0% | SI
2020-10-23 | 10 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 11 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE RALCO U1 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 16 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 17 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE RALCO U1 | 80% | 100% | 80% | 80% | SI
2020-10-23 | 20 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE RALCO U1 | 80% | 100% | 80% | 80% | SI
2020-10-23 | 0 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 5 | HE RALCO U2 | 66% | 100% | 66% | 0% | SI
2020-10-23 | 6 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 7 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 12 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 14 | HE RALCO U2 | 50% | 100% | 50% | 0% | SI
2020-10-23 | 15 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 17 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE RALCO U2 | 66% | 100% | 66% | 0% | SI
2020-10-23 | 19 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE RALCO U2 | 50% | 100% | 50% | 0% | SI
2020-10-23 | 23 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE RAPEL U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE RAPEL U3 | 80% | 100% | 80% | 80% | SI
2020-10-23 | 22 | HE RAPEL U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 0 | TER ANGAMOS U1 | 60% | 100% | 60% | 0% | SI
2020-10-23 | 1 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 2 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-23 | 3 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 4 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-23 | 5 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 6 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 7 | TER ANGAMOS U1 | 33% | 100% | 33% | 0% | SI
2020-10-23 | 8 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 9 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 10 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 11 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-23 | 12 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-23 | 13 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 14 | TER ANGAMOS U1 | 33% | 100% | 33% | 0% | SI
2020-10-23 | 15 | TER ANGAMOS U1 | 33% | 100% | 33% | 0% | SI
2020-10-23 | 16 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 17 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 18 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 19 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 20 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 21 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 22 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 23 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 0 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 1 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 2 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 3 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 4 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 5 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 6 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 7 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 8 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 9 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-23 | 10 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 11 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 12 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 13 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-23 | 14 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-23 | 15 | TER COCHRANE U2 | 66% | 100% | 66% | 0% | SI
2020-10-23 | 16 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 17 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 18 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 19 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 20 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 21 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-23 | 22 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-23 | 23 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 1 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 7 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 13 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 15 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 16 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 20 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 21 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 22 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 23 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 0 | TER GUACOLDA U4 | 80% | 100% | 80% | 80% | SI
2020-10-23 | 1 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 2 | TER GUACOLDA U4 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 3 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 4 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 5 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 6 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 7 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 8 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 9 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 10 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 11 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 12 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 13 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 14 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 15 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 16 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 17 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 18 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 19 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 20 | TER GUACOLDA U4 | 20% | 100% | 20% | 0% | SI
2020-10-23 | 21 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 22 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 23 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 9 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 10 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 11 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 12 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 13 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 14 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 15 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 16 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 17 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 18 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 0 | TER MEJILLONES CTM3-TG | 34% | 100% | 34% | 0% | SI
2020-10-23 | 1 | TER MEJILLONES CTM3-TG | 80% | 100% | 80% | 80% | SI
2020-10-23 | 2 | TER MEJILLONES CTM3-TG | 50% | 100% | 50% | 0% | SI
2020-10-23 | 3 | TER MEJILLONES CTM3-TG | 80% | 100% | 80% | 80% | SI
2020-10-23 | 4 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 5 | TER MEJILLONES CTM3-TG | 50% | 100% | 50% | 0% | SI
2020-10-23 | 6 | TER MEJILLONES CTM3-TG | 34% | 100% | 34% | 0% | SI
2020-10-23 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | TER MEJILLONES CTM3-TG | 66% | 100% | 66% | 0% | SI
2020-10-23 | 20 | TER MEJILLONES CTM3-TG | 50% | 100% | 50% | 0% | SI
2020-10-23 | 21 | TER MEJILLONES CTM3-TG | 0% | 100% | 0% | 0% | SI
2020-10-23 | 22 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 23 | TER MEJILLONES CTM3-TG | 75% | 100% | 75% | 75% | SI
2020-10-23 | 0 | TER NORGENER U1 | 40% | 100% | 40% | 0% | SI
2020-10-23 | 1 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-23 | 2 | TER NORGENER U1 | 66% | 100% | 66% | 0% | SI
2020-10-23 | 3 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 4 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-23 | 5 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-23 | 6 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-23 | 7 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 8 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 12 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 19 | TER NORGENER U1 | 75% | 100% | 75% | 75% | SI
2020-10-23 | 20 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-23 | 21 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-23 | 22 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-23 | 23 | TER NORGENER U1 | 60% | 100% | 60% | 0% | SI
2020-10-23 | 0 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-23 | 1 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 2 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-23 | 3 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 4 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-23 | 5 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-23 | 6 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-23 | 7 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-23 | 8 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 9 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 10 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-23 | 11 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 12 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-23 | 13 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-23 | 14 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-23 | 15 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-23 | 16 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-23 | 17 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 18 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 19 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-23 | 20 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-23 | 21 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-23 | 22 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-23 | 23 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-23 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 21 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 22 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-23 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-23 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-23 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-23 | 0 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 1 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 2 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 3 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 4 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 5 | TER TOCOPILLA U16-TG-TV | 83% | 100% | 83% | 83% | SI
2020-10-23 | 6 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 7 | TER TOCOPILLA U16-TG-TV | 100% | 100% | 100% | 100% | SI
2020-10-23 | 8 | TER TOCOPILLA U16-TG-TV | 83% | 100% | 83% | 83% | SI
2020-10-23 | 9 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 10 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 11 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 12 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 13 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 14 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 15 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 16 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 17 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 18 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 19 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 20 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 21 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-23 | 22 | TER TOCOPILLA U16-TG-TV | 100% | 100% | 100% | 100% | SI
2020-10-23 | 23 | TER TOCOPILLA U16-TG-TV | 50% | 100% | 50% | 0% | SI
2020-10-24 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE ANGOSTURA U2 | 80% | 100% | 80% | 80% | SI
2020-10-24 | 22 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 12 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 13 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE CANUTILLAR U1 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 21 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 12 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE CANUTILLAR U2 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 10 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 1 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 2 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 3 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 4 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 5 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 6 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 7 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 8 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 9 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 10 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 11 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 12 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 13 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 14 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 15 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 16 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-24 | 17 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 18 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 19 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 20 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-24 | 21 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 22 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-24 | 23 | HE PANGUE U1 | 80% | 0% | 0% | 0% | SI
2020-10-24 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 0 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 16 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 22 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 23 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 2 | HE PEHUENCHE U2 | 34% | 100% | 34% | 0% | SI
2020-10-24 | 3 | HE PEHUENCHE U2 | 66% | 100% | 66% | 0% | SI
2020-10-24 | 4 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 10 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 12 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 13 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 14 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 15 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 16 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 18 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 2 | HE RALCO U1 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 3 | HE RALCO U1 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 4 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 9 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 11 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 12 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 13 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 14 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 15 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 16 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE RALCO U1 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 19 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 23 | HE RALCO U1 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 0 | HE RALCO U2 | 80% | 100% | 80% | 80% | SI
2020-10-24 | 1 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 2 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 3 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 6 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 10 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 11 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 12 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 13 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 14 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 15 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 16 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE RALCO U2 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 19 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE RALCO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE RALCO U2 | 60% | 100% | 60% | 0% | SI
2020-10-24 | 23 | HE RALCO U2 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE RAPEL U1 | No Participó | 5% | 5% | 0% | SI
2020-10-24 | 12 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 13 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 14 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 15 | HE RAPEL U1 | No Participó | 91.67% | 91.67% | 92% | SI
2020-10-24 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE RAPEL U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE RAPEL U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE RAPEL U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE RAPEL U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE RAPEL U2 | No Participó | 5% | 5% | 0% | SI
2020-10-24 | 12 | HE RAPEL U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 13 | HE RAPEL U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 14 | HE RAPEL U2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 15 | HE RAPEL U2 | No Participó | 91.67% | 91.67% | 92% | SI
2020-10-24 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE RAPEL U3 | No Participó | 5% | 5% | 0% | SI
2020-10-24 | 12 | HE RAPEL U3 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 13 | HE RAPEL U3 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 14 | HE RAPEL U3 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 15 | HE RAPEL U3 | No Participó | 91.67% | 91.67% | 92% | SI
2020-10-24 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE RAPEL U3 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE RAPEL U3 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE RAPEL U3 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE RAPEL U4 | No Participó | 5% | 5% | 0% | SI
2020-10-24 | 12 | HE RAPEL U4 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 13 | HE RAPEL U4 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 14 | HE RAPEL U4 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 15 | HE RAPEL U4 | No Participó | 91.67% | 91.67% | 92% | SI
2020-10-24 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | HE RAPEL U5 | No Participó | 5% | 5% | 0% | SI
2020-10-24 | 12 | HE RAPEL U5 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 13 | HE RAPEL U5 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 14 | HE RAPEL U5 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 15 | HE RAPEL U5 | No Participó | 91.67% | 91.67% | 92% | SI
2020-10-24 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 0 | TER ANGAMOS U1 | 20% | 100% | 20% | 0% | SI
2020-10-24 | 1 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 2 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 3 | TER ANGAMOS U1 | 66% | 100% | 66% | 0% | SI
2020-10-24 | 4 | TER ANGAMOS U1 | 17% | 100% | 17% | 0% | SI
2020-10-24 | 5 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 6 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 7 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 8 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 9 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 10 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 11 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 12 | TER ANGAMOS U1 | 66% | 100% | 66% | 0% | SI
2020-10-24 | 13 | TER ANGAMOS U1 | 17% | 100% | 17% | 0% | SI
2020-10-24 | 14 | TER ANGAMOS U1 | 17% | 100% | 17% | 0% | SI
2020-10-24 | 15 | TER ANGAMOS U1 | 40% | 100% | 40% | 0% | SI
2020-10-24 | 16 | TER ANGAMOS U1 | 33% | 100% | 33% | 0% | SI
2020-10-24 | 17 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 18 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 19 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 20 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 21 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 22 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 23 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 0 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-24 | 6 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 7 | TER COCHRANE U2 | 60% | 100% | 60% | 0% | SI
2020-10-24 | 8 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-24 | 9 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 10 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 11 | TER COCHRANE U2 | 33% | 100% | 33% | 0% | SI
2020-10-24 | 12 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 13 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 14 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 15 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 16 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 17 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 18 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 19 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 20 | TER COCHRANE U2 | 75% | 100% | 75% | 75% | SI
2020-10-24 | 21 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 22 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 23 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 0 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 1 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 3 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 10 | TER GUACOLDA U3 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 11 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 12 | TER GUACOLDA U3 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 15 | TER GUACOLDA U3 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 16 | TER GUACOLDA U3 | 33% | 100% | 33% | 0% | SI
2020-10-24 | 17 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 18 | TER GUACOLDA U3 | 80% | 100% | 80% | 80% | SI
2020-10-24 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 21 | TER GUACOLDA U3 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 22 | TER GUACOLDA U3 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 23 | TER GUACOLDA U3 | 80% | 100% | 80% | 80% | SI
2020-10-24 | 0 | TER GUACOLDA U4 | 20% | 100% | 20% | 0% | SI
2020-10-24 | 1 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 2 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 3 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 4 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 5 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 6 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 7 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 8 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 9 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 10 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 11 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 12 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 13 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 14 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 15 | TER GUACOLDA U4 | 51% | 100% | 51% | 0% | SI
2020-10-24 | 16 | TER GUACOLDA U4 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 17 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 18 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 20 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 21 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 22 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 23 | TER GUACOLDA U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 9 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 10 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 11 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 12 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 13 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 14 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 18 | TER HORNITOS U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 0 | TER MEJILLONES CTM3-TG | 40% | 100% | 40% | 0% | SI
2020-10-24 | 1 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 2 | TER MEJILLONES CTM3-TG | 0% | 100% | 0% | 0% | SI
2020-10-24 | 3 | TER MEJILLONES CTM3-TG | 33% | 100% | 33% | 0% | SI
2020-10-24 | 4 | TER MEJILLONES CTM3-TG | 0% | 100% | 0% | 0% | SI
2020-10-24 | 5 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 6 | TER MEJILLONES CTM3-TG | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 7 | TER MEJILLONES CTM3-TG | 40% | 100% | 40% | 0% | SI
2020-10-24 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | TER NORGENER U1 | 20% | 100% | 20% | 0% | SI
2020-10-24 | 1 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 2 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-24 | 3 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 4 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 5 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 6 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-24 | 7 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 8 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 19 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-24 | 20 | TER NORGENER U1 | 75% | 100% | 75% | 75% | SI
2020-10-24 | 21 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-24 | 22 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 23 | TER NORGENER U1 | 0% | 100% | 0% | 0% | SI
2020-10-24 | 0 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-24 | 1 | TER NORGENER U2 | 25% | 100% | 25% | 0% | SI
2020-10-24 | 2 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-24 | 3 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-24 | 4 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-24 | 5 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 6 | TER NORGENER U2 | 80% | 100% | 80% | 80% | SI
2020-10-24 | 7 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 8 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 9 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 10 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-24 | 11 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-24 | 12 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 13 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 14 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 15 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 16 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-24 | 17 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-24 | 18 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-24 | 19 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 20 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 21 | TER NORGENER U2 | 25% | 100% | 25% | 0% | SI
2020-10-24 | 22 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 23 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-24 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 9 | TER QUINTERO U1 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 10 | TER QUINTERO U1 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 11 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 12 | TER QUINTERO U1 | 0% | 100% | 0% | 0% | SI
2020-10-24 | 13 | TER QUINTERO U1 | 83% | 100% | 83% | 83% | SI
2020-10-24 | 14 | TER QUINTERO U1 | 66% | 100% | 66% | 0% | SI
2020-10-24 | 15 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 16 | TER QUINTERO U1 | 17% | 100% | 17% | 0% | SI
2020-10-24 | 17 | TER QUINTERO U1 | 0% | 100% | 0% | 0% | SI
2020-10-24 | 18 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 19 | TER QUINTERO U1 | 60% | 100% | 60% | 0% | SI
2020-10-24 | 20 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-24 | 21 | TER QUINTERO U1 | 67% | 100% | 67% | 0% | SI
2020-10-24 | 22 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 23 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 21 | TER QUINTERO U2 | 60% | 100% | 60% | 0% | SI
2020-10-24 | 22 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 23 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-24 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-24 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-24 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 0 | TER TOCOPILLA U16-TG-TV | 66% | 100% | 66% | 0% | SI
2020-10-24 | 1 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 2 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 3 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 4 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 5 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 6 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-24 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-24 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 3 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 8 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 12 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 20 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 21 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 8 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 20 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 21 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE COLBÚN U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 12 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-25 | 1 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-25 | 2 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-25 | 3 | HE PANGUE U1 | 67% | 0% | 0% | 0% | SI
2020-10-25 | 4 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-25 | 5 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-25 | 6 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-25 | 7 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-25 | 8 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-25 | 9 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-25 | 10 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-25 | 11 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-25 | 12 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-25 | 13 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-25 | 14 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-25 | 15 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-25 | 16 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-25 | 17 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-25 | 18 | HE PANGUE U1 | 60% | 0% | 0% | 0% | SI
2020-10-25 | 19 | HE PANGUE U1 | 75% | 0% | 0% | 0% | SI
2020-10-25 | 20 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-25 | 21 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-25 | 22 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-25 | 23 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-25 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 0 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 12 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 13 | HE PEHUENCHE U1 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 14 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 15 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 16 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 17 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 21 | HE PEHUENCHE U1 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 22 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 23 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 0 | HE PEHUENCHE U2 | 60% | 100% | 60% | 0% | SI
2020-10-25 | 1 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 2 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 3 | HE PEHUENCHE U2 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 4 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 6 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 8 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 9 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 11 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 12 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 14 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 16 | HE PEHUENCHE U2 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 17 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE PEHUENCHE U2 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 21 | HE PEHUENCHE U2 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 22 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 23 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 0 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE RALCO U1 | 66% | 100% | 66% | 0% | SI
2020-10-25 | 2 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 3 | HE RALCO U1 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 4 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 5 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 6 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 8 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 13 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 19 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 20 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 22 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 23 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 2 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 3 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 4 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 6 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 14 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 17 | HE RALCO U2 | 33% | 100% | 33% | 0% | SI
2020-10-25 | 18 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE RALCO U2 | 33% | 100% | 33% | 0% | SI
2020-10-25 | 20 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 21 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 22 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 23 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE RAPEL U4 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 20 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 0 | TER ANGAMOS U1 | 20% | 100% | 20% | 0% | SI
2020-10-25 | 1 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 2 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 3 | TER ANGAMOS U1 | 40% | 100% | 40% | 0% | SI
2020-10-25 | 4 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 5 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 6 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 7 | TER ANGAMOS U1 | 33% | 100% | 33% | 0% | SI
2020-10-25 | 8 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 9 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 10 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 11 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 12 | TER ANGAMOS U1 | 66% | 100% | 66% | 0% | SI
2020-10-25 | 13 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 14 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 15 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 16 | TER ANGAMOS U1 | 66% | 100% | 66% | 0% | SI
2020-10-25 | 17 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 18 | TER ANGAMOS U1 | 33% | 100% | 33% | 0% | SI
2020-10-25 | 19 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 20 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 21 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 22 | TER ANGAMOS U1 | 66% | 100% | 66% | 0% | SI
2020-10-25 | 23 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 21 | TER ANGAMOS U2 | No Verificable | 46.67% | 0% | 0% | NO
2020-10-25 | 22 | TER ANGAMOS U2 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 23 | TER ANGAMOS U2 | No Verificable | 16.67% | 0% | 0% | NO
2020-10-25 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 0 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 1 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 2 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 3 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 4 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 5 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 6 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 7 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 8 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 9 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 10 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 11 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 12 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 13 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 14 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 15 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-25 | 16 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-25 | 17 | TER COCHRANE U2 | 75% | 100% | 75% | 75% | SI
2020-10-25 | 18 | TER COCHRANE U2 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 19 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 20 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 21 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 22 | TER COCHRANE U2 | 33% | 100% | 33% | 0% | SI
2020-10-25 | 23 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 0 | TER GUACOLDA U3 | 75% | 100% | 75% | 75% | SI
2020-10-25 | 1 | TER GUACOLDA U3 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 2 | TER GUACOLDA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 3 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | TER GUACOLDA U3 | 60% | 100% | 60% | 0% | SI
2020-10-25 | 8 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 1 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 2 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 3 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 4 | TER GUACOLDA U4 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 5 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 6 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 7 | TER GUACOLDA U4 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 8 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 8 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | TER HORNITOS U1 | No Participó | 66.67% | 66.67% | 0% | SI
2020-10-25 | 19 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 20 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 21 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 22 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 23 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 0 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | TER NORGENER U1 | 75% | 100% | 75% | 75% | SI
2020-10-25 | 1 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-25 | 2 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 3 | TER NORGENER U1 | 0% | 100% | 0% | 0% | SI
2020-10-25 | 4 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-25 | 5 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 6 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 7 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 8 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 19 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 20 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-25 | 21 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 22 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 23 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 0 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-25 | 1 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-25 | 2 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-25 | 3 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 4 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 5 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 6 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 7 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 8 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 9 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 10 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-25 | 11 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 12 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-25 | 13 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-25 | 14 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 15 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 16 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-25 | 17 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 18 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 19 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 20 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-25 | 21 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-25 | 22 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 23 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 0 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 1 | TER QUINTERO U1 | 34% | 100% | 34% | 0% | SI
2020-10-25 | 2 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 3 | TER QUINTERO U1 | 17% | 100% | 17% | 0% | SI
2020-10-25 | 4 | TER QUINTERO U1 | 0% | 100% | 0% | 0% | SI
2020-10-25 | 5 | TER QUINTERO U1 | 75% | 100% | 75% | 75% | SI
2020-10-25 | 6 | TER QUINTERO U1 | 67% | 100% | 67% | 0% | SI
2020-10-25 | 7 | TER QUINTERO U1 | 66% | 100% | 66% | 0% | SI
2020-10-25 | 8 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 9 | TER QUINTERO U1 | 33% | 100% | 33% | 0% | SI
2020-10-25 | 10 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 11 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 12 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 13 | TER QUINTERO U1 | 75% | 100% | 75% | 75% | SI
2020-10-25 | 14 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 15 | TER QUINTERO U1 | 34% | 100% | 34% | 0% | SI
2020-10-25 | 16 | TER QUINTERO U1 | 83% | 100% | 83% | 83% | SI
2020-10-25 | 17 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 18 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 19 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-25 | 20 | TER QUINTERO U1 | 100% | 100% | 100% | 100% | SI
2020-10-25 | 21 | TER QUINTERO U1 | 25% | 100% | 25% | 0% | SI
2020-10-25 | 22 | TER QUINTERO U1 | 66% | 100% | 66% | 0% | SI
2020-10-25 | 23 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-25 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-25 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-25 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 71.67% | 71.67% | 0% | SI
2020-10-25 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-25 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 16.67% | 16.67% | 0% | SI
2020-10-25 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-25 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 9 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 12 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 15 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 18 | HE CANUTILLAR U1 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 10 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 10 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 16 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 1 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 2 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 3 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 4 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 5 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 6 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 7 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 8 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 9 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 10 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 11 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 12 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 13 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 14 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 15 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 16 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 17 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 18 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 19 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 20 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 21 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 22 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 23 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-26 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 0 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE PEHUENCHE U1 | 80% | 100% | 80% | 80% | SI
2020-10-26 | 2 | HE PEHUENCHE U1 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 3 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 5 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 6 | HE PEHUENCHE U1 | 40% | 100% | 40% | 0% | SI
2020-10-26 | 7 | HE PEHUENCHE U1 | 75% | 100% | 75% | 75% | SI
2020-10-26 | 8 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 12 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 13 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 9 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 12 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 13 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 18 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 19 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE RALCO U1 | 80% | 100% | 80% | 80% | SI
2020-10-26 | 1 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 2 | HE RALCO U1 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 3 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 4 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 5 | HE RALCO U1 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 6 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 7 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 8 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 9 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 12 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 0 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 1 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE RALCO U2 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 5 | HE RALCO U2 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 6 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 8 | HE RALCO U2 | 66% | 100% | 66% | 0% | SI
2020-10-26 | 9 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 10 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 12 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 13 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE RALCO U2 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 15 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 23 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE RAPEL U1 | No Participó | 86.67% | 86.67% | 87% | SI
2020-10-26 | 12 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 13 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 14 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 15 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 16 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 17 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 18 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 19 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 20 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 21 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 22 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 23 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 0 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 9 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 9 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 0 | TER ANGAMOS U1 | 40% | 100% | 40% | 0% | SI
2020-10-26 | 1 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 2 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 3 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 4 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 5 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 6 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 7 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 8 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 9 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 10 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 11 | TER ANGAMOS U1 | 33% | 100% | 33% | 0% | SI
2020-10-26 | 12 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 13 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 14 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 15 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 16 | TER ANGAMOS U1 | 20% | 100% | 20% | 0% | SI
2020-10-26 | 17 | TER ANGAMOS U1 | 40% | 100% | 40% | 0% | SI
2020-10-26 | 18 | TER ANGAMOS U1 | 66% | 100% | 66% | 0% | SI
2020-10-26 | 19 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 20 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 21 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 22 | TER ANGAMOS U1 | 66% | 100% | 66% | 0% | SI
2020-10-26 | 23 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 0 | TER COCHRANE U2 | 40% | 100% | 40% | 0% | SI
2020-10-26 | 1 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 2 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 3 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 4 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 5 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 6 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 7 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 8 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 9 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 10 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 11 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 12 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 13 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 14 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 15 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 16 | TER COCHRANE U2 | 0% | 100% | 0% | 0% | SI
2020-10-26 | 17 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 18 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 19 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 20 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 21 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 22 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 23 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 0 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 1 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 2 | TER HORNITOS U1 | No Participó | 10% | 10% | 0% | SI
2020-10-26 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 9 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 10 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 0 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | TER NORGENER U1 | 60% | 100% | 60% | 0% | SI
2020-10-26 | 1 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 2 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 3 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 4 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-26 | 5 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 6 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 7 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 8 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-26 | 19 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-26 | 20 | TER NORGENER U1 | 66% | 100% | 66% | 0% | SI
2020-10-26 | 21 | TER NORGENER U1 | 40% | 100% | 40% | 0% | SI
2020-10-26 | 22 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-26 | 23 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-26 | 0 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 1 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 2 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 3 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-26 | 4 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-26 | 5 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 6 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-26 | 7 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 8 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 9 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 10 | TER NORGENER U2 | 34% | 100% | 34% | 0% | SI
2020-10-26 | 11 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 12 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 13 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 14 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-26 | 15 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 16 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-26 | 17 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 18 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 19 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 20 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 21 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 22 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-26 | 23 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 0 | TER QUINTERO U1 | 60% | 100% | 60% | 0% | SI
2020-10-26 | 1 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 2 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 3 | TER QUINTERO U1 | 60% | 100% | 60% | 0% | SI
2020-10-26 | 4 | TER QUINTERO U1 | 66% | 100% | 66% | 0% | SI
2020-10-26 | 5 | TER QUINTERO U1 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 6 | TER QUINTERO U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 7 | TER QUINTERO U1 | 66% | 100% | 66% | 0% | SI
2020-10-26 | 8 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 9 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 10 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 11 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 12 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 13 | TER QUINTERO U1 | 75% | 100% | 75% | 75% | SI
2020-10-26 | 14 | TER QUINTERO U1 | 67% | 100% | 67% | 0% | SI
2020-10-26 | 15 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 16 | TER QUINTERO U1 | 83% | 100% | 83% | 83% | SI
2020-10-26 | 17 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 18 | TER QUINTERO U1 | 75% | 100% | 75% | 75% | SI
2020-10-26 | 19 | TER QUINTERO U1 | 75% | 100% | 75% | 75% | SI
2020-10-26 | 20 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 21 | TER QUINTERO U1 | 80% | 100% | 80% | 80% | SI
2020-10-26 | 22 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 23 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-26 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-26 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-26 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-26 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-26 | 20 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 21 | TER TOCOPILLA U16-TG-TV | 34% | 100% | 34% | 0% | SI
2020-10-26 | 22 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-26 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE ANGOSTURA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 15 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 5 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 0 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE CIPRESES U1 | 75% | 100% | 75% | 75% | SI
2020-10-27 | 8 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE CIPRESES U3 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 2 | HE CIPRESES U3 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 3 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 5 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 11 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE CIPRESES U3 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 14 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE CIPRESES U3 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 18 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE CIPRESES U3 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 21 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 1 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 2 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 3 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 4 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 5 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 6 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 7 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-27 | 8 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-27 | 9 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-27 | 10 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 11 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 12 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 13 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 14 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 15 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 16 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 17 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 18 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 19 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 20 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 21 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 22 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 23 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-27 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 0 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 1 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 2 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 5 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 7 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE PEHUENCHE U1 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 11 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 15 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 17 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 23 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 5 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 7 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE PEHUENCHE U2 | 40% | 100% | 40% | 0% | SI
2020-10-27 | 9 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 23 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 9 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 10 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 11 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 12 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE RALCO U1 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 14 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 15 | HE RALCO U1 | 34% | 100% | 34% | 0% | SI
2020-10-27 | 16 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 22 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 4 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 5 | HE RALCO U2 | 80% | 100% | 80% | 80% | SI
2020-10-27 | 6 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 10 | HE RALCO U2 | 80% | 100% | 80% | 80% | SI
2020-10-27 | 11 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE RALCO U2 | 66% | 100% | 66% | 0% | SI
2020-10-27 | 14 | HE RALCO U2 | 100% | 75% | 75% | 75% | SI
2020-10-27 | 15 | HE RALCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 16 | HE RALCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 17 | HE RALCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 18 | HE RALCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 19 | HE RALCO U2 | 100% | 83.33% | 83.33% | 83% | SI
2020-10-27 | 20 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 22 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 23 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 0 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 1 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 2 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 3 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 4 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 5 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 6 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 7 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 8 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 9 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 10 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 11 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 12 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 13 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 14 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 15 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 16 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 17 | HE RAPEL U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 18 | HE RAPEL U1 | No Participó | 90% | 90% | 90% | SI
2020-10-27 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE RAPEL U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE RAPEL U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE RAPEL U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE RAPEL U2 | 25% | 100% | 25% | 0% | SI
2020-10-27 | 14 | HE RAPEL U2 | 0% | 100% | 0% | 0% | SI
2020-10-27 | 15 | HE RAPEL U2 | 0% | 100% | 0% | 0% | SI
2020-10-27 | 16 | HE RAPEL U2 | 0% | 100% | 0% | 0% | SI
2020-10-27 | 17 | HE RAPEL U2 | 0% | 100% | 0% | 0% | SI
2020-10-27 | 18 | HE RAPEL U2 | 0% | 100% | 0% | 0% | SI
2020-10-27 | 19 | HE RAPEL U2 | 0% | 100% | 0% | 0% | SI
2020-10-27 | 20 | HE RAPEL U2 | 0% | 100% | 0% | 0% | SI
2020-10-27 | 21 | HE RAPEL U2 | 0% | 100% | 0% | 0% | SI
2020-10-27 | 22 | HE RAPEL U2 | 0% | 100% | 0% | 0% | SI
2020-10-27 | 23 | HE RAPEL U2 | 17% | 100% | 17% | 0% | SI
2020-10-27 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE RAPEL U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE RAPEL U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE RAPEL U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE RAPEL U3 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE RAPEL U4 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 2 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE RAPEL U4 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 9 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 0 | TER ANGAMOS U1 | 80% | 100% | 80% | 80% | SI
2020-10-27 | 1 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 2 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 3 | TER ANGAMOS U1 | 33% | 100% | 33% | 0% | SI
2020-10-27 | 4 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 5 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 6 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 7 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 8 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 9 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 10 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 11 | TER ANGAMOS U1 | 17% | 100% | 17% | 0% | SI
2020-10-27 | 12 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 13 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 14 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 15 | TER ANGAMOS U1 | No Participó | 13.33% | 13.33% | 0% | SI
2020-10-27 | 16 | TER ANGAMOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 17 | TER ANGAMOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 18 | TER ANGAMOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 19 | TER ANGAMOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 20 | TER ANGAMOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 21 | TER ANGAMOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 22 | TER ANGAMOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 23 | TER ANGAMOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 0 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-27 | 1 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 2 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 3 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 4 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 5 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 6 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 7 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 8 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 9 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 10 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 11 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 12 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 13 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 14 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 15 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 16 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 17 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 18 | TER COCHRANE U2 | 66% | 100% | 66% | 0% | SI
2020-10-27 | 19 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 20 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 21 | TER COCHRANE U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 22 | TER COCHRANE U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 23 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 0 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | TER HORNITOS U1 | No Participó | 21.67% | 21.67% | 0% | SI
2020-10-27 | 2 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 3 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 4 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 5 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 6 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 7 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 8 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 9 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 10 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 11 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 12 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 13 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 14 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 15 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 16 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 17 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 18 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 19 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 20 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 21 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 22 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 23 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | TER KELAR CC1-TG1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 2 | TER KELAR CC1-TG1 | 33% | 100% | 33% | 0% | SI
2020-10-27 | 3 | TER KELAR CC1-TG1 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 4 | TER KELAR CC1-TG1 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 5 | TER KELAR CC1-TG1 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 6 | TER KELAR CC1-TG1 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | TER KELAR CC1-TG1 | No Participó | 18.33% | 18.33% | 0% | SI
2020-10-27 | 18 | TER KELAR CC1-TG1 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 19 | TER KELAR CC1-TG1 | No Participó | 56.67% | 56.67% | 0% | SI
2020-10-27 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | TER KELAR CC1-TG2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 2 | TER KELAR CC1-TG2 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 3 | TER KELAR CC1-TG2 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 4 | TER KELAR CC1-TG2 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 5 | TER KELAR CC1-TG2 | 33% | 100% | 33% | 0% | SI
2020-10-27 | 6 | TER KELAR CC1-TG2 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 0 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 1 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-27 | 2 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-27 | 3 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-27 | 4 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 5 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 6 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 7 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-27 | 8 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 9 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 19 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-27 | 20 | TER NORGENER U1 | 40% | 100% | 40% | 0% | SI
2020-10-27 | 21 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 22 | TER NORGENER U1 | 25% | 100% | 25% | 0% | SI
2020-10-27 | 23 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 0 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 1 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 2 | TER NORGENER U2 | 80% | 100% | 80% | 80% | SI
2020-10-27 | 3 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 4 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 5 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-27 | 6 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 7 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 8 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-27 | 9 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-27 | 10 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 11 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 12 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 13 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 14 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 15 | TER NORGENER U2 | 34% | 100% | 34% | 0% | SI
2020-10-27 | 16 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 17 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 18 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 19 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 20 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 21 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-27 | 22 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 23 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 0 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | TER QUINTERO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 8 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 9 | TER QUINTERO U1 | 75% | 100% | 75% | 75% | SI
2020-10-27 | 10 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 11 | TER QUINTERO U1 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 12 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 13 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 14 | TER QUINTERO U1 | 75% | 100% | 75% | 75% | SI
2020-10-27 | 15 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 16 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 17 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 18 | TER QUINTERO U1 | 33% | 100% | 33% | 0% | SI
2020-10-27 | 19 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 20 | TER QUINTERO U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 21 | TER QUINTERO U1 | 33% | 100% | 33% | 0% | SI
2020-10-27 | 22 | TER QUINTERO U1 | 75% | 100% | 75% | 75% | SI
2020-10-27 | 23 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | TER QUINTERO U2 | 60% | 100% | 60% | 0% | SI
2020-10-27 | 17 | TER QUINTERO U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 18 | TER QUINTERO U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 19 | TER QUINTERO U2 | 100% | 100% | 100% | 100% | SI
2020-10-27 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | TER TALTAL U1 | 40% | 100% | 40% | 0% | SI
2020-10-27 | 2 | TER TALTAL U1 | 17% | 100% | 17% | 0% | SI
2020-10-27 | 3 | TER TALTAL U1 | 50% | 100% | 50% | 0% | SI
2020-10-27 | 4 | TER TALTAL U1 | 67% | 100% | 67% | 0% | SI
2020-10-27 | 5 | TER TALTAL U1 | 34% | 100% | 34% | 0% | SI
2020-10-27 | 6 | TER TALTAL U1 | 83% | 100% | 83% | 83% | SI
2020-10-27 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | TER TALTAL U2 | No Participó | 63.33% | 63.33% | 0% | SI
2020-10-27 | 6 | TER TALTAL U2 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 7 | TER TALTAL U2 | No Participó | 50% | 50% | 0% | SI
2020-10-27 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-27 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-27 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0% | SI
2020-10-27 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 65% | 65% | 0% | SI
2020-10-27 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 18 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-27 | 19 | TER TOCOPILLA U16-TG-TV | 0% | 100% | 0% | 0% | SI
2020-10-27 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-27 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 10 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 11 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 12 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 13 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 14 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 22 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | HE ANGOSTURA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 15 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 22 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 3 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 10 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 11 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 15 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 3 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 10 | HE CANUTILLAR U2 | 67% | 100% | 67% | 0% | SI
2020-10-28 | 11 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 14 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 15 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 10 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 20 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 21 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 22 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 23 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 10 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 20 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 21 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 2 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | HE COLBÚN U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 1 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 2 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 3 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 4 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 5 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 6 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 7 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 8 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 9 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 10 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 11 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 12 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 13 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 14 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 15 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 16 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 17 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 18 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 19 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 20 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 21 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 22 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 23 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-28 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 0 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 1 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 2 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 3 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 4 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 5 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 6 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 7 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 8 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 9 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 10 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 11 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 12 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 13 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 14 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 15 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 16 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 17 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 18 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 19 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 20 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 21 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 22 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 23 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 2 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 3 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 4 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 5 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 6 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 7 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 8 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 9 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 10 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 11 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 12 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 13 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 14 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 15 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 16 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 17 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 18 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 22 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 23 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 0 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 1 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 2 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 3 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 4 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 5 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 6 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 7 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 8 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 9 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 10 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 11 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 12 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 13 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 14 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 15 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 16 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 17 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 18 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 19 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 20 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 21 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 22 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 23 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 0 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 1 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 2 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 3 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 4 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 5 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 6 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 7 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 8 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 9 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 10 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 11 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 12 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 13 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 14 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 15 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 17 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 18 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 19 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 20 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 21 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 22 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 23 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 1 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 2 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 3 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 4 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 5 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 6 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 7 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 8 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 9 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 10 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 11 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 1 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 2 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 3 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 4 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 5 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 6 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 7 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 8 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 9 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 10 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 11 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 12 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 13 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 14 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 15 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 16 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 20 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 0 | TER ANGAMOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 1 | TER ANGAMOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 2 | TER ANGAMOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 3 | TER ANGAMOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 4 | TER ANGAMOS U1 | No Participó | 58.33% | 58.33% | 0% | SI
2020-10-28 | 5 | TER ANGAMOS U1 | 80% | 100% | 80% | 80% | SI
2020-10-28 | 6 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 7 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 8 | TER ANGAMOS U1 | 66% | 100% | 66% | 0% | SI
2020-10-28 | 9 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 10 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 11 | TER ANGAMOS U1 | 66% | 100% | 66% | 0% | SI
2020-10-28 | 12 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-28 | 13 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 14 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-28 | 15 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-28 | 16 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-28 | 17 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 18 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 19 | TER ANGAMOS U1 | 60% | 100% | 60% | 0% | SI
2020-10-28 | 20 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 21 | TER ANGAMOS U1 | 66% | 100% | 66% | 0% | SI
2020-10-28 | 22 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 23 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 0 | TER COCHRANE U2 | 20% | 100% | 20% | 0% | SI
2020-10-28 | 1 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-28 | 2 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-28 | 3 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 4 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 5 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 6 | TER COCHRANE U2 | 50% | 100% | 50% | 0% | SI
2020-10-28 | 7 | TER COCHRANE U2 | 25% | 100% | 25% | 0% | SI
2020-10-28 | 8 | TER COCHRANE U2 | 25% | 100% | 25% | 0% | SI
2020-10-28 | 9 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-28 | 15 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 16 | TER COCHRANE U2 | 33% | 100% | 33% | 0% | SI
2020-10-28 | 17 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-28 | 18 | TER COCHRANE U2 | 75% | 100% | 75% | 75% | SI
2020-10-28 | 19 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 20 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 21 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 22 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 23 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 0 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 1 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 2 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 3 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 4 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 5 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 6 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 7 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 8 | TER HORNITOS U1 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 9 | TER HORNITOS U1 | No Participó | 98.33% | 98.33% | 100% | SI
2020-10-28 | 10 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 11 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 12 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 0 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | TER NORGENER U1 | 75% | 100% | 75% | 75% | SI
2020-10-28 | 1 | TER NORGENER U1 | 40% | 100% | 40% | 0% | SI
2020-10-28 | 2 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-28 | 3 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-28 | 4 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-28 | 5 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 6 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-28 | 7 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-28 | 8 | TER NORGENER U1 | 0% | 100% | 0% | 0% | SI
2020-10-28 | 9 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-28 | 19 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-28 | 20 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-28 | 21 | TER NORGENER U1 | 66% | 100% | 66% | 0% | SI
2020-10-28 | 22 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-28 | 23 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-28 | 0 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-28 | 1 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-28 | 2 | TER NORGENER U2 | 0% | 100% | 0% | 0% | SI
2020-10-28 | 3 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-28 | 4 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-28 | 5 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-28 | 6 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-28 | 7 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-28 | 8 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-28 | 9 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 10 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-28 | 11 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 12 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 13 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-28 | 14 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-28 | 15 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-28 | 16 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 17 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-28 | 18 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-28 | 19 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-28 | 20 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-28 | 21 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-28 | 22 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-28 | 23 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-28 | 0 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 1 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 2 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 3 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 4 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 5 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 6 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 7 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 8 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 9 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 10 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 11 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 12 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 13 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 14 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 15 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 16 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 17 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 18 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 19 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 20 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 21 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 22 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 23 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 18 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 19 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 20 | TER QUINTERO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | TER TALTAL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-28 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-28 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-28 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 0 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 1 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 2 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 3 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 4 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-28 | 21 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 22 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-28 | 23 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 2 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 15 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 20 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 21 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 22 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 7 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 17 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 0 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 1 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 5 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 16 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 19 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 21 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 22 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 23 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 9 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 10 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 16 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 22 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 23 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 10 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 14 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 15 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 20 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 21 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 19 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 20 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 21 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 22 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 23 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 10 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE CIPRESES U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 20 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 21 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE COLBÚN U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 22 | HE COLBÚN U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 23 | HE COLBÚN U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 1 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 2 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 3 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 4 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 5 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 6 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 7 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 8 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 9 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 10 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 11 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 12 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 13 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 14 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 15 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 16 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 17 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 18 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 19 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 20 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 21 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 22 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 23 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-29 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 0 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 1 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 2 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 3 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 4 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 5 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 6 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 7 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 8 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 9 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 10 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 11 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 12 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 13 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 14 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 15 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 16 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 17 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 18 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 19 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 20 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 21 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 22 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 23 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 7 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 8 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 9 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 10 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 11 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 12 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 13 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 14 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 15 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 16 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 17 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 18 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 19 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 23 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 0 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 1 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 2 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 3 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 4 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 5 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 6 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 7 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 8 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 9 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 10 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 11 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 12 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 13 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 14 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 15 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 16 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 17 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 18 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 19 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 20 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 21 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 22 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 23 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 0 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 1 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 2 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 3 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 4 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 5 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 6 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 7 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 8 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 9 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 10 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 11 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 12 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 13 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 14 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 15 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 17 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 18 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 19 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 20 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 21 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 22 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 23 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 11 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 12 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 13 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 14 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 15 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 16 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 17 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 18 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 19 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 23 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 21 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 22 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 23 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 0 | TER ANGAMOS U1 | 80% | 100% | 80% | 80% | SI
2020-10-29 | 1 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-29 | 2 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-29 | 3 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 4 | TER ANGAMOS U1 | 33% | 100% | 33% | 0% | SI
2020-10-29 | 5 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-29 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | TER ANGAMOS U1 | 0% | 100% | 0% | 0% | SI
2020-10-29 | 9 | TER ANGAMOS U1 | 17% | 100% | 17% | 0% | SI
2020-10-29 | 10 | TER ANGAMOS U1 | 17% | 100% | 17% | 0% | SI
2020-10-29 | 11 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-29 | 12 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 13 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-29 | 14 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 15 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-29 | 16 | TER ANGAMOS U1 | 17% | 100% | 17% | 0% | SI
2020-10-29 | 17 | TER ANGAMOS U1 | 17% | 100% | 17% | 0% | SI
2020-10-29 | 18 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 19 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 20 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 21 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 0 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 1 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 2 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 3 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 4 | TER COCHRANE U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 5 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 6 | TER COCHRANE U2 | 60% | 100% | 60% | 0% | SI
2020-10-29 | 7 | TER COCHRANE U2 | 66% | 100% | 66% | 0% | SI
2020-10-29 | 8 | TER COCHRANE U2 | 0% | 100% | 0% | 0% | SI
2020-10-29 | 9 | TER COCHRANE U2 | 0% | 100% | 0% | 0% | SI
2020-10-29 | 10 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 16 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-29 | 17 | TER COCHRANE U2 | 40% | 100% | 40% | 0% | SI
2020-10-29 | 18 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 19 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 20 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 21 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 22 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 23 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 9 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 11 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 12 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 0 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER NORGENER U1 | 60% | 100% | 60% | 0% | SI
2020-10-29 | 1 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 2 | TER NORGENER U1 | 80% | 100% | 80% | 80% | SI
2020-10-29 | 3 | TER NORGENER U1 | 0% | 100% | 0% | 0% | SI
2020-10-29 | 4 | TER NORGENER U1 | 80% | 100% | 80% | 80% | SI
2020-10-29 | 5 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-29 | 6 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-29 | 7 | TER NORGENER U1 | 0% | 100% | 0% | 0% | SI
2020-10-29 | 8 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 16 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 18 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-29 | 19 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-29 | 20 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 21 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 22 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 23 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 0 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-29 | 1 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 2 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-29 | 3 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-29 | 4 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-29 | 5 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-29 | 6 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 7 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-29 | 8 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-29 | 9 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-29 | 10 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | TER NORGENER U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | TER NORGENER U2 | 20% | 100% | 20% | 0% | SI
2020-10-29 | 13 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 15 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 16 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-29 | 17 | TER NORGENER U2 | 80% | 100% | 80% | 80% | SI
2020-10-29 | 18 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-29 | 19 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-29 | 20 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-29 | 21 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-29 | 22 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 23 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-29 | 0 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 1 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 2 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 3 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 4 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 5 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 6 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 7 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 8 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 9 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 10 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 11 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 12 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 13 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 14 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 15 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 16 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 17 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 18 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 19 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 20 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 21 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 22 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 23 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-29 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-29 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0% | SI
2020-10-29 | 6 | TER TOCOPILLA U14 | No Participó | 30% | 30% | 0% | SI
2020-10-29 | 7 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 0 | TER TOCOPILLA U16-TG-TV | 0% | 100% | 0% | 0% | SI
2020-10-29 | 1 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 2 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 3 | TER TOCOPILLA U16-TG-TV | 67% | 100% | 67% | 0% | SI
2020-10-29 | 4 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 5 | TER TOCOPILLA U16-TG-TV | 66% | 100% | 66% | 0% | SI
2020-10-29 | 6 | TER TOCOPILLA U16-TG-TV | 0% | 100% | 0% | 0% | SI
2020-10-29 | 7 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 8 | TER TOCOPILLA U16-TG-TV | 100% | 100% | 100% | 100% | SI
2020-10-29 | 9 | TER TOCOPILLA U16-TG-TV | 83% | 100% | 83% | 83% | SI
2020-10-29 | 10 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 11 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 12 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 13 | TER TOCOPILLA U16-TG-TV | 66% | 100% | 66% | 0% | SI
2020-10-29 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 100% | 100% | 100% | SI
2020-10-29 | 19 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 20 | TER TOCOPILLA U16-TG-TV | 100% | 100% | 100% | 100% | SI
2020-10-29 | 21 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 22 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-29 | 23 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 1 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 2 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | HE ANGOSTURA U2 | 80% | 100% | 80% | 80% | SI
2020-10-30 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 11 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 12 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 13 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 14 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 20 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 21 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 22 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 23 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 0 | HE ANGOSTURA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | HE ANGOSTURA U3 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 23 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 1 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 2 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 3 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 11 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 12 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 15 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 21 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 0 | HE CANUTILLAR U2 | 80% | 100% | 80% | 80% | SI
2020-10-30 | 1 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 2 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 3 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 4 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 6 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 7 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 11 | HE CANUTILLAR U2 | 67% | 100% | 67% | 0% | SI
2020-10-30 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 13 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 15 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 22 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 0 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 1 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 2 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 3 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 4 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 5 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 6 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 7 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 8 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 9 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 10 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 11 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 12 | HE CIPRESES U1 | No Verificable | 81.67% | 0% | 0% | SI
2020-10-30 | 13 | HE CIPRESES U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 14 | HE CIPRESES U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 15 | HE CIPRESES U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 16 | HE CIPRESES U1 | No Verificable | 20% | 0% | 0% | SI
2020-10-30 | 17 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 18 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 19 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 20 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 21 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 22 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 23 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 0 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 1 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 2 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 3 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 4 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 5 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 6 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 7 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 8 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 9 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 10 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 11 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 12 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 13 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 14 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 15 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 16 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 17 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 18 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 19 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 20 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 21 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 22 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 23 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 0 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 2 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 3 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 4 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 5 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 6 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 7 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 8 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 9 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 10 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 11 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 12 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 13 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 14 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 15 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 16 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 17 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 18 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 19 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 20 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 21 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 22 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 23 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 20 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 1 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 20 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 1 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 2 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 3 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 4 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 5 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 6 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 7 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 8 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 9 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 10 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 11 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 12 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 13 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 14 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 15 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 16 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 17 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 18 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 19 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 20 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 21 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 22 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 23 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-30 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 0 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 1 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 2 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 3 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 4 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 5 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 6 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 7 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 8 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 9 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 10 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 11 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 12 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 13 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 14 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 15 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 16 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 17 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 18 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 19 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 20 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 21 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 22 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 23 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 0 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 3 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 4 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 10 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 11 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 14 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 15 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 16 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 17 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 1 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 2 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 3 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 4 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 5 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 6 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 7 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 8 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 9 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 10 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 11 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 12 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 13 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 14 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 15 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 16 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 17 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 18 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 19 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 20 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 21 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 22 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 23 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 0 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 1 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 2 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 3 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 4 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 5 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 6 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 7 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 8 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 9 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 10 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 11 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 12 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 13 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 14 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 15 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 16 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 17 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 18 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 19 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 20 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 21 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 22 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 23 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 12 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 21 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 22 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 2 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 3 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 4 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 5 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 6 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 7 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 8 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 9 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 20 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 21 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 22 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 23 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 23 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 0 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 1 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 2 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-30 | 3 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 4 | TER ANGAMOS U1 | 33% | 100% | 33% | 0% | SI
2020-10-30 | 5 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 6 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 7 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-30 | 8 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-30 | 9 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-30 | 10 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-30 | 11 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-30 | 12 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 13 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-30 | 14 | TER ANGAMOS U1 | 33% | 100% | 33% | 0% | SI
2020-10-30 | 15 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-30 | 16 | TER ANGAMOS U1 | 25% | 100% | 25% | 0% | SI
2020-10-30 | 17 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 18 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 19 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 20 | TER ANGAMOS U1 | 66% | 100% | 66% | 0% | SI
2020-10-30 | 21 | TER ANGAMOS U1 | 17% | 100% | 17% | 0% | SI
2020-10-30 | 22 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-30 | 23 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 0 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 1 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 2 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 3 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 4 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 5 | TER COCHRANE U2 | 75% | 100% | 75% | 75% | SI
2020-10-30 | 6 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 7 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-30 | 8 | TER COCHRANE U2 | 75% | 100% | 75% | 75% | SI
2020-10-30 | 9 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 10 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 11 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 12 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 13 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 14 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 15 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-30 | 16 | TER COCHRANE U2 | 66% | 100% | 66% | 0% | SI
2020-10-30 | 17 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-30 | 18 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-30 | 19 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 20 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 21 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-30 | 23 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 0 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 8 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 9 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 10 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 11 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 18 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 23 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-30 | 0 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | TER NORGENER U1 | 80% | 100% | 80% | 80% | SI
2020-10-30 | 1 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 2 | TER NORGENER U1 | 60% | 100% | 60% | 0% | SI
2020-10-30 | 3 | TER NORGENER U1 | 80% | 100% | 80% | 80% | SI
2020-10-30 | 4 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 5 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-30 | 6 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-30 | 7 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 8 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 9 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 10 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 15 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 18 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 19 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-30 | 20 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-30 | 21 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-30 | 22 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 23 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-30 | 0 | TER NORGENER U2 | 80% | 100% | 80% | 80% | SI
2020-10-30 | 1 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 2 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-30 | 3 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-30 | 4 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-30 | 5 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-30 | 6 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-30 | 7 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-30 | 8 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-30 | 9 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-30 | 10 | TER NORGENER U2 | 51% | 100% | 51% | 0% | SI
2020-10-30 | 11 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-30 | 12 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-30 | 13 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-30 | 14 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 15 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-30 | 16 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-30 | 17 | TER NORGENER U2 | 51% | 100% | 51% | 0% | SI
2020-10-30 | 18 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-30 | 19 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-30 | 20 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-30 | 21 | TER NORGENER U2 | 67% | 100% | 67% | 0% | SI
2020-10-30 | 22 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-30 | 23 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 0 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 1 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 2 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 3 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 4 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 5 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 6 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 7 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 8 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 9 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 10 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 11 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 12 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 13 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 14 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 15 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 16 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 17 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 18 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 19 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 20 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 21 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 22 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 23 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-30 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 23 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-30 | 0 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-30 | 0 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 1 | TER TOCOPILLA U16-TG-TV | 83% | 100% | 83% | 83% | SI
2020-10-30 | 2 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 3 | TER TOCOPILLA U16-TG-TV | 66% | 100% | 66% | 0% | SI
2020-10-30 | 4 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 5 | TER TOCOPILLA U16-TG-TV | 75% | 100% | 75% | 75% | SI
2020-10-30 | 6 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 7 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 8 | TER TOCOPILLA U16-TG-TV | 50% | 100% | 50% | 0% | SI
2020-10-30 | 9 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 10 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 11 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 12 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 13 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 14 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 15 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 16 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 17 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 18 | TER TOCOPILLA U16-TG-TV | 75% | 100% | 75% | 75% | SI
2020-10-30 | 19 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 20 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 21 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 22 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-30 | 23 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 0 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE ANGOSTURA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 2 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 3 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 7 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 11 | HE ANGOSTURA U2 | 80% | 100% | 80% | 80% | SI
2020-10-31 | 12 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 13 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 14 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 15 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE ANGOSTURA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE ANGOSTURA U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 21 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 22 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 23 | HE ANGOSTURA U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 0 | HE ANGOSTURA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 1 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE ANGOSTURA U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 7 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE ANGOSTURA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE ANTUCO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 1 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 2 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 3 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 4 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 5 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 6 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 7 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 8 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 9 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 10 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 11 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 12 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 13 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 14 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 15 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 16 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 17 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 18 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 19 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 20 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 21 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 22 | HE ANTUCO U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 23 | HE ANTUCO U2 | No Participó | 1.667% | 1.667% | 0% | SI
2020-10-31 | 0 | HE CANUTILLAR U1 | 80% | 100% | 80% | 80% | SI
2020-10-31 | 1 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 2 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE CANUTILLAR U1 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 5 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 9 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 10 | HE CANUTILLAR U1 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 13 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 14 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 15 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE CANUTILLAR U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 3 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 4 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 10 | HE CANUTILLAR U2 | 33% | 100% | 33% | 0% | SI
2020-10-31 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 14 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 15 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 21 | HE CANUTILLAR U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE CANUTILLAR U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 0 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 2 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 3 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 5 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 7 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE CIPRESES U1 | 60% | 100% | 60% | 0% | SI
2020-10-31 | 10 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 11 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE CIPRESES U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE CIPRESES U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 17 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE CIPRESES U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE CIPRESES U2 | 20% | 100% | 20% | 0% | SI
2020-10-31 | 1 | HE CIPRESES U2 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 2 | HE CIPRESES U2 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 3 | HE CIPRESES U2 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 4 | HE CIPRESES U2 | 17% | 100% | 17% | 0% | SI
2020-10-31 | 5 | HE CIPRESES U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 6 | HE CIPRESES U2 | 0% | 100% | 0% | 0% | SI
2020-10-31 | 7 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 8 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 9 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 10 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 11 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 12 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 13 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 14 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 15 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 16 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 17 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 18 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 19 | HE CIPRESES U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 20 | HE CIPRESES U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE CIPRESES U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE CIPRESES U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE CIPRESES U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE CIPRESES U3 | 80% | 100% | 80% | 80% | SI
2020-10-31 | 1 | HE CIPRESES U3 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 2 | HE CIPRESES U3 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 3 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE CIPRESES U3 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 5 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 7 | HE CIPRESES U3 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 8 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 10 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 11 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE CIPRESES U3 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 14 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE CIPRESES U3 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 20 | HE CIPRESES U3 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE CIPRESES U3 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 22 | HE CIPRESES U3 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 23 | HE CIPRESES U3 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE COLBÚN U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE COLBÚN U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 9 | HE COLBÚN U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 10 | HE COLBÚN U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 11 | HE COLBÚN U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE COLBÚN U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 1 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 2 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 3 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 4 | HE PANGUE U1 | 80% | 0% | 0% | 0% | SI
2020-10-31 | 5 | HE PANGUE U1 | No Verificable | 0% | 0% | 0% | SI
2020-10-31 | 6 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 7 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 8 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 9 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 10 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 11 | HE PANGUE U1 | 83% | 0% | 0% | 0% | SI
2020-10-31 | 12 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 13 | HE PANGUE U1 | 75% | 0% | 0% | 0% | SI
2020-10-31 | 14 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 15 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 16 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 17 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 18 | HE PANGUE U1 | 75% | 0% | 0% | 0% | SI
2020-10-31 | 19 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 20 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 21 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 22 | HE PANGUE U1 | 100% | 0% | 0% | 0% | SI
2020-10-31 | 23 | HE PANGUE U1 | 100% | 1.667% | 1.667% | 0% | SI
2020-10-31 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 23 | HE PANGUE U2 | No Participó | 1.667% | 1.667% | 0% | SI
2020-10-31 | 0 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 2 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 3 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 4 | HE PEHUENCHE U1 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 5 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 7 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 10 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 11 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 12 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 13 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 14 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 15 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 16 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 17 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 20 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 21 | HE PEHUENCHE U1 | 33% | 100% | 33% | 0% | SI
2020-10-31 | 22 | HE PEHUENCHE U1 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 23 | HE PEHUENCHE U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 0 | HE PEHUENCHE U2 | 60% | 100% | 60% | 0% | SI
2020-10-31 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 3 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 4 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 10 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 11 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE PEHUENCHE U2 | 60% | 100% | 60% | 0% | SI
2020-10-31 | 14 | HE PEHUENCHE U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 15 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 16 | HE PEHUENCHE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 17 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE RALCO U1 | 80% | 100% | 80% | 80% | SI
2020-10-31 | 1 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 2 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 3 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 5 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE RALCO U1 | 50% | 100% | 50% | 0% | SI
2020-10-31 | 7 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE RALCO U1 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 9 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 10 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 11 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 14 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE RALCO U1 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 19 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE RALCO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 23 | HE RALCO U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 2 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 3 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 5 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 7 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 9 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 10 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 11 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 12 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE RALCO U2 | 50% | 100% | 50% | 0% | SI
2020-10-31 | 14 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 16 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 18 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 19 | HE RALCO U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE RALCO U2 | 80% | 100% | 80% | 80% | SI
2020-10-31 | 21 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 22 | HE RALCO U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 23 | HE RALCO U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 12 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE RAPEL U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE RAPEL U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 2 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 3 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 4 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 5 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 6 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 7 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 8 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 9 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE RAPEL U4 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 20 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE RAPEL U4 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 1 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 2 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 3 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 4 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 5 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 6 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 7 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 8 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 9 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 10 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 11 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 12 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 13 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 14 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 15 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 16 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 17 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 18 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 19 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 20 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 21 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 22 | TER ANDINA U1 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 23 | TER ANDINA U1 | No Participó | 1.667% | 1.667% | 0% | SI
2020-10-31 | 0 | TER ANGAMOS U1 | 60% | 100% | 60% | 0% | SI
2020-10-31 | 1 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 2 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 3 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 4 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 5 | TER ANGAMOS U1 | 40% | 100% | 40% | 0% | SI
2020-10-31 | 6 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-31 | 7 | TER ANGAMOS U1 | 60% | 100% | 60% | 0% | SI
2020-10-31 | 8 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 9 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 10 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-31 | 11 | TER ANGAMOS U1 | 40% | 100% | 40% | 0% | SI
2020-10-31 | 12 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 13 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-31 | 14 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 15 | TER ANGAMOS U1 | 33% | 100% | 33% | 0% | SI
2020-10-31 | 16 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 17 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 18 | TER ANGAMOS U1 | 66% | 100% | 66% | 0% | SI
2020-10-31 | 19 | TER ANGAMOS U1 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 20 | TER ANGAMOS U1 | 50% | 100% | 50% | 0% | SI
2020-10-31 | 21 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 22 | TER ANGAMOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 23 | TER ANGAMOS U1 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 0 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 1 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 2 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 3 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 4 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 5 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 6 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 7 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 8 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 9 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 10 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 11 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 12 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 13 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 14 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 15 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 16 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 17 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 18 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 19 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 20 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 21 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 22 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 23 | TER ANGAMOS U2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 0 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 1 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 2 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 3 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 4 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 5 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 6 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 7 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 8 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 9 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 10 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 11 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 12 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 13 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 14 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 15 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 16 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 17 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 18 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 19 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 20 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 21 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 22 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 23 | TER ATACAMA CC1-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 0 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 1 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 2 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 3 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 4 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 5 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 6 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 7 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 8 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 9 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 10 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 11 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 12 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 13 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 14 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 15 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 16 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 17 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 18 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 19 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 20 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 21 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 22 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 23 | TER ATACAMA CC1-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 0 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 1 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 2 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 3 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 4 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 5 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 6 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 7 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 8 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 9 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 10 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 11 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 12 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 13 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 14 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 15 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 16 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 17 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 18 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 19 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 20 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 21 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 22 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 23 | TER ATACAMA CC2-TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 0 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 1 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 2 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 3 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 4 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 5 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 6 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 7 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 8 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 9 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 10 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 11 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 12 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 13 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 14 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 15 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 16 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 17 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 18 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 19 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 20 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 21 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 22 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 23 | TER ATACAMA CC2-TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 1 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 2 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 3 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 4 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 5 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 6 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 7 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 8 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 9 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 10 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 11 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 12 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 13 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 14 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 15 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 16 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 17 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 18 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 19 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 20 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 21 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 22 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 23 | TER COCHRANE U1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 0 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-31 | 1 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 2 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 3 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 4 | TER COCHRANE U2 | 60% | 100% | 60% | 0% | SI
2020-10-31 | 5 | TER COCHRANE U2 | 75% | 100% | 75% | 75% | SI
2020-10-31 | 6 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 7 | TER COCHRANE U2 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 8 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 9 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 10 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 11 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 12 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 13 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 14 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 15 | TER COCHRANE U2 | 80% | 100% | 80% | 80% | SI
2020-10-31 | 16 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 17 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 18 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 19 | TER COCHRANE U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 20 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 21 | TER COCHRANE U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 23 | TER COCHRANE U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 0 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 8 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 9 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 10 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 11 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 18 | TER HORNITOS U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 19 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | TER HORNITOS U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | TER IEM U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | TER MEJILLONES CTM1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 1 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 2 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 3 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 4 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 5 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 6 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 7 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 8 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 9 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 10 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 11 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 12 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 13 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 14 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 15 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 16 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 17 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 18 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 19 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 20 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 21 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 22 | TER MEJILLONES CTM2 | No Participó | 0% | 0% | 0% | SI
2020-10-31 | 23 | TER MEJILLONES CTM2 | No Participó | 1.667% | 1.667% | 0% | SI
2020-10-31 | 0 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | TER NORGENER U1 | 20% | 100% | 20% | 0% | SI
2020-10-31 | 1 | TER NORGENER U1 | 50% | 100% | 50% | 0% | SI
2020-10-31 | 2 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 3 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 4 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-31 | 5 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 6 | TER NORGENER U1 | 17% | 100% | 17% | 0% | SI
2020-10-31 | 7 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 8 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 9 | TER NORGENER U1 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 10 | TER NORGENER U1 | 51% | 100% | 51% | 0% | SI
2020-10-31 | 11 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 12 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 13 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 14 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 15 | TER NORGENER U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 16 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 17 | TER NORGENER U1 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 18 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 19 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-31 | 20 | TER NORGENER U1 | 75% | 100% | 75% | 75% | SI
2020-10-31 | 21 | TER NORGENER U1 | 80% | 100% | 80% | 80% | SI
2020-10-31 | 22 | TER NORGENER U1 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 23 | TER NORGENER U1 | 33% | 100% | 33% | 0% | SI
2020-10-31 | 0 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-31 | 1 | TER NORGENER U2 | 25% | 100% | 25% | 0% | SI
2020-10-31 | 2 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 3 | TER NORGENER U2 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 4 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-31 | 5 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 6 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-31 | 7 | TER NORGENER U2 | 66% | 100% | 66% | 0% | SI
2020-10-31 | 8 | TER NORGENER U2 | 60% | 100% | 60% | 0% | SI
2020-10-31 | 9 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-31 | 10 | TER NORGENER U2 | 80% | 100% | 80% | 80% | SI
2020-10-31 | 11 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 12 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 13 | TER NORGENER U2 | 75% | 100% | 75% | 75% | SI
2020-10-31 | 14 | TER NORGENER U2 | 40% | 100% | 40% | 0% | SI
2020-10-31 | 15 | TER NORGENER U2 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 16 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-31 | 17 | TER NORGENER U2 | 100% | 100% | 100% | 100% | SI
2020-10-31 | 18 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-31 | 19 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-31 | 20 | TER NORGENER U2 | 17% | 100% | 17% | 0% | SI
2020-10-31 | 21 | TER NORGENER U2 | 33% | 100% | 33% | 0% | SI
2020-10-31 | 22 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-31 | 23 | TER NORGENER U2 | 50% | 100% | 50% | 0% | SI
2020-10-31 | 0 | TER QUINTERO U1 | 0% | 100% | 0% | 0% | SI
2020-10-31 | 1 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 2 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 3 | TER QUINTERO U1 | 80% | 100% | 80% | 80% | SI
2020-10-31 | 4 | TER QUINTERO U1 | 66% | 100% | 66% | 0% | SI
2020-10-31 | 5 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 6 | TER QUINTERO U1 | 17% | 100% | 17% | 0% | SI
2020-10-31 | 7 | TER QUINTERO U1 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 8 | TER QUINTERO U1 | 25% | 100% | 25% | 0% | SI
2020-10-31 | 9 | TER QUINTERO U1 | 67% | 100% | 67% | 0% | SI
2020-10-31 | 10 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-31 | 11 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-31 | 12 | TER QUINTERO U1 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 13 | TER QUINTERO U1 | 83% | 100% | 83% | 83% | SI
2020-10-31 | 14 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 15 | TER QUINTERO U1 | 75% | 100% | 75% | 75% | SI
2020-10-31 | 16 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-31 | 17 | TER QUINTERO U1 | 50% | 100% | 50% | 0% | SI
2020-10-31 | 18 | TER QUINTERO U1 | 66% | 100% | 66% | 0% | SI
2020-10-31 | 19 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 20 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 21 | TER QUINTERO U1 | 40% | 100% | 40% | 0% | SI
2020-10-31 | 22 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 23 | TER QUINTERO U1 | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 0 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | TER QUINTERO U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | TER TALTAL U1 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | TER TALTAL U2 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 1 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 2 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 3 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 4 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 5 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 6 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 7 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 8 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 9 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 10 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 11 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 12 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 13 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 14 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 15 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 16 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 17 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 18 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 19 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 20 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 21 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 22 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 23 | TER TARAPACÁ TGTAR | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 0 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 1 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 2 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 3 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 4 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 5 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 6 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 7 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 8 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 9 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 10 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 11 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 12 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 13 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 14 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 15 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 16 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 17 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 18 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 19 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 20 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 21 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 22 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 23 | TER TOCOPILLA TG1 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 0 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 1 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 2 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 3 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 4 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 5 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 6 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 7 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 8 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 9 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 10 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 11 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 12 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 13 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 14 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 15 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 16 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 17 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 18 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 19 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 20 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 21 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 22 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 23 | TER TOCOPILLA TG2 | No Verificable | 100% | 0% | 0% | NO
2020-10-31 | 0 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 1 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 2 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 3 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 4 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 5 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 6 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 7 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 8 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 9 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 10 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 11 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 12 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 13 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 14 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 15 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 16 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 17 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 18 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 19 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 20 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 21 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 22 | TER TOCOPILLA TG3 | No Verificable | 0% | 0% | 0% | NO
2020-10-31 | 23 | TER TOCOPILLA TG3 | No Verificable | 1.667% | 0% | 0% | NO
2020-10-31 | 0 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | TER TOCOPILLA U14 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 1 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 2 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 3 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 4 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 5 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 6 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 7 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 8 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 9 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 10 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 11 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 12 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 13 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 14 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 15 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 16 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 17 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 18 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 19 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 20 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 21 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 22 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 23 | TER TOCOPILLA U15 | No Participó | 100% | 100% | 100% | SI
2020-10-31 | 0 | TER TOCOPILLA U16-TG-TV | 40% | 100% | 40% | 0% | SI
2020-10-31 | 1 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 2 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 3 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 4 | TER TOCOPILLA U16-TG-TV | 0% | 100% | 0% | 0% | SI
2020-10-31 | 5 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 6 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 7 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 8 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 9 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 10 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 11 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 12 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 13 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 14 | TER TOCOPILLA U16-TG-TV | 0% | 100% | 0% | 0% | SI
2020-10-31 | 15 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 16 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 17 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 18 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 19 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 20 | TER TOCOPILLA U16-TG-TV | 75% | 100% | 75% | 75% | SI
2020-10-31 | 21 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI
2020-10-31 | 22 | TER TOCOPILLA U16-TG-TV | 66% | 100% | 66% | 0% | SI
2020-10-31 | 23 | TER TOCOPILLA U16-TG-TV | No Verificable | 100% | 0% | 0% | SI

## CSF Mensual
Desempeño Control Secundario de Frecuencia SEN
Mes: | 2020-10-01
Unidad | Disponibilidad (Fdis_CSF) | Desempeño (DCSF) | Factor de Desempeño (Fd_CSF)
HE CANUTILLAR U1 | 100% | 99.84% | 100%
HE CANUTILLAR U2 | 100% | 99.95% | 100%
HE CIPRESES U1 | 98.54% | 98.47% | 100%
HE CIPRESES U2 | 99.08% | 99.08% | 100%
HE CIPRESES U3 | 96.51% | 96.32% | 100%
HE COLBÚN U1 | 100% | 99.03% | 100%
HE COLBÚN U2 | 100% | 99.5% | 100%
HE EL TORO U1 | 100% | 100% | 100%
HE EL TORO U2 | 100% | 100% | 100%
HE EL TORO U3 | 100% | 100% | 100%
HE EL TORO U4 | 100% | 100% | 100%
HE PANGUE U1 | 48.33% | 48.33% | 0%
HE PANGUE U2 | 0.00224% | 0.00224% | 0%
HE PEHUENCHE U1 | 100% | 98.86% | 100%
HE PEHUENCHE U2 | 100% | 99.24% | 100%
HE RALCO U1 | 99.09% | 93.52% | 94%
HE RALCO U2 | 98.49% | 93.22% | 93%
HE RAPEL U1 | 95.39% | 95.39% | 100%
HE RAPEL U2 | 99.46% | 99.46% | 100%
HE RAPEL U3 | 99.46% | 99.46% | 100%
HE RAPEL U4 | 99.46% | 99.46% | 100%
HE RAPEL U5 | 99.46% | 99.46% | 100%
PFV LUZ DEL NORTE | 0.00224% | 0.00224% | 0%
TER ANGAMOS U1 | 94.95% | 93.43% | 93%
TER ANGAMOS U2 | 99.54% | 98.7% | 100%
TER ANTILHUE U1 | 100% | 100% | 100%
TER ANTILHUE U2 | 100% | 100% | 100%
TER ATACAMA CC1-TG1 | 100% | 100% | 100%
TER ATACAMA CC1-TG2 | 99.77% | 99.77% | 100%
TER ATACAMA CC1-TV | 100% | 100% | 100%
TER ATACAMA CC2-TG1 | 88.3% | 88.3% | 88%
TER ATACAMA CC2-TG2 | 100% | 100% | 100%
TER ATACAMA CC2-TV | 98.71% | 98.44% | 100%
TER CANDELARIA U1 | 100% | 100% | 100%
TER CANDELARIA U2 | 100% | 100% | 100%
TER COCHRANE U1 | 99.6% | 99.34% | 100%
TER COCHRANE U2 | 97.03% | 96.52% | 100%
TER GUACOLDA U1 | 99.64% | 99.64% | 100%
TER GUACOLDA U2 | 100% | 100% | 100%
TER GUACOLDA U3 | 99.3% | 99.3% | 100%
TER GUACOLDA U4 | 100% | 100% | 100%
TER GUACOLDA U5 | 95.92% | 95.8% | 100%
TER KELAR CC1-TG1 | 98.73% | 98.73% | 100%
TER KELAR CC1-TG2 | 98.87% | 98.87% | 100%
TER KELAR TV | 100% | 99.61% | 100%
TER LOS VIENTOS U1 | 100% | 100% | 100%
TER MEJILLONES CTM3-TG | 96% | 96% | 100%
TER MEJILLONES CTM3-TV | 96.48% | 95.44% | 100%
TER NEHUENCO II CC1-TG | 100% | 100% | 100%
TER NEHUENCO II CC1-TV | 100% | 99.89% | 100%
TER NUEVA RENCA CC1-TG | 0.00224% | 0.00224% | 0%
TER SAN ISIDRO CC1-TG | 100% | 100% | 100%
TER SAN ISIDRO CC1-TV | 100% | 99.97% | 100%
TER SAN ISIDRO II CC1-TG | 100% | 100% | 100%
TER SAN ISIDRO II CC1-TV | 100% | 98.34% | 100%
TER TER NEHUENCO 9B U1 | 100% | 100% | 100%
TER TOCOPILLA TG3 | 0.00224% | 0.00224% | 0%
TER TOCOPILLA U14 | 0.00224% | 0.00224% | 0%
TER TOCOPILLA U16-TG-TV | 0.00224% | 0.00224% | 0%

## CSF Horario
Desempeño Control Secundario de Frecuencia SEN
Mes: | 2020-10-01
Fecha | Hora | Unidad | Respuesta CSF (Fact_CSF) | Disponibilidad (Fdis_CSF) | Desempeño (DCSF) | Factor de Desempeño (Fd_CSF)
2020-10-01 | 0 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 21 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-01 | 0 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 21 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-01 | 0 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 1 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 2 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 3 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 4 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 5 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 6 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 7 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 8 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 9 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 10 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 11 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 12 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 13 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 14 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 15 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 16 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 17 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 18 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 19 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 20 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-01 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 1 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 2 | HE CIPRESES U3 | 99.44% | 100% | 99.44% | 100%
2020-10-01 | 3 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 4 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 5 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 6 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 7 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 8 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 9 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 10 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 11 | HE CIPRESES U3 | 97.78% | 100% | 97.78% | 100%
2020-10-01 | 12 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 13 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 14 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 15 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 16 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 17 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 18 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 19 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 20 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-01 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-01 | 1 | HE COLBÚN U1 | 99.56% | 100% | 99.56% | 100%
2020-10-01 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-01 | 3 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | HE COLBÚN U1 | 97.75% | 100% | 97.75% | 100%
2020-10-01 | 10 | HE COLBÚN U1 | 99.56% | 100% | 99.56% | 100%
2020-10-01 | 11 | HE COLBÚN U1 | 99% | 100% | 99% | 100%
2020-10-01 | 12 | HE COLBÚN U1 | 98.78% | 100% | 98.78% | 100%
2020-10-01 | 13 | HE COLBÚN U1 | 99.67% | 100% | 99.67% | 100%
2020-10-01 | 14 | HE COLBÚN U1 | 99.67% | 100% | 99.67% | 100%
2020-10-01 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-01 | 16 | HE COLBÚN U1 | 98% | 100% | 98% | 100%
2020-10-01 | 17 | HE COLBÚN U1 | 99.32% | 100% | 99.32% | 100%
2020-10-01 | 18 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | HE COLBÚN U1 | 99.28% | 100% | 99.28% | 100%
2020-10-01 | 20 | HE COLBÚN U1 | 99.89% | 100% | 99.89% | 100%
2020-10-01 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-01 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-01 | 23 | HE COLBÚN U1 | 99.89% | 100% | 99.89% | 100%
2020-10-01 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-01 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-01 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-01 | 3 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-01 | 11 | HE COLBÚN U2 | 99.67% | 100% | 99.67% | 100%
2020-10-01 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-01 | 13 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-01 | 14 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-01 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-01 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-01 | 23 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-01 | 0 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 1 | HE PEHUENCHE U1 | 99.67% | 100% | 99.67% | 100%
2020-10-01 | 2 | HE PEHUENCHE U1 | 98.22% | 100% | 98.22% | 100%
2020-10-01 | 3 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 4 | HE PEHUENCHE U1 | 96.44% | 100% | 96.44% | 100%
2020-10-01 | 5 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 6 | HE PEHUENCHE U1 | 88.89% | 100% | 88.89% | 88.89%
2020-10-01 | 7 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 8 | HE PEHUENCHE U1 | 88.44% | 100% | 88.44% | 88.44%
2020-10-01 | 9 | HE PEHUENCHE U1 | 92.67% | 100% | 92.67% | 92.67%
2020-10-01 | 10 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 11 | HE PEHUENCHE U1 | 85.56% | 100% | 85.56% | 85.56%
2020-10-01 | 12 | HE PEHUENCHE U1 | 93.11% | 100% | 93.11% | 93.11%
2020-10-01 | 13 | HE PEHUENCHE U1 | 96.89% | 100% | 96.89% | 100%
2020-10-01 | 14 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 15 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 16 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 17 | HE PEHUENCHE U1 | 99.44% | 100% | 99.44% | 100%
2020-10-01 | 18 | HE PEHUENCHE U1 | 95.78% | 100% | 95.78% | 100%
2020-10-01 | 19 | HE PEHUENCHE U1 | 99.56% | 100% | 99.56% | 100%
2020-10-01 | 20 | HE PEHUENCHE U1 | 96.65% | 100% | 96.65% | 100%
2020-10-01 | 21 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 22 | HE PEHUENCHE U1 | 96% | 100% | 96% | 100%
2020-10-01 | 23 | HE PEHUENCHE U1 | 96.89% | 100% | 96.89% | 100%
2020-10-01 | 0 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 1 | HE PEHUENCHE U2 | 99.67% | 100% | 99.67% | 100%
2020-10-01 | 2 | HE PEHUENCHE U2 | 97.78% | 100% | 97.78% | 100%
2020-10-01 | 3 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 4 | HE PEHUENCHE U2 | 94.11% | 100% | 94.11% | 94.11%
2020-10-01 | 5 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 6 | HE PEHUENCHE U2 | 90.89% | 100% | 90.89% | 90.89%
2020-10-01 | 7 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 8 | HE PEHUENCHE U2 | 87% | 100% | 87% | 87%
2020-10-01 | 9 | HE PEHUENCHE U2 | 92.11% | 100% | 92.11% | 92.11%
2020-10-01 | 10 | HE PEHUENCHE U2 | 98.89% | 100% | 98.89% | 100%
2020-10-01 | 11 | HE PEHUENCHE U2 | 84.78% | 100% | 84.78% | 84.78%
2020-10-01 | 12 | HE PEHUENCHE U2 | 92.78% | 100% | 92.78% | 92.78%
2020-10-01 | 13 | HE PEHUENCHE U2 | 96.78% | 100% | 96.78% | 100%
2020-10-01 | 14 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 15 | HE PEHUENCHE U2 | 95.44% | 100% | 95.44% | 100%
2020-10-01 | 16 | HE PEHUENCHE U2 | 96.22% | 100% | 96.22% | 100%
2020-10-01 | 17 | HE PEHUENCHE U2 | 97.89% | 100% | 97.89% | 100%
2020-10-01 | 18 | HE PEHUENCHE U2 | 92.78% | 100% | 92.78% | 92.78%
2020-10-01 | 19 | HE PEHUENCHE U2 | 99.56% | 100% | 99.56% | 100%
2020-10-01 | 20 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 21 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 22 | HE PEHUENCHE U2 | 94% | 100% | 94% | 94%
2020-10-01 | 23 | HE PEHUENCHE U2 | 95.89% | 100% | 95.89% | 100%
2020-10-01 | 0 | HE RALCO U1 | 100% | 100% | 100% | 100%
2020-10-01 | 1 | HE RALCO U1 | 88.89% | 100% | 88.89% | 88.89%
2020-10-01 | 2 | HE RALCO U1 | 94.56% | 100% | 94.56% | 94.56%
2020-10-01 | 3 | HE RALCO U1 | 92.78% | 100% | 92.78% | 92.78%
2020-10-01 | 4 | HE RALCO U1 | 61.89% | 100% | 61.89% | 0%
2020-10-01 | 5 | HE RALCO U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | HE RALCO U1 | 63.55% | 100% | 63.55% | 0%
2020-10-01 | 7 | HE RALCO U1 | 88% | 100% | 88% | 88%
2020-10-01 | 8 | HE RALCO U1 | 85.22% | 100% | 85.22% | 85.22%
2020-10-01 | 9 | HE RALCO U1 | 82.44% | 100% | 82.44% | 82.44%
2020-10-01 | 10 | HE RALCO U1 | 90.11% | 100% | 90.11% | 90.11%
2020-10-01 | 11 | HE RALCO U1 | 85.44% | 100% | 85.44% | 85.44%
2020-10-01 | 12 | HE RALCO U1 | 87.89% | 100% | 87.89% | 87.89%
2020-10-01 | 13 | HE RALCO U1 | 95.67% | 100% | 95.67% | 100%
2020-10-01 | 14 | HE RALCO U1 | 97.22% | 100% | 97.22% | 100%
2020-10-01 | 15 | HE RALCO U1 | 95.11% | 100% | 95.11% | 100%
2020-10-01 | 16 | HE RALCO U1 | 81.33% | 100% | 81.33% | 81.33%
2020-10-01 | 17 | HE RALCO U1 | 86.45% | 100% | 86.45% | 86.45%
2020-10-01 | 18 | HE RALCO U1 | 95.11% | 100% | 95.11% | 100%
2020-10-01 | 19 | HE RALCO U1 | 97.67% | 100% | 97.67% | 100%
2020-10-01 | 20 | HE RALCO U1 | 96.11% | 100% | 96.11% | 100%
2020-10-01 | 21 | HE RALCO U1 | 94.33% | 100% | 94.33% | 94.33%
2020-10-01 | 22 | HE RALCO U1 | 96.56% | 100% | 96.56% | 100%
2020-10-01 | 23 | HE RALCO U1 | 91.33% | 100% | 91.33% | 91.33%
2020-10-01 | 0 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-01 | 1 | HE RALCO U2 | 98.56% | 100% | 98.56% | 100%
2020-10-01 | 2 | HE RALCO U2 | 99.11% | 100% | 99.11% | 100%
2020-10-01 | 3 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-01 | 4 | HE RALCO U2 | 99.89% | 100% | 99.89% | 100%
2020-10-01 | 5 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-01 | 6 | HE RALCO U2 | 97.67% | 100% | 97.67% | 100%
2020-10-01 | 7 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-01 | 8 | HE RALCO U2 | 89.78% | 100% | 89.78% | 89.78%
2020-10-01 | 9 | HE RALCO U2 | 92.33% | 100% | 92.33% | 92.33%
2020-10-01 | 10 | HE RALCO U2 | 97.67% | 100% | 97.67% | 100%
2020-10-01 | 11 | HE RALCO U2 | 90.11% | 100% | 90.11% | 90.11%
2020-10-01 | 12 | HE RALCO U2 | 96.89% | 100% | 96.89% | 100%
2020-10-01 | 13 | HE RALCO U2 | 97.44% | 100% | 97.44% | 100%
2020-10-01 | 14 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-01 | 15 | HE RALCO U2 | 98.33% | 100% | 98.33% | 100%
2020-10-01 | 16 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-01 | 17 | HE RALCO U2 | 99.44% | 100% | 99.44% | 100%
2020-10-01 | 18 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-01 | 19 | HE RALCO U2 | 99.78% | 100% | 99.78% | 100%
2020-10-01 | 20 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-01 | 21 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-01 | 22 | HE RALCO U2 | 96.89% | 100% | 96.89% | 100%
2020-10-01 | 23 | HE RALCO U2 | 98.78% | 100% | 98.78% | 100%
2020-10-01 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | HE RAPEL U2 | 100% | 100% | 100% | 100%
2020-10-01 | 21 | HE RAPEL U2 | 100% | 100% | 100% | 100%
2020-10-01 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | HE RAPEL U2 | 100% | 100% | 100% | 100%
2020-10-01 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | HE RAPEL U4 | 100% | 100% | 100% | 100%
2020-10-01 | 21 | HE RAPEL U4 | 100% | 100% | 100% | 100%
2020-10-01 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 1 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 2 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 3 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 4 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 5 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 6 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 7 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 8 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 9 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 10 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 11 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 12 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 13 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 14 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 15 | PFV LUZ DEL NORTE | 93.98% | 0% | 0% | 0%
2020-10-01 | 16 | PFV LUZ DEL NORTE | 100% | 0% | 0% | 0%
2020-10-01 | 17 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 18 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 19 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 20 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 21 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 22 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 23 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-01 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-01 | 1 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-01 | 2 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-01 | 3 | TER ANGAMOS U2 | 96.67% | 100% | 96.67% | 100%
2020-10-01 | 4 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-01 | 5 | TER ANGAMOS U2 | 97.67% | 100% | 97.67% | 100%
2020-10-01 | 6 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-01 | 7 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER ANGAMOS U2 | 99.66% | 100% | 99.66% | 100%
2020-10-01 | 9 | TER ANGAMOS U2 | 88.67% | 100% | 88.67% | 88.67%
2020-10-01 | 10 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-01 | 11 | TER ANGAMOS U2 | 97.12% | 100% | 97.12% | 100%
2020-10-01 | 12 | TER ANGAMOS U2 | 99.72% | 100% | 99.72% | 100%
2020-10-01 | 13 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-01 | 14 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-01 | 15 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-01 | 16 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-01 | 17 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-01 | 18 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-01 | 19 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 9 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 10 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 11 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 12 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 13 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 14 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 15 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 16 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 17 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 18 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-01 | 19 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 9 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 10 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 11 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 12 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 13 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 14 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 15 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 16 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 17 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 18 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-01 | 19 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-01 | 1 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-01 | 3 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-01 | 4 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-01 | 5 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-01 | 6 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-01 | 7 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-01 | 8 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-01 | 9 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-01 | 19 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-01 | 20 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-01 | 21 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-01 | 22 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-01 | 23 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-01 | 0 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-01 | 5 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-01 | 6 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-01 | 7 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-01 | 8 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-01 | 20 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-01 | 21 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-01 | 22 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-01 | 23 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-01 | 0 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 1 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 12 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 21 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 22 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 23 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-01 | 0 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-01 | 1 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-01 | 2 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-01 | 3 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-01 | 4 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-01 | 5 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-01 | 6 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-01 | 7 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-01 | 8 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-01 | 9 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-01 | 10 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-01 | 18 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-01 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-01 | 20 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-01 | 21 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-01 | 22 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-01 | 23 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-01 | 0 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-01 | 1 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-01 | 2 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-01 | 3 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-01 | 4 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-01 | 5 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-01 | 6 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-01 | 7 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-01 | 8 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-01 | 9 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER GUACOLDA U5 | 99.77% | 100% | 99.77% | 100%
2020-10-01 | 20 | TER GUACOLDA U5 | 90.89% | 100% | 90.89% | 90.89%
2020-10-01 | 21 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-01 | 22 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-01 | 23 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-01 | 1 | TER MEJILLONES CTM3-TV | 99.63% | 100% | 99.63% | 100%
2020-10-01 | 2 | TER MEJILLONES CTM3-TV | 73.21% | 100% | 73.21% | 0%
2020-10-01 | 3 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER MEJILLONES CTM3-TV | 95.17% | 100% | 95.17% | 100%
2020-10-01 | 18 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-01 | 19 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-01 | 20 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-01 | 21 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-01 | 22 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-01 | 23 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-01 | 0 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 1 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 2 | TER NEHUENCO II CC1-TV | 95.78% | 100% | 95.78% | 100%
2020-10-01 | 3 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 4 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 5 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 6 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 7 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 8 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 9 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 10 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 11 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 12 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 13 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 14 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 15 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 16 | TER NEHUENCO II CC1-TV | 97.56% | 100% | 97.56% | 100%
2020-10-01 | 17 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 18 | TER NEHUENCO II CC1-TV | 99.11% | 100% | 99.11% | 100%
2020-10-01 | 19 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 20 | TER NEHUENCO II CC1-TV | 99.33% | 100% | 99.33% | 100%
2020-10-01 | 21 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 22 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 23 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 0 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 1 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 2 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 3 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 4 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 5 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 6 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 7 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 8 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 9 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 10 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 11 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 12 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 13 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 14 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 15 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 16 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 17 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 18 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 19 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 20 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 21 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 22 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 23 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-01 | 0 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER SAN ISIDRO II CC1-TV | 95.33% | 100% | 95.33% | 100%
2020-10-01 | 1 | TER SAN ISIDRO II CC1-TV | 99.67% | 100% | 99.67% | 100%
2020-10-01 | 2 | TER SAN ISIDRO II CC1-TV | 96.89% | 100% | 96.89% | 100%
2020-10-01 | 3 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 4 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 5 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 6 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 7 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 8 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 9 | TER SAN ISIDRO II CC1-TV | 95% | 100% | 95% | 95%
2020-10-01 | 10 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 11 | TER SAN ISIDRO II CC1-TV | 97.44% | 100% | 97.44% | 100%
2020-10-01 | 12 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 13 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 14 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 15 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 16 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 17 | TER SAN ISIDRO II CC1-TV | 94.78% | 100% | 94.78% | 94.78%
2020-10-01 | 18 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 19 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 20 | TER SAN ISIDRO II CC1-TV | 96.44% | 100% | 96.44% | 100%
2020-10-01 | 21 | TER SAN ISIDRO II CC1-TV | 51.33% | 100% | 51.33% | 0%
2020-10-01 | 22 | TER SAN ISIDRO II CC1-TV | 86.55% | 100% | 86.55% | 86.55%
2020-10-01 | 23 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-01 | 0 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 1 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 2 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 3 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 4 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 5 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 6 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 7 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 8 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 9 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 10 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 11 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 12 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 13 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 14 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 15 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 16 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 17 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 18 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 19 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 20 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 21 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 22 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 23 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-01 | 0 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 1 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 2 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 3 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 4 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 5 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 6 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 7 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 8 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 9 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 10 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 11 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 12 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 13 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 14 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 15 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 16 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 17 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 18 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 19 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 20 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 21 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 22 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 23 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-01 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-01 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-01 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-02 | 21 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-02 | 21 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | HE CIPRESES U1 | 95.12% | 100% | 95.12% | 100%
2020-10-02 | 1 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-02 | 2 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-02 | 17 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-02 | 18 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-02 | 19 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-02 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 1 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 2 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 3 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 4 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 5 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 6 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 7 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 8 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 9 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 10 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 11 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 12 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 13 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 14 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 15 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 16 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 17 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 18 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 19 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-02 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | HE CIPRESES U3 | 98.29% | 100% | 98.29% | 100%
2020-10-02 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-02 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-02 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-02 | 3 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-02 | 20 | HE COLBÚN U1 | 99.78% | 100% | 99.78% | 100%
2020-10-02 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-02 | 22 | HE COLBÚN U1 | 99.77% | 100% | 99.77% | 100%
2020-10-02 | 23 | HE COLBÚN U1 | 98.22% | 100% | 98.22% | 100%
2020-10-02 | 0 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-02 | 20 | HE COLBÚN U2 | 99.67% | 100% | 99.67% | 100%
2020-10-02 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-02 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-02 | 23 | HE COLBÚN U2 | 97.78% | 100% | 97.78% | 100%
2020-10-02 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-02 | 0 | HE PEHUENCHE U1 | 98.67% | 100% | 98.67% | 100%
2020-10-02 | 1 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 2 | HE PEHUENCHE U1 | 88.22% | 100% | 88.22% | 88.22%
2020-10-02 | 3 | HE PEHUENCHE U1 | 94.67% | 100% | 94.67% | 94.67%
2020-10-02 | 4 | HE PEHUENCHE U1 | 98.11% | 100% | 98.11% | 100%
2020-10-02 | 5 | HE PEHUENCHE U1 | 87.22% | 100% | 87.22% | 87.22%
2020-10-02 | 6 | HE PEHUENCHE U1 | 99.44% | 100% | 99.44% | 100%
2020-10-02 | 7 | HE PEHUENCHE U1 | 91.78% | 100% | 91.78% | 91.78%
2020-10-02 | 8 | HE PEHUENCHE U1 | 96.11% | 100% | 96.11% | 100%
2020-10-02 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 10 | HE PEHUENCHE U1 | 95.85% | 100% | 95.85% | 100%
2020-10-02 | 11 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 12 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 15 | HE PEHUENCHE U1 | 89.11% | 100% | 89.11% | 89.11%
2020-10-02 | 16 | HE PEHUENCHE U1 | 88.56% | 100% | 88.56% | 88.56%
2020-10-02 | 17 | HE PEHUENCHE U1 | 96.56% | 100% | 96.56% | 100%
2020-10-02 | 18 | HE PEHUENCHE U1 | 95.78% | 100% | 95.78% | 100%
2020-10-02 | 19 | HE PEHUENCHE U1 | 96.56% | 100% | 96.56% | 100%
2020-10-02 | 20 | HE PEHUENCHE U1 | 97.89% | 100% | 97.89% | 100%
2020-10-02 | 21 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 22 | HE PEHUENCHE U1 | 99.67% | 100% | 99.67% | 100%
2020-10-02 | 23 | HE PEHUENCHE U1 | 98.33% | 100% | 98.33% | 100%
2020-10-02 | 0 | HE PEHUENCHE U2 | 98% | 100% | 98% | 100%
2020-10-02 | 1 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-02 | 2 | HE PEHUENCHE U2 | 92.78% | 100% | 92.78% | 92.78%
2020-10-02 | 3 | HE PEHUENCHE U2 | 94.89% | 100% | 94.89% | 94.89%
2020-10-02 | 4 | HE PEHUENCHE U2 | 98.44% | 100% | 98.44% | 100%
2020-10-02 | 5 | HE PEHUENCHE U2 | 93.11% | 100% | 93.11% | 93.11%
2020-10-02 | 6 | HE PEHUENCHE U2 | 99.44% | 100% | 99.44% | 100%
2020-10-02 | 7 | HE PEHUENCHE U2 | 95.33% | 100% | 95.33% | 100%
2020-10-02 | 8 | HE PEHUENCHE U2 | 95.44% | 100% | 95.44% | 100%
2020-10-02 | 9 | HE PEHUENCHE U2 | 97.78% | 100% | 97.78% | 100%
2020-10-02 | 10 | HE PEHUENCHE U2 | 98.33% | 100% | 98.33% | 100%
2020-10-02 | 11 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-02 | 12 | HE PEHUENCHE U2 | 97% | 100% | 97% | 100%
2020-10-02 | 13 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-02 | 14 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-02 | 15 | HE PEHUENCHE U2 | 88.11% | 100% | 88.11% | 88.11%
2020-10-02 | 16 | HE PEHUENCHE U2 | 89.56% | 100% | 89.56% | 89.56%
2020-10-02 | 17 | HE PEHUENCHE U2 | 94.56% | 100% | 94.56% | 94.56%
2020-10-02 | 18 | HE PEHUENCHE U2 | 96.78% | 100% | 96.78% | 100%
2020-10-02 | 19 | HE PEHUENCHE U2 | 98.22% | 100% | 98.22% | 100%
2020-10-02 | 20 | HE PEHUENCHE U2 | 98.67% | 100% | 98.67% | 100%
2020-10-02 | 21 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-02 | 22 | HE PEHUENCHE U2 | 98.89% | 100% | 98.89% | 100%
2020-10-02 | 23 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-02 | 0 | HE RALCO U1 | 99.33% | 100% | 99.33% | 100%
2020-10-02 | 1 | HE RALCO U1 | 94.56% | 100% | 94.56% | 94.56%
2020-10-02 | 2 | HE RALCO U1 | 88.33% | 100% | 88.33% | 88.33%
2020-10-02 | 3 | HE RALCO U1 | 90.33% | 100% | 90.33% | 90.33%
2020-10-02 | 4 | HE RALCO U1 | 95.89% | 100% | 95.89% | 100%
2020-10-02 | 5 | HE RALCO U1 | 90.89% | 100% | 90.89% | 90.89%
2020-10-02 | 6 | HE RALCO U1 | 98.56% | 100% | 98.56% | 100%
2020-10-02 | 7 | HE RALCO U1 | 93.89% | 100% | 93.89% | 93.89%
2020-10-02 | 8 | HE RALCO U1 | 80.78% | 100% | 80.78% | 80.78%
2020-10-02 | 9 | HE RALCO U1 | 94.22% | 100% | 94.22% | 94.22%
2020-10-02 | 10 | HE RALCO U1 | 54.67% | 100% | 54.67% | 0%
2020-10-02 | 11 | HE RALCO U1 | 94% | 100% | 94% | 94%
2020-10-02 | 12 | HE RALCO U1 | 97.78% | 100% | 97.78% | 100%
2020-10-02 | 13 | HE RALCO U1 | 95.56% | 100% | 95.56% | 100%
2020-10-02 | 14 | HE RALCO U1 | 92.67% | 100% | 92.67% | 92.67%
2020-10-02 | 15 | HE RALCO U1 | 88.67% | 100% | 88.67% | 88.67%
2020-10-02 | 16 | HE RALCO U1 | 90.44% | 100% | 90.44% | 90.44%
2020-10-02 | 17 | HE RALCO U1 | 94.78% | 100% | 94.78% | 94.78%
2020-10-02 | 18 | HE RALCO U1 | 92.89% | 100% | 92.89% | 92.89%
2020-10-02 | 19 | HE RALCO U1 | 93.89% | 100% | 93.89% | 93.89%
2020-10-02 | 20 | HE RALCO U1 | 90.67% | 100% | 90.67% | 90.67%
2020-10-02 | 21 | HE RALCO U1 | 85.44% | 100% | 85.44% | 85.44%
2020-10-02 | 22 | HE RALCO U1 | 99.67% | 100% | 99.67% | 100%
2020-10-02 | 23 | HE RALCO U1 | 90.11% | 100% | 90.11% | 90.11%
2020-10-02 | 0 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-02 | 1 | HE RALCO U2 | 95.33% | 100% | 95.33% | 100%
2020-10-02 | 2 | HE RALCO U2 | 99.22% | 100% | 99.22% | 100%
2020-10-02 | 3 | HE RALCO U2 | 98.33% | 100% | 98.33% | 100%
2020-10-02 | 4 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-02 | 5 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-02 | 6 | HE RALCO U2 | 99.56% | 100% | 99.56% | 100%
2020-10-02 | 7 | HE RALCO U2 | 95.33% | 100% | 95.33% | 100%
2020-10-02 | 8 | HE RALCO U2 | 98.56% | 100% | 98.56% | 100%
2020-10-02 | 9 | HE RALCO U2 | 99.78% | 100% | 99.78% | 100%
2020-10-02 | 10 | HE RALCO U2 | 99.56% | 100% | 99.56% | 100%
2020-10-02 | 11 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-02 | 12 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-02 | 13 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-02 | 14 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-02 | 15 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-02 | 16 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-02 | 17 | HE RALCO U2 | 95.56% | 100% | 95.56% | 100%
2020-10-02 | 18 | HE RALCO U2 | 96.56% | 100% | 96.56% | 100%
2020-10-02 | 19 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-02 | 20 | HE RALCO U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-02 | 22 | HE RALCO U2 | 97.22% | 100% | 97.22% | 100%
2020-10-02 | 23 | HE RALCO U2 | 98.22% | 100% | 98.22% | 100%
2020-10-02 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | HE RAPEL U2 | 100% | 100% | 100% | 100%
2020-10-02 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | HE RAPEL U2 | 100% | 100% | 100% | 100%
2020-10-02 | 21 | HE RAPEL U2 | 100% | 100% | 100% | 100%
2020-10-02 | 22 | HE RAPEL U2 | 100% | 100% | 100% | 100%
2020-10-02 | 23 | HE RAPEL U2 | 100% | 100% | 100% | 100%
2020-10-02 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | HE RAPEL U3 | 100% | 100% | 100% | 100%
2020-10-02 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | HE RAPEL U4 | 100% | 100% | 100% | 100%
2020-10-02 | 21 | HE RAPEL U4 | 100% | 100% | 100% | 100%
2020-10-02 | 22 | HE RAPEL U4 | 100% | 100% | 100% | 100%
2020-10-02 | 23 | HE RAPEL U4 | 100% | 100% | 100% | 100%
2020-10-02 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 1 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 2 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 3 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 4 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 5 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 6 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 7 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 8 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 9 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 10 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 11 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 12 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 13 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 14 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 15 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 16 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 17 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 18 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 19 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 20 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 21 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 22 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 23 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-02 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-02 | 7 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-02 | 8 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-02 | 9 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-02 | 10 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-02 | 11 | TER ANGAMOS U2 | 98.22% | 100% | 98.22% | 100%
2020-10-02 | 12 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-02 | 13 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-02 | 14 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-02 | 15 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-02 | 16 | TER ANGAMOS U2 | 90.67% | 100% | 90.67% | 90.67%
2020-10-02 | 17 | TER ANGAMOS U2 | 98.78% | 100% | 98.78% | 100%
2020-10-02 | 18 | TER ANGAMOS U2 | 99.89% | 100% | 99.89% | 100%
2020-10-02 | 19 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-02 | 20 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-02 | 20 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-02 | 21 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-02 | 22 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-02 | 23 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-02 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 7 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 8 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 9 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 10 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 11 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 12 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 13 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 14 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 15 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 16 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 17 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 18 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 19 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-02 | 20 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-02 | 9 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-02 | 10 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-02 | 11 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-02 | 12 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-02 | 13 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-02 | 14 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-02 | 15 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-02 | 16 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-02 | 17 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-02 | 18 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-02 | 19 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-02 | 1 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-02 | 2 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-02 | 3 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-02 | 4 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-02 | 5 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-02 | 6 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-02 | 7 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-02 | 8 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-02 | 9 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-02 | 10 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-02 | 11 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-02 | 12 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-02 | 18 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-02 | 19 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-02 | 20 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-02 | 1 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-02 | 2 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-02 | 3 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-02 | 4 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-02 | 5 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-02 | 6 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-02 | 7 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-02 | 8 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-02 | 9 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-02 | 10 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-02 | 11 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-02 | 12 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-02 | 1 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-02 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-02 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-02 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-02 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-02 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-02 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-02 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-02 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-02 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-02 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-02 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-02 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-02 | 14 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-02 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-02 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-02 | 20 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 1 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 2 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 3 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 4 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 5 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 6 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 7 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 8 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 9 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 10 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 11 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 12 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 13 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 14 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 18 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 20 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 23 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-02 | 0 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-02 | 3 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-02 | 4 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-02 | 5 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-02 | 6 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-02 | 7 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-02 | 8 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-02 | 9 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-02 | 10 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-02 | 11 | TER GUACOLDA U5 | 99.33% | 100% | 99.33% | 100%
2020-10-02 | 12 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-02 | 13 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-02 | 14 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-02 | 19 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-02 | 20 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 1 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 2 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 3 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 4 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 5 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 6 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 7 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 8 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 14 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 15 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 16 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 17 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 18 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 19 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 20 | TER MEJILLONES CTM3-TV | 98.89% | 100% | 98.89% | 100%
2020-10-02 | 21 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 22 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 23 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-02 | 0 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER NEHUENCO II CC1-TV | 99% | 100% | 99% | 100%
2020-10-02 | 1 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-02 | 2 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-02 | 3 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-02 | 4 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-02 | 5 | TER NEHUENCO II CC1-TV | 97.89% | 100% | 97.89% | 100%
2020-10-02 | 6 | TER NEHUENCO II CC1-TV | 97.22% | 100% | 97.22% | 100%
2020-10-02 | 7 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-02 | 8 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-02 | 9 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER NEHUENCO II CC1-TV | 99.8% | 100% | 99.8% | 100%
2020-10-02 | 16 | TER NEHUENCO II CC1-TV | 83.44% | 100% | 83.44% | 83.44%
2020-10-02 | 17 | TER NEHUENCO II CC1-TV | 84% | 100% | 84% | 84%
2020-10-02 | 18 | TER NEHUENCO II CC1-TV | 98.56% | 100% | 98.56% | 100%
2020-10-02 | 19 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-02 | 20 | TER NEHUENCO II CC1-TV | 97.89% | 100% | 97.89% | 100%
2020-10-02 | 21 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-02 | 22 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-02 | 23 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-02 | 0 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 1 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 2 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 3 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 4 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 5 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 6 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 7 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 8 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 9 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 10 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 11 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 12 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 13 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 14 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 15 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 16 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 17 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 18 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 19 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 20 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 21 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 22 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 23 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-02 | 0 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-02 | 1 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 1 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 2 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 3 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 4 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 5 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 6 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 7 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 8 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 9 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 10 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 11 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 12 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 13 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 14 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 15 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 16 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 17 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 18 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 19 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 20 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 21 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 22 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 23 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-02 | 0 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 1 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 2 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 3 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 4 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 5 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 6 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 7 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 8 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 9 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 10 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 11 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 12 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 13 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 14 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 15 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 16 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 17 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 18 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 19 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 20 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 21 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 22 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 23 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-02 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-02 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-02 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 9 | HE CANUTILLAR U1 | 99.78% | 100% | 99.78% | 100%
2020-10-03 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 20 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-03 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 20 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 22 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-03 | 0 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | HE CIPRESES U1 | 90.01% | 100% | 90.01% | 90.01%
2020-10-03 | 2 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 3 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 4 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 5 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 6 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 7 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 8 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 9 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 10 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 11 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 12 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 13 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 14 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 15 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 16 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 17 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 18 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 19 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 20 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-03 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 1 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 2 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 3 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 4 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 5 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 6 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 7 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 8 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 9 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 10 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 11 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 12 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 13 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 14 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 15 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 16 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 17 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 18 | HE CIPRESES U3 | 97.56% | 100% | 97.56% | 100%
2020-10-03 | 19 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 20 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 21 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 22 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 23 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-03 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-03 | 1 | HE COLBÚN U1 | 97.44% | 100% | 97.44% | 100%
2020-10-03 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-03 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-03 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-03 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-03 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-03 | 7 | HE COLBÚN U1 | 96.56% | 100% | 96.56% | 100%
2020-10-03 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-03 | 9 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | HE COLBÚN U1 | 99.76% | 100% | 99.76% | 100%
2020-10-03 | 11 | HE COLBÚN U1 | 99.44% | 100% | 99.44% | 100%
2020-10-03 | 12 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-03 | 13 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | HE COLBÚN U1 | 95.64% | 100% | 95.64% | 100%
2020-10-03 | 19 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-03 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-03 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-03 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-03 | 23 | HE COLBÚN U1 | 99.89% | 100% | 99.89% | 100%
2020-10-03 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-03 | 1 | HE COLBÚN U2 | 98.11% | 100% | 98.11% | 100%
2020-10-03 | 2 | HE COLBÚN U2 | 98.67% | 100% | 98.67% | 100%
2020-10-03 | 3 | HE COLBÚN U2 | 98.44% | 100% | 98.44% | 100%
2020-10-03 | 4 | HE COLBÚN U2 | 99.78% | 100% | 99.78% | 100%
2020-10-03 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-03 | 6 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-03 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-03 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-03 | 22 | HE COLBÚN U2 | 99.89% | 100% | 99.89% | 100%
2020-10-03 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-03 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-03 | 0 | HE PEHUENCHE U1 | 99.22% | 100% | 99.22% | 100%
2020-10-03 | 1 | HE PEHUENCHE U1 | 92.56% | 100% | 92.56% | 92.56%
2020-10-03 | 2 | HE PEHUENCHE U1 | 99.56% | 100% | 99.56% | 100%
2020-10-03 | 3 | HE PEHUENCHE U1 | 99.78% | 100% | 99.78% | 100%
2020-10-03 | 4 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-03 | 5 | HE PEHUENCHE U1 | 99.33% | 100% | 99.33% | 100%
2020-10-03 | 6 | HE PEHUENCHE U1 | 98.78% | 100% | 98.78% | 100%
2020-10-03 | 7 | HE PEHUENCHE U1 | 95.33% | 100% | 95.33% | 100%
2020-10-03 | 8 | HE PEHUENCHE U1 | 94.44% | 100% | 94.44% | 94.44%
2020-10-03 | 9 | HE PEHUENCHE U1 | 89.13% | 100% | 89.13% | 89.13%
2020-10-03 | 10 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | HE PEHUENCHE U1 | 63.92% | 100% | 63.92% | 0%
2020-10-03 | 13 | HE PEHUENCHE U1 | 92.11% | 100% | 92.11% | 92.11%
2020-10-03 | 14 | HE PEHUENCHE U1 | 94.11% | 100% | 94.11% | 94.11%
2020-10-03 | 15 | HE PEHUENCHE U1 | 83.67% | 100% | 83.67% | 83.67%
2020-10-03 | 16 | HE PEHUENCHE U1 | 94.56% | 100% | 94.56% | 94.56%
2020-10-03 | 17 | HE PEHUENCHE U1 | 90.89% | 100% | 90.89% | 90.89%
2020-10-03 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-03 | 19 | HE PEHUENCHE U1 | 97.67% | 100% | 97.67% | 100%
2020-10-03 | 20 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-03 | 21 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-03 | 22 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-03 | 23 | HE PEHUENCHE U1 | 99.78% | 100% | 99.78% | 100%
2020-10-03 | 0 | HE PEHUENCHE U2 | 95.33% | 100% | 95.33% | 100%
2020-10-03 | 1 | HE PEHUENCHE U2 | 93% | 100% | 93% | 93%
2020-10-03 | 2 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 3 | HE PEHUENCHE U2 | 99.78% | 100% | 99.78% | 100%
2020-10-03 | 4 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | HE PEHUENCHE U2 | 97.36% | 100% | 97.36% | 100%
2020-10-03 | 7 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 8 | HE PEHUENCHE U2 | 96.56% | 100% | 96.56% | 100%
2020-10-03 | 9 | HE PEHUENCHE U2 | 92% | 100% | 92% | 92%
2020-10-03 | 10 | HE PEHUENCHE U2 | 99.11% | 100% | 99.11% | 100%
2020-10-03 | 11 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 12 | HE PEHUENCHE U2 | 98.89% | 100% | 98.89% | 100%
2020-10-03 | 13 | HE PEHUENCHE U2 | 93.33% | 100% | 93.33% | 93.33%
2020-10-03 | 14 | HE PEHUENCHE U2 | 90.22% | 100% | 90.22% | 90.22%
2020-10-03 | 15 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 16 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 18 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 19 | HE PEHUENCHE U2 | 97% | 100% | 97% | 100%
2020-10-03 | 20 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 21 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 22 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 23 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 0 | HE RALCO U1 | 89.11% | 100% | 89.11% | 89.11%
2020-10-03 | 1 | HE RALCO U1 | 56.56% | 100% | 56.56% | 0%
2020-10-03 | 2 | HE RALCO U1 | 98.56% | 100% | 98.56% | 100%
2020-10-03 | 3 | HE RALCO U1 | 97% | 100% | 97% | 100%
2020-10-03 | 4 | HE RALCO U1 | 98.56% | 100% | 98.56% | 100%
2020-10-03 | 5 | HE RALCO U1 | 97.11% | 100% | 97.11% | 100%
2020-10-03 | 6 | HE RALCO U1 | 94.44% | 100% | 94.44% | 94.44%
2020-10-03 | 7 | HE RALCO U1 | 91.44% | 100% | 91.44% | 91.44%
2020-10-03 | 8 | HE RALCO U1 | 88.56% | 100% | 88.56% | 88.56%
2020-10-03 | 9 | HE RALCO U1 | 92.78% | 100% | 92.78% | 92.78%
2020-10-03 | 10 | HE RALCO U1 | 97.78% | 100% | 97.78% | 100%
2020-10-03 | 11 | HE RALCO U1 | 86.22% | 100% | 86.22% | 86.22%
2020-10-03 | 12 | HE RALCO U1 | 65.44% | 100% | 65.44% | 0%
2020-10-03 | 13 | HE RALCO U1 | 83.89% | 100% | 83.89% | 83.89%
2020-10-03 | 14 | HE RALCO U1 | 83% | 100% | 83% | 83%
2020-10-03 | 15 | HE RALCO U1 | 84% | 100% | 84% | 84%
2020-10-03 | 16 | HE RALCO U1 | 93.56% | 100% | 93.56% | 93.56%
2020-10-03 | 17 | HE RALCO U1 | 91.44% | 100% | 91.44% | 91.44%
2020-10-03 | 18 | HE RALCO U1 | 95.67% | 100% | 95.67% | 100%
2020-10-03 | 19 | HE RALCO U1 | 94.67% | 100% | 94.67% | 94.67%
2020-10-03 | 20 | HE RALCO U1 | 95% | 100% | 95% | 95%
2020-10-03 | 21 | HE RALCO U1 | 100% | 100% | 100% | 100%
2020-10-03 | 22 | HE RALCO U1 | 96% | 100% | 96% | 100%
2020-10-03 | 23 | HE RALCO U1 | 100% | 100% | 100% | 100%
2020-10-03 | 0 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-03 | 1 | HE RALCO U2 | 91% | 100% | 91% | 91%
2020-10-03 | 2 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-03 | 3 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-03 | 4 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-03 | 5 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-03 | 6 | HE RALCO U2 | 97% | 100% | 97% | 100%
2020-10-03 | 7 | HE RALCO U2 | 95.56% | 100% | 95.56% | 100%
2020-10-03 | 8 | HE RALCO U2 | 92.56% | 100% | 92.56% | 92.56%
2020-10-03 | 9 | HE RALCO U2 | 95.22% | 100% | 95.22% | 100%
2020-10-03 | 10 | HE RALCO U2 | 99.33% | 100% | 99.33% | 100%
2020-10-03 | 11 | HE RALCO U2 | 93.89% | 100% | 93.89% | 93.89%
2020-10-03 | 12 | HE RALCO U2 | 98.33% | 100% | 98.33% | 100%
2020-10-03 | 13 | HE RALCO U2 | 96.89% | 100% | 96.89% | 100%
2020-10-03 | 14 | HE RALCO U2 | 95.78% | 100% | 95.78% | 100%
2020-10-03 | 15 | HE RALCO U2 | 85.67% | 100% | 85.67% | 85.67%
2020-10-03 | 16 | HE RALCO U2 | 91.11% | 100% | 91.11% | 91.11%
2020-10-03 | 17 | HE RALCO U2 | 93.22% | 100% | 93.22% | 93.22%
2020-10-03 | 18 | HE RALCO U2 | 98.33% | 100% | 98.33% | 100%
2020-10-03 | 19 | HE RALCO U2 | 96.33% | 100% | 96.33% | 100%
2020-10-03 | 20 | HE RALCO U2 | 97.44% | 100% | 97.44% | 100%
2020-10-03 | 21 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-03 | 22 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-03 | 23 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-03 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 1 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 2 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 3 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 4 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 5 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 6 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 7 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 8 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 9 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 10 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 11 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 12 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 13 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 14 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 15 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 16 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 17 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 18 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 19 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 20 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 21 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 22 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 23 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-03 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-03 | 9 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-03 | 10 | TER ANGAMOS U2 | 99.11% | 100% | 99.11% | 100%
2020-10-03 | 11 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-03 | 12 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-03 | 13 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-03 | 14 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-03 | 15 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-03 | 16 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-03 | 17 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-03 | 18 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-03 | 19 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-03 | 1 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-03 | 8 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-03 | 9 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-03 | 10 | TER COCHRANE U1 | 98.4% | 100% | 98.4% | 100%
2020-10-03 | 11 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-03 | 12 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-03 | 13 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-03 | 14 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-03 | 15 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-03 | 16 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-03 | 17 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-03 | 18 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-03 | 19 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 8 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 9 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 10 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 11 | TER COCHRANE U2 | 97.78% | 100% | 97.78% | 100%
2020-10-03 | 12 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 13 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 14 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 15 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 16 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 17 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 18 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-03 | 19 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-03 | 4 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-03 | 5 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-03 | 6 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-03 | 7 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-03 | 8 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-03 | 9 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-03 | 10 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-03 | 20 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-03 | 21 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-03 | 22 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-03 | 23 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-03 | 0 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-03 | 2 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-03 | 3 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-03 | 4 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-03 | 5 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-03 | 6 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-03 | 7 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-03 | 8 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-03 | 9 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-03 | 10 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-03 | 19 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-03 | 20 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-03 | 21 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-03 | 22 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-03 | 23 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-03 | 0 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-03 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-03 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-03 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-03 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-03 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-03 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-03 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-03 | 15 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-03 | 16 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-03 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-03 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-03 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-03 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-03 | 21 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-03 | 22 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-03 | 23 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-03 | 0 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 1 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 2 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 3 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 4 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 5 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 6 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 7 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 8 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 9 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 10 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 11 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 12 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 13 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 14 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 15 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 16 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 17 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 18 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 20 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 21 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 22 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 23 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-03 | 0 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-03 | 9 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-03 | 10 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-03 | 11 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-03 | 12 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER GUACOLDA U5 | 98.32% | 100% | 98.32% | 100%
2020-10-03 | 19 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-03 | 20 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-03 | 21 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-03 | 22 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-03 | 23 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-03 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER KELAR CC1-TG2 | No Participó | 28.33% | 28.33% | 0%
2020-10-03 | 18 | TER KELAR CC1-TG2 | No Participó | 0% | 0% | 0%
2020-10-03 | 19 | TER KELAR CC1-TG2 | No Participó | 0% | 0% | 0%
2020-10-03 | 20 | TER KELAR CC1-TG2 | No Participó | 0% | 0% | 0%
2020-10-03 | 21 | TER KELAR CC1-TG2 | No Participó | 0% | 0% | 0%
2020-10-03 | 22 | TER KELAR CC1-TG2 | No Participó | 0% | 0% | 0%
2020-10-03 | 23 | TER KELAR CC1-TG2 | No Participó | 0% | 0% | 0%
2020-10-03 | 0 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 1 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 2 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 3 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 4 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 5 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 6 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 7 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 8 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 9 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 10 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 11 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 12 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 13 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 14 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 15 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 16 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 17 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 18 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 19 | TER MEJILLONES CTM3-TV | 97.78% | 100% | 97.78% | 100%
2020-10-03 | 20 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 21 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 22 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-03 | 23 | TER MEJILLONES CTM3-TV | 98.22% | 100% | 98.22% | 100%
2020-10-03 | 0 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-03 | 1 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-03 | 2 | TER NEHUENCO II CC1-TV | 97.33% | 100% | 97.33% | 100%
2020-10-03 | 3 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-03 | 4 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-03 | 5 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-03 | 6 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-03 | 7 | TER NEHUENCO II CC1-TV | 96.78% | 100% | 96.78% | 100%
2020-10-03 | 8 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-03 | 9 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-03 | 10 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-03 | 12 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-03 | 13 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-03 | 14 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER NEHUENCO II CC1-TV | 96.74% | 100% | 96.74% | 100%
2020-10-03 | 19 | TER NEHUENCO II CC1-TV | 97.33% | 100% | 97.33% | 100%
2020-10-03 | 20 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-03 | 21 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-03 | 22 | TER NEHUENCO II CC1-TV | 97.44% | 100% | 97.44% | 100%
2020-10-03 | 23 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-03 | 0 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 1 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 2 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 3 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 4 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 5 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 6 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 7 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 8 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 9 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 10 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 11 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 12 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 13 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 14 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 15 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 16 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 17 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 18 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 19 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 20 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 21 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 22 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 23 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-03 | 0 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 1 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 2 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 3 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 4 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 5 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 6 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 7 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 8 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 9 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 10 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 11 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 12 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 13 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 14 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 15 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 16 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 17 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 18 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 19 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 20 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 21 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 22 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 23 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-03 | 0 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 1 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 2 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 3 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 4 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 5 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 6 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 7 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 8 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 9 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 10 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 11 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 12 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 13 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 14 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 15 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 16 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 17 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 18 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 19 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 20 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 21 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 22 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 23 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-03 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-03 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-03 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 9 | HE CANUTILLAR U1 | 97.44% | 100% | 97.44% | 100%
2020-10-04 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 21 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 23 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-04 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 10 | HE CANUTILLAR U2 | 99.42% | 100% | 99.42% | 100%
2020-10-04 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 21 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-04 | 0 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 1 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 2 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 3 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 4 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 5 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 6 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 7 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 8 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 9 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 10 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 11 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 12 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 14 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 16 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 17 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 18 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 19 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 20 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-04 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 1 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 2 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 3 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 4 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 5 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 6 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 7 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 8 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 9 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 10 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 12 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 13 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 14 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 15 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 16 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 17 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 18 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 19 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 20 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 23 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-04 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-04 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-04 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-04 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-04 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-04 | 5 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-04 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-04 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-04 | 23 | HE COLBÚN U1 | 99.89% | 100% | 99.89% | 100%
2020-10-04 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-04 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-04 | 2 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | HE COLBÚN U2 | 99.56% | 100% | 99.56% | 100%
2020-10-04 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-04 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-04 | 8 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | HE COLBÚN U2 | 95.64% | 100% | 95.64% | 100%
2020-10-04 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-04 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-04 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-04 | 23 | HE COLBÚN U2 | 99.89% | 100% | 99.89% | 100%
2020-10-04 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-04 | 0 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 1 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 2 | HE PEHUENCHE U1 | 97.11% | 100% | 97.11% | 100%
2020-10-04 | 3 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 4 | HE PEHUENCHE U1 | 99.89% | 100% | 99.89% | 100%
2020-10-04 | 5 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 6 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 8 | HE PEHUENCHE U1 | 99.11% | 100% | 99.11% | 100%
2020-10-04 | 9 | HE PEHUENCHE U1 | 96.78% | 100% | 96.78% | 100%
2020-10-04 | 10 | HE PEHUENCHE U1 | 98.78% | 100% | 98.78% | 100%
2020-10-04 | 11 | HE PEHUENCHE U1 | 95.44% | 100% | 95.44% | 100%
2020-10-04 | 12 | HE PEHUENCHE U1 | 98.56% | 100% | 98.56% | 100%
2020-10-04 | 13 | HE PEHUENCHE U1 | 95.44% | 100% | 95.44% | 100%
2020-10-04 | 14 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 15 | HE PEHUENCHE U1 | 96.22% | 100% | 96.22% | 100%
2020-10-04 | 16 | HE PEHUENCHE U1 | 91% | 100% | 91% | 91%
2020-10-04 | 17 | HE PEHUENCHE U1 | 95.67% | 100% | 95.67% | 100%
2020-10-04 | 18 | HE PEHUENCHE U1 | 98.44% | 100% | 98.44% | 100%
2020-10-04 | 19 | HE PEHUENCHE U1 | 96.67% | 100% | 96.67% | 100%
2020-10-04 | 20 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 21 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 22 | HE PEHUENCHE U1 | 96.56% | 100% | 96.56% | 100%
2020-10-04 | 23 | HE PEHUENCHE U1 | 99.67% | 100% | 99.67% | 100%
2020-10-04 | 0 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-04 | 1 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-04 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | HE PEHUENCHE U2 | 98.69% | 100% | 98.69% | 100%
2020-10-04 | 20 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-04 | 21 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-04 | 22 | HE PEHUENCHE U2 | 97.22% | 100% | 97.22% | 100%
2020-10-04 | 23 | HE PEHUENCHE U2 | 99.78% | 100% | 99.78% | 100%
2020-10-04 | 0 | HE RALCO U1 | 97.89% | 100% | 97.89% | 100%
2020-10-04 | 1 | HE RALCO U1 | 87.67% | 100% | 87.67% | 87.67%
2020-10-04 | 2 | HE RALCO U1 | 98.67% | 100% | 98.67% | 100%
2020-10-04 | 3 | HE RALCO U1 | 100% | 100% | 100% | 100%
2020-10-04 | 4 | HE RALCO U1 | 96.33% | 100% | 96.33% | 100%
2020-10-04 | 5 | HE RALCO U1 | 98.44% | 100% | 98.44% | 100%
2020-10-04 | 6 | HE RALCO U1 | 89.78% | 100% | 89.78% | 89.78%
2020-10-04 | 7 | HE RALCO U1 | 98.89% | 100% | 98.89% | 100%
2020-10-04 | 8 | HE RALCO U1 | 95.33% | 100% | 95.33% | 100%
2020-10-04 | 9 | HE RALCO U1 | 87.33% | 100% | 87.33% | 87.33%
2020-10-04 | 10 | HE RALCO U1 | 86.22% | 100% | 86.22% | 86.22%
2020-10-04 | 11 | HE RALCO U1 | 92.11% | 100% | 92.11% | 92.11%
2020-10-04 | 12 | HE RALCO U1 | 93.89% | 100% | 93.89% | 93.89%
2020-10-04 | 13 | HE RALCO U1 | 85.22% | 100% | 85.22% | 85.22%
2020-10-04 | 14 | HE RALCO U1 | 92.44% | 100% | 92.44% | 92.44%
2020-10-04 | 15 | HE RALCO U1 | 96.44% | 100% | 96.44% | 100%
2020-10-04 | 16 | HE RALCO U1 | 88.11% | 100% | 88.11% | 88.11%
2020-10-04 | 17 | HE RALCO U1 | 85.44% | 100% | 85.44% | 85.44%
2020-10-04 | 18 | HE RALCO U1 | 98.33% | 100% | 98.33% | 100%
2020-10-04 | 19 | HE RALCO U1 | 91.33% | 100% | 91.33% | 91.33%
2020-10-04 | 20 | HE RALCO U1 | 88.33% | 100% | 88.33% | 88.33%
2020-10-04 | 21 | HE RALCO U1 | 96.67% | 100% | 96.67% | 100%
2020-10-04 | 22 | HE RALCO U1 | 93.33% | 100% | 93.33% | 93.33%
2020-10-04 | 23 | HE RALCO U1 | 99% | 100% | 99% | 100%
2020-10-04 | 0 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-04 | 1 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-04 | 2 | HE RALCO U2 | 99% | 100% | 99% | 100%
2020-10-04 | 3 | HE RALCO U2 | 99.22% | 100% | 99.22% | 100%
2020-10-04 | 4 | HE RALCO U2 | 97.33% | 100% | 97.33% | 100%
2020-10-04 | 5 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-04 | 6 | HE RALCO U2 | 96.89% | 100% | 96.89% | 100%
2020-10-04 | 7 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-04 | 8 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-04 | 9 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-04 | 10 | HE RALCO U2 | 85% | 100% | 85% | 85%
2020-10-04 | 11 | HE RALCO U2 | 86.89% | 100% | 86.89% | 86.89%
2020-10-04 | 12 | HE RALCO U2 | 94% | 100% | 94% | 94%
2020-10-04 | 13 | HE RALCO U2 | 87.11% | 100% | 87.11% | 87.11%
2020-10-04 | 14 | HE RALCO U2 | 86.89% | 100% | 86.89% | 86.89%
2020-10-04 | 15 | HE RALCO U2 | 95.22% | 100% | 95.22% | 100%
2020-10-04 | 16 | HE RALCO U2 | 88.56% | 100% | 88.56% | 88.56%
2020-10-04 | 17 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-04 | 18 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-04 | 19 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-04 | 20 | HE RALCO U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | HE RALCO U2 | 93.46% | 100% | 93.46% | 93.46%
2020-10-04 | 22 | HE RALCO U2 | 86.67% | 100% | 86.67% | 86.67%
2020-10-04 | 23 | HE RALCO U2 | 68.63% | 100% | 68.63% | 0%
2020-10-04 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-04 | 1 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-04 | 2 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-04 | 3 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-04 | 4 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-04 | 5 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-04 | 6 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-04 | 7 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-04 | 8 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-04 | 9 | PFV LUZ DEL NORTE | 100% | 0% | 0% | 0%
2020-10-04 | 10 | PFV LUZ DEL NORTE | 100% | 0% | 0% | 0%
2020-10-04 | 11 | PFV LUZ DEL NORTE | 100% | 0% | 0% | 0%
2020-10-04 | 12 | PFV LUZ DEL NORTE | 100% | 0% | 0% | 0%
2020-10-04 | 13 | PFV LUZ DEL NORTE | 99.89% | 0% | 0% | 0%
2020-10-04 | 14 | PFV LUZ DEL NORTE | 100% | 0% | 0% | 0%
2020-10-04 | 15 | PFV LUZ DEL NORTE | 99.44% | 0% | 0% | 0%
2020-10-04 | 16 | PFV LUZ DEL NORTE | 99.89% | 0% | 0% | 0%
2020-10-04 | 17 | PFV LUZ DEL NORTE | 100% | 0% | 0% | 0%
2020-10-04 | 18 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-04 | 19 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-04 | 20 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-04 | 21 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-04 | 22 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-04 | 23 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-04 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-04 | 3 | TER ANGAMOS U2 | 58.11% | 100% | 58.11% | 0%
2020-10-04 | 4 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-04 | 5 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-04 | 6 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-04 | 7 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-04 | 8 | TER ANGAMOS U2 | 99.48% | 100% | 99.48% | 100%
2020-10-04 | 9 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-04 | 10 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-04 | 11 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-04 | 12 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-04 | 13 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-04 | 14 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-04 | 15 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-04 | 16 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-04 | 17 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-04 | 18 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-04 | 19 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-04 | 20 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 8 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 9 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 10 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 11 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 12 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 13 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 14 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 15 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 16 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 17 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 18 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-04 | 19 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-04 | 7 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-04 | 8 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-04 | 9 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-04 | 10 | TER COCHRANE U2 | 99.69% | 100% | 99.69% | 100%
2020-10-04 | 11 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-04 | 12 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-04 | 13 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-04 | 14 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-04 | 15 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-04 | 16 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-04 | 17 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-04 | 18 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-04 | 19 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-04 | 1 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-04 | 2 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-04 | 4 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-04 | 5 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-04 | 6 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-04 | 7 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-04 | 8 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-04 | 20 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-04 | 21 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-04 | 22 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-04 | 23 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-04 | 0 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-04 | 1 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-04 | 20 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-04 | 21 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-04 | 22 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-04 | 23 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-04 | 0 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 1 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 12 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 21 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 22 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 23 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-04 | 0 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 1 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 2 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 3 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 4 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 5 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 6 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 7 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 8 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 9 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 10 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 11 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 12 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 13 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 20 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 21 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 22 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 23 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-04 | 0 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-04 | 1 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-04 | 2 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-04 | 3 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-04 | 4 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-04 | 5 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-04 | 6 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-04 | 7 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-04 | 8 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-04 | 9 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER GUACOLDA U5 | 95.31% | 100% | 95.31% | 100%
2020-10-04 | 20 | TER GUACOLDA U5 | 95.11% | 100% | 95.11% | 100%
2020-10-04 | 21 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-04 | 22 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-04 | 23 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-04 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER KELAR CC1-TG2 | No Participó | 0% | 0% | 0%
2020-10-04 | 1 | TER KELAR CC1-TG2 | No Participó | 28.33% | 28.33% | 0%
2020-10-04 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-04 | 5 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-04 | 6 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-04 | 7 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-04 | 8 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-04 | 9 | TER KELAR TV | 96.44% | 100% | 96.44% | 100%
2020-10-04 | 10 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-04 | 11 | TER KELAR TV | 99.78% | 100% | 99.78% | 100%
2020-10-04 | 12 | TER KELAR TV | 99.78% | 100% | 99.78% | 100%
2020-10-04 | 13 | TER KELAR TV | 95.22% | 100% | 95.22% | 100%
2020-10-04 | 14 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-04 | 15 | TER KELAR TV | 95.67% | 100% | 95.67% | 100%
2020-10-04 | 16 | TER KELAR TV | 93.56% | 100% | 93.56% | 93.56%
2020-10-04 | 17 | TER KELAR TV | 99.67% | 100% | 99.67% | 100%
2020-10-04 | 18 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-04 | 19 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-04 | 20 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-04 | 21 | TER KELAR TV | 96.56% | 100% | 96.56% | 100%
2020-10-04 | 22 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-04 | 23 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-04 | 0 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 1 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 2 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 3 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 4 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 5 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 6 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 7 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 8 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 9 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 10 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 11 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 12 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 13 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 14 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 15 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 16 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 17 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 18 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 19 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 20 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 21 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 22 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-04 | 23 | TER MEJILLONES CTM3-TV | 99.67% | 100% | 99.67% | 100%
2020-10-04 | 0 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-04 | 1 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-04 | 2 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-04 | 3 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-04 | 4 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-04 | 5 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-04 | 6 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-04 | 7 | TER NEHUENCO II CC1-TV | 97.67% | 100% | 97.67% | 100%
2020-10-04 | 8 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER NEHUENCO II CC1-TV | 97.51% | 100% | 97.51% | 100%
2020-10-04 | 19 | TER NEHUENCO II CC1-TV | 97.44% | 100% | 97.44% | 100%
2020-10-04 | 20 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-04 | 21 | TER NEHUENCO II CC1-TV | 97.33% | 100% | 97.33% | 100%
2020-10-04 | 22 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-04 | 23 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-04 | 0 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 1 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 2 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 3 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 4 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 5 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 6 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 7 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 8 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 9 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 10 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 11 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 12 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 13 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 14 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 15 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 16 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 17 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 18 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 19 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 20 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 21 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 22 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 23 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-04 | 0 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 1 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 2 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 3 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 4 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 5 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 6 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 7 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 8 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 9 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 10 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 11 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 12 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 13 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 14 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 15 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 16 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 17 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 18 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 19 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 20 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 21 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 22 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 23 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-04 | 0 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 1 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 2 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 3 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 4 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 5 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 6 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 7 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 8 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 9 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 10 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 11 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 12 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 13 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 14 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 15 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 16 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 17 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 18 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 19 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 20 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 21 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 22 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 23 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-04 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-04 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-04 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 14 | HE CANUTILLAR U1 | 99.78% | 100% | 99.78% | 100%
2020-10-05 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-05 | 20 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-05 | 20 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 1 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 2 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 3 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 6 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 7 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 8 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 9 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 10 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 11 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 12 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 13 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 14 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 15 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 16 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 17 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 18 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 19 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-05 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-05 | 1 | HE CIPRESES U3 | 96.44% | 100% | 96.44% | 100%
2020-10-05 | 2 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-05 | 3 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-05 | 4 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-05 | 5 | HE CIPRESES U3 | 98% | 100% | 98% | 100%
2020-10-05 | 6 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-05 | 7 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-05 | 8 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-05 | 9 | HE CIPRESES U3 | 98% | 100% | 98% | 100%
2020-10-05 | 10 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-05 | 11 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-05 | 12 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-05 | 13 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-05 | 14 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-05 | 15 | HE CIPRESES U3 | 98.11% | 100% | 98.11% | 100%
2020-10-05 | 16 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-05 | 17 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-05 | 18 | HE CIPRESES U3 | 96.56% | 100% | 96.56% | 100%
2020-10-05 | 19 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-05 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-05 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-05 | 2 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-05 | 3 | HE COLBÚN U1 | 99.89% | 100% | 99.89% | 100%
2020-10-05 | 4 | HE COLBÚN U1 | 99.22% | 100% | 99.22% | 100%
2020-10-05 | 5 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-05 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-05 | 7 | HE COLBÚN U1 | 96.78% | 100% | 96.78% | 100%
2020-10-05 | 8 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-05 | 9 | HE COLBÚN U1 | 98.78% | 100% | 98.78% | 100%
2020-10-05 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-05 | 11 | HE COLBÚN U1 | 99.33% | 100% | 99.33% | 100%
2020-10-05 | 12 | HE COLBÚN U1 | 93.06% | 100% | 93.06% | 93.06%
2020-10-05 | 13 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | HE COLBÚN U1 | 98.28% | 100% | 98.28% | 100%
2020-10-05 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-05 | 21 | HE COLBÚN U1 | 99.88% | 100% | 99.88% | 100%
2020-10-05 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-05 | 23 | HE COLBÚN U1 | 99.67% | 100% | 99.67% | 100%
2020-10-05 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-05 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-05 | 2 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | HE COLBÚN U2 | 99.65% | 100% | 99.65% | 100%
2020-10-05 | 8 | HE COLBÚN U2 | 99.78% | 100% | 99.78% | 100%
2020-10-05 | 9 | HE COLBÚN U2 | 97.22% | 100% | 97.22% | 100%
2020-10-05 | 10 | HE COLBÚN U2 | 99.33% | 100% | 99.33% | 100%
2020-10-05 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-05 | 12 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-05 | 19 | HE COLBÚN U2 | 98.44% | 100% | 98.44% | 100%
2020-10-05 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-05 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-05 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-05 | 23 | HE COLBÚN U2 | 99.11% | 100% | 99.11% | 100%
2020-10-05 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-05 | 0 | HE PEHUENCHE U1 | 99.33% | 100% | 99.33% | 100%
2020-10-05 | 1 | HE PEHUENCHE U1 | 99% | 100% | 99% | 100%
2020-10-05 | 2 | HE PEHUENCHE U1 | 99.78% | 100% | 99.78% | 100%
2020-10-05 | 3 | HE PEHUENCHE U1 | 98.22% | 100% | 98.22% | 100%
2020-10-05 | 4 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-05 | 5 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-05 | 6 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-05 | 7 | HE PEHUENCHE U1 | 78.78% | 100% | 78.78% | 78.78%
2020-10-05 | 8 | HE PEHUENCHE U1 | 98% | 100% | 98% | 100%
2020-10-05 | 9 | HE PEHUENCHE U1 | 79.33% | 100% | 79.33% | 79.33%
2020-10-05 | 10 | HE PEHUENCHE U1 | 93.78% | 100% | 93.78% | 93.78%
2020-10-05 | 11 | HE PEHUENCHE U1 | 98.89% | 100% | 98.89% | 100%
2020-10-05 | 12 | HE PEHUENCHE U1 | 87.22% | 100% | 87.22% | 87.22%
2020-10-05 | 13 | HE PEHUENCHE U1 | 90.56% | 100% | 90.56% | 90.56%
2020-10-05 | 14 | HE PEHUENCHE U1 | 88.56% | 100% | 88.56% | 88.56%
2020-10-05 | 15 | HE PEHUENCHE U1 | 96.33% | 100% | 96.33% | 100%
2020-10-05 | 16 | HE PEHUENCHE U1 | 97.67% | 100% | 97.67% | 100%
2020-10-05 | 17 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-05 | 18 | HE PEHUENCHE U1 | 99.78% | 100% | 99.78% | 100%
2020-10-05 | 19 | HE PEHUENCHE U1 | 91.33% | 100% | 91.33% | 91.33%
2020-10-05 | 20 | HE PEHUENCHE U1 | 91.38% | 100% | 91.38% | 91.38%
2020-10-05 | 21 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | HE PEHUENCHE U2 | 99.33% | 100% | 99.33% | 100%
2020-10-05 | 1 | HE PEHUENCHE U2 | 99% | 100% | 99% | 100%
2020-10-05 | 2 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 3 | HE PEHUENCHE U2 | 98.22% | 100% | 98.22% | 100%
2020-10-05 | 4 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 5 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 6 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 7 | HE PEHUENCHE U2 | 79% | 100% | 79% | 79%
2020-10-05 | 8 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 9 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | HE PEHUENCHE U2 | 90.37% | 100% | 90.37% | 90.37%
2020-10-05 | 20 | HE PEHUENCHE U2 | 95.89% | 100% | 95.89% | 100%
2020-10-05 | 21 | HE PEHUENCHE U2 | 94.56% | 100% | 94.56% | 94.56%
2020-10-05 | 22 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 23 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 0 | HE RALCO U1 | 98.56% | 100% | 98.56% | 100%
2020-10-05 | 1 | HE RALCO U1 | 99.56% | 100% | 99.56% | 100%
2020-10-05 | 2 | HE RALCO U1 | 93.22% | 100% | 93.22% | 93.22%
2020-10-05 | 3 | HE RALCO U1 | 71% | 100% | 71% | 0%
2020-10-05 | 4 | HE RALCO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | HE RALCO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | HE RALCO U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | HE RALCO U1 | 72.29% | 100% | 72.29% | 0%
2020-10-05 | 8 | HE RALCO U1 | 89.56% | 100% | 89.56% | 89.56%
2020-10-05 | 9 | HE RALCO U1 | 80.44% | 100% | 80.44% | 80.44%
2020-10-05 | 10 | HE RALCO U1 | 71.56% | 100% | 71.56% | 0%
2020-10-05 | 11 | HE RALCO U1 | 92.89% | 100% | 92.89% | 92.89%
2020-10-05 | 12 | HE RALCO U1 | 86.33% | 100% | 86.33% | 86.33%
2020-10-05 | 13 | HE RALCO U1 | 87.89% | 100% | 87.89% | 87.89%
2020-10-05 | 14 | HE RALCO U1 | 77.67% | 100% | 77.67% | 77.67%
2020-10-05 | 15 | HE RALCO U1 | 94.78% | 100% | 94.78% | 94.78%
2020-10-05 | 16 | HE RALCO U1 | 86% | 100% | 86% | 86%
2020-10-05 | 17 | HE RALCO U1 | 78.12% | 100% | 78.12% | 78.12%
2020-10-05 | 18 | HE RALCO U1 | 98.44% | 100% | 98.44% | 100%
2020-10-05 | 19 | HE RALCO U1 | 93% | 100% | 93% | 93%
2020-10-05 | 20 | HE RALCO U1 | 94.11% | 100% | 94.11% | 94.11%
2020-10-05 | 21 | HE RALCO U1 | 98.33% | 100% | 98.33% | 100%
2020-10-05 | 22 | HE RALCO U1 | 94.11% | 100% | 94.11% | 94.11%
2020-10-05 | 23 | HE RALCO U1 | 98.78% | 100% | 98.78% | 100%
2020-10-05 | 0 | HE RALCO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | HE RALCO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | HE RALCO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | HE RALCO U2 | 70.66% | 100% | 70.66% | 0%
2020-10-05 | 4 | HE RALCO U2 | 88.78% | 100% | 88.78% | 88.78%
2020-10-05 | 5 | HE RALCO U2 | 94.89% | 100% | 94.89% | 94.89%
2020-10-05 | 6 | HE RALCO U2 | 98.67% | 100% | 98.67% | 100%
2020-10-05 | 7 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-05 | 8 | HE RALCO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | HE RALCO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | HE RALCO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | HE RALCO U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | HE RALCO U2 | 92.58% | 100% | 92.58% | 92.58%
2020-10-05 | 13 | HE RALCO U2 | 89% | 100% | 89% | 89%
2020-10-05 | 14 | HE RALCO U2 | 72.56% | 100% | 72.56% | 0%
2020-10-05 | 15 | HE RALCO U2 | 93.78% | 100% | 93.78% | 93.78%
2020-10-05 | 16 | HE RALCO U2 | 89.56% | 100% | 89.56% | 89.56%
2020-10-05 | 17 | HE RALCO U2 | 94.67% | 100% | 94.67% | 94.67%
2020-10-05 | 18 | HE RALCO U2 | 99.33% | 100% | 99.33% | 100%
2020-10-05 | 19 | HE RALCO U2 | 93% | 100% | 93% | 93%
2020-10-05 | 20 | HE RALCO U2 | 95.56% | 100% | 95.56% | 100%
2020-10-05 | 21 | HE RALCO U2 | 98.22% | 100% | 98.22% | 100%
2020-10-05 | 22 | HE RALCO U2 | 95% | 100% | 95% | 95%
2020-10-05 | 23 | HE RALCO U2 | 97% | 100% | 97% | 100%
2020-10-05 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 1 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 2 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 3 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 4 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 5 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 6 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 7 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 8 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 9 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 10 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 11 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 12 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 13 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 14 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 15 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 16 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 17 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 18 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 19 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 20 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 21 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 22 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 23 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-05 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-05 | 10 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-05 | 11 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-05 | 12 | TER ANGAMOS U2 | 98.11% | 100% | 98.11% | 100%
2020-10-05 | 13 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-05 | 14 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-05 | 15 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-05 | 16 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-05 | 17 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-05 | 18 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-05 | 19 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-05 | 9 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-05 | 10 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-05 | 11 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-05 | 12 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-05 | 13 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-05 | 14 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-05 | 15 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-05 | 16 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-05 | 17 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-05 | 18 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-05 | 19 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-05 | 20 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 9 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 10 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 11 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 12 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 13 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 14 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 15 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 16 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 17 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 18 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 19 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-05 | 20 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-05 | 3 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-05 | 4 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-05 | 5 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-05 | 6 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-05 | 7 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-05 | 8 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-05 | 9 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-05 | 10 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-05 | 11 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-05 | 12 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-05 | 3 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-05 | 4 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-05 | 5 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-05 | 6 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-05 | 7 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-05 | 8 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-05 | 9 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-05 | 10 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-05 | 11 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-05 | 12 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-05 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-05 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-05 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-05 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-05 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-05 | 8 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-05 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-05 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-05 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-05 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-05 | 14 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-05 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-05 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-05 | 20 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-05 | 2 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-05 | 3 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-05 | 4 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-05 | 5 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-05 | 6 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-05 | 7 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-05 | 8 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-05 | 9 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-05 | 10 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-05 | 11 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-05 | 12 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-05 | 13 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-05 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-05 | 20 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-05 | 4 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-05 | 5 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-05 | 6 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-05 | 7 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-05 | 11 | TER GUACOLDA U5 | 95.44% | 100% | 95.44% | 100%
2020-10-05 | 12 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-05 | 13 | TER GUACOLDA U5 | 99.14% | 100% | 99.14% | 100%
2020-10-05 | 14 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-05 | 15 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-05 | 16 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-05 | 17 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-05 | 18 | TER GUACOLDA U5 | 98.16% | 100% | 98.16% | 100%
2020-10-05 | 19 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-05 | 20 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 1 | TER KELAR TV | 99.56% | 100% | 99.56% | 100%
2020-10-05 | 2 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 3 | TER KELAR TV | 99.78% | 100% | 99.78% | 100%
2020-10-05 | 4 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 5 | TER KELAR TV | 97.44% | 100% | 97.44% | 100%
2020-10-05 | 6 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 7 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 8 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 9 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 10 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 11 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 12 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 13 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 14 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 15 | TER KELAR TV | 98.67% | 100% | 98.67% | 100%
2020-10-05 | 16 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 17 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 18 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 19 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 20 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 21 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 22 | TER KELAR TV | 99.89% | 100% | 99.89% | 100%
2020-10-05 | 23 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-05 | 0 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER MEJILLONES CTM3-TV | 96.44% | 100% | 96.44% | 100%
2020-10-05 | 1 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 2 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 3 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 4 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 5 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 6 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 7 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 8 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 9 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 10 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 11 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 12 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 13 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 14 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 15 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 16 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 17 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 18 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 19 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 20 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 21 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 22 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 23 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-05 | 0 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 1 | TER NEHUENCO II CC1-TV | 96.67% | 100% | 96.67% | 100%
2020-10-05 | 2 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 3 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 4 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 5 | TER NEHUENCO II CC1-TV | 93% | 100% | 93% | 93%
2020-10-05 | 6 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 7 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 8 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 9 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 10 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 13 | TER NEHUENCO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 14 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 1 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 2 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 3 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 4 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 5 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 6 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 7 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 8 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 9 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 10 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 11 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 12 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 13 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 14 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 15 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 16 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 17 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 18 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 19 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 20 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 21 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 22 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 23 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-05 | 0 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 13 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 14 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 15 | TER SAN ISIDRO II CC1-TV | 86.22% | 100% | 86.22% | 86.22%
2020-10-05 | 16 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 17 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 18 | TER SAN ISIDRO II CC1-TV | 87.11% | 100% | 87.11% | 87.11%
2020-10-05 | 19 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 20 | TER SAN ISIDRO II CC1-TV | 94% | 100% | 94% | 94%
2020-10-05 | 21 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 22 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 23 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-05 | 0 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 1 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 2 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 3 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 4 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 5 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 6 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 7 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 8 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 9 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 10 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 11 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 12 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 13 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 14 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 15 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 16 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 17 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 18 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 19 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 20 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 21 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 22 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 23 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-05 | 0 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 1 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 2 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 3 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 4 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 5 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 6 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 7 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 8 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 9 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 10 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 11 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 12 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 13 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 14 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 15 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 16 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 17 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 18 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 19 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 20 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 21 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 22 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 23 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-05 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-05 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-05 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 0 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 12 | HE CANUTILLAR U1 | 99.56% | 100% | 99.56% | 100%
2020-10-06 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-06 | 20 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-06 | 21 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-06 | 2 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-06 | 3 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-06 | 4 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-06 | 5 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-06 | 12 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-06 | 13 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-06 | 14 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-06 | 16 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-06 | 17 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 1 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 2 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 3 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 4 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 5 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 6 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 7 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 8 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 9 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 10 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 11 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 12 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 13 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 14 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 15 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 16 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 17 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 18 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-06 | 19 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-06 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-06 | 2 | HE COLBÚN U1 | 99.89% | 100% | 99.89% | 100%
2020-10-06 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-06 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-06 | 5 | HE COLBÚN U1 | 99.11% | 100% | 99.11% | 100%
2020-10-06 | 6 | HE COLBÚN U1 | 99.67% | 100% | 99.67% | 100%
2020-10-06 | 7 | HE COLBÚN U1 | 98.22% | 100% | 98.22% | 100%
2020-10-06 | 8 | HE COLBÚN U1 | 99.67% | 100% | 99.67% | 100%
2020-10-06 | 9 | HE COLBÚN U1 | 98.22% | 100% | 98.22% | 100%
2020-10-06 | 10 | HE COLBÚN U1 | 99.78% | 100% | 99.78% | 100%
2020-10-06 | 11 | HE COLBÚN U1 | 99.89% | 100% | 99.89% | 100%
2020-10-06 | 12 | HE COLBÚN U1 | 99.44% | 100% | 99.44% | 100%
2020-10-06 | 13 | HE COLBÚN U1 | 99.22% | 100% | 99.22% | 100%
2020-10-06 | 14 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-06 | 15 | HE COLBÚN U1 | 99.56% | 100% | 99.56% | 100%
2020-10-06 | 16 | HE COLBÚN U1 | 99.33% | 100% | 99.33% | 100%
2020-10-06 | 17 | HE COLBÚN U1 | 95.89% | 100% | 95.89% | 100%
2020-10-06 | 18 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-06 | 19 | HE COLBÚN U1 | 95.67% | 100% | 95.67% | 100%
2020-10-06 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-06 | 21 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-06 | 23 | HE COLBÚN U1 | 98.11% | 100% | 98.11% | 100%
2020-10-06 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-06 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-06 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-06 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-06 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-06 | 5 | HE COLBÚN U2 | 99.22% | 100% | 99.22% | 100%
2020-10-06 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-06 | 7 | HE COLBÚN U2 | 98.22% | 100% | 98.22% | 100%
2020-10-06 | 8 | HE COLBÚN U2 | 99.67% | 100% | 99.67% | 100%
2020-10-06 | 9 | HE COLBÚN U2 | 98.56% | 100% | 98.56% | 100%
2020-10-06 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-06 | 11 | HE COLBÚN U2 | 99.89% | 100% | 99.89% | 100%
2020-10-06 | 12 | HE COLBÚN U2 | 99.44% | 100% | 99.44% | 100%
2020-10-06 | 13 | HE COLBÚN U2 | 99.22% | 100% | 99.22% | 100%
2020-10-06 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-06 | 15 | HE COLBÚN U2 | 99.56% | 100% | 99.56% | 100%
2020-10-06 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-06 | 17 | HE COLBÚN U2 | 97.44% | 100% | 97.44% | 100%
2020-10-06 | 18 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-06 | 19 | HE COLBÚN U2 | 99.22% | 100% | 99.22% | 100%
2020-10-06 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-06 | 21 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-06 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-06 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-06 | 0 | HE PEHUENCHE U1 | 98.71% | 100% | 98.71% | 100%
2020-10-06 | 1 | HE PEHUENCHE U1 | 99% | 100% | 99% | 100%
2020-10-06 | 2 | HE PEHUENCHE U1 | 93.78% | 100% | 93.78% | 93.78%
2020-10-06 | 3 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-06 | 4 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-06 | 5 | HE PEHUENCHE U1 | 95.33% | 100% | 95.33% | 100%
2020-10-06 | 6 | HE PEHUENCHE U1 | 98% | 100% | 98% | 100%
2020-10-06 | 7 | HE PEHUENCHE U1 | 98.56% | 100% | 98.56% | 100%
2020-10-06 | 8 | HE PEHUENCHE U1 | 92.89% | 100% | 92.89% | 92.89%
2020-10-06 | 9 | HE PEHUENCHE U1 | 87% | 100% | 87% | 87%
2020-10-06 | 10 | HE PEHUENCHE U1 | 88.44% | 100% | 88.44% | 88.44%
2020-10-06 | 11 | HE PEHUENCHE U1 | 99.44% | 100% | 99.44% | 100%
2020-10-06 | 12 | HE PEHUENCHE U1 | 99.22% | 100% | 99.22% | 100%
2020-10-06 | 13 | HE PEHUENCHE U1 | 94% | 100% | 94% | 94%
2020-10-06 | 14 | HE PEHUENCHE U1 | 98.78% | 100% | 98.78% | 100%
2020-10-06 | 15 | HE PEHUENCHE U1 | 98.22% | 100% | 98.22% | 100%
2020-10-06 | 16 | HE PEHUENCHE U1 | 97% | 100% | 97% | 100%
2020-10-06 | 17 | HE PEHUENCHE U1 | 87.89% | 100% | 87.89% | 87.89%
2020-10-06 | 18 | HE PEHUENCHE U1 | 99.56% | 100% | 99.56% | 100%
2020-10-06 | 19 | HE PEHUENCHE U1 | 82.22% | 100% | 82.22% | 82.22%
2020-10-06 | 20 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-06 | 21 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-06 | 22 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-06 | 23 | HE PEHUENCHE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-06 | 20 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-06 | 21 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-06 | 22 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-06 | 23 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-06 | 0 | HE RALCO U1 | 95.22% | 100% | 95.22% | 100%
2020-10-06 | 1 | HE RALCO U1 | 95% | 100% | 95% | 95%
2020-10-06 | 2 | HE RALCO U1 | 74.22% | 100% | 74.22% | 0%
2020-10-06 | 3 | HE RALCO U1 | 95.11% | 100% | 95.11% | 100%
2020-10-06 | 4 | HE RALCO U1 | 95.89% | 100% | 95.89% | 100%
2020-10-06 | 5 | HE RALCO U1 | 96.11% | 100% | 96.11% | 100%
2020-10-06 | 6 | HE RALCO U1 | 81% | 100% | 81% | 81%
2020-10-06 | 7 | HE RALCO U1 | 94.44% | 100% | 94.44% | 94.44%
2020-10-06 | 8 | HE RALCO U1 | 97.89% | 100% | 97.89% | 100%
2020-10-06 | 9 | HE RALCO U1 | 79.33% | 100% | 79.33% | 79.33%
2020-10-06 | 10 | HE RALCO U1 | 75.78% | 100% | 75.78% | 75.78%
2020-10-06 | 11 | HE RALCO U1 | 99.89% | 100% | 99.89% | 100%
2020-10-06 | 12 | HE RALCO U1 | 99.44% | 100% | 99.44% | 100%
2020-10-06 | 13 | HE RALCO U1 | 95.78% | 100% | 95.78% | 100%
2020-10-06 | 14 | HE RALCO U1 | 86.45% | 100% | 86.45% | 86.45%
2020-10-06 | 15 | HE RALCO U1 | 87% | 100% | 87% | 87%
2020-10-06 | 16 | HE RALCO U1 | 92.78% | 100% | 92.78% | 92.78%
2020-10-06 | 17 | HE RALCO U1 | 86.89% | 100% | 86.89% | 86.89%
2020-10-06 | 18 | HE RALCO U1 | 99.67% | 100% | 99.67% | 100%
2020-10-06 | 19 | HE RALCO U1 | 71.89% | 100% | 71.89% | 0%
2020-10-06 | 20 | HE RALCO U1 | 96.56% | 100% | 96.56% | 100%
2020-10-06 | 21 | HE RALCO U1 | 100% | 100% | 100% | 100%
2020-10-06 | 22 | HE RALCO U1 | 99.56% | 100% | 99.56% | 100%
2020-10-06 | 23 | HE RALCO U1 | 93.89% | 100% | 93.89% | 93.89%
2020-10-06 | 0 | HE RALCO U2 | 96% | 100% | 96% | 100%
2020-10-06 | 1 | HE RALCO U2 | 92.11% | 100% | 92.11% | 92.11%
2020-10-06 | 2 | HE RALCO U2 | 72.89% | 100% | 72.89% | 0%
2020-10-06 | 3 | HE RALCO U2 | 94.78% | 100% | 94.78% | 94.78%
2020-10-06 | 4 | HE RALCO U2 | 94.89% | 100% | 94.89% | 94.89%
2020-10-06 | 5 | HE RALCO U2 | 95.89% | 100% | 95.89% | 100%
2020-10-06 | 6 | HE RALCO U2 | 80% | 100% | 80% | 80%
2020-10-06 | 7 | HE RALCO U2 | 96.56% | 100% | 96.56% | 100%
2020-10-06 | 8 | HE RALCO U2 | 98.56% | 100% | 98.56% | 100%
2020-10-06 | 9 | HE RALCO U2 | 79.89% | 100% | 79.89% | 79.89%
2020-10-06 | 10 | HE RALCO U2 | 76.33% | 100% | 76.33% | 76.33%
2020-10-06 | 11 | HE RALCO U2 | 99.89% | 100% | 99.89% | 100%
2020-10-06 | 12 | HE RALCO U2 | 99.33% | 100% | 99.33% | 100%
2020-10-06 | 13 | HE RALCO U2 | 94.22% | 100% | 94.22% | 94.22%
2020-10-06 | 14 | HE RALCO U2 | 84.11% | 100% | 84.11% | 84.11%
2020-10-06 | 15 | HE RALCO U2 | 87.44% | 100% | 87.44% | 87.44%
2020-10-06 | 16 | HE RALCO U2 | 96.56% | 100% | 96.56% | 100%
2020-10-06 | 17 | HE RALCO U2 | 87.56% | 100% | 87.56% | 87.56%
2020-10-06 | 18 | HE RALCO U2 | 96.78% | 100% | 96.78% | 100%
2020-10-06 | 19 | HE RALCO U2 | 71.11% | 100% | 71.11% | 0%
2020-10-06 | 20 | HE RALCO U2 | 88.89% | 100% | 88.89% | 88.89%
2020-10-06 | 21 | HE RALCO U2 | 100% | 100% | 100% | 100%
2020-10-06 | 22 | HE RALCO U2 | 99.67% | 100% | 99.67% | 100%
2020-10-06 | 23 | HE RALCO U2 | 93.22% | 100% | 93.22% | 93.22%
2020-10-06 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 1 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 2 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 3 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 4 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 5 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 6 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 7 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 8 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 9 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 10 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 11 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 12 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 13 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 14 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 15 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 16 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 17 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 18 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 19 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 20 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 21 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 22 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 23 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-06 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-06 | 10 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-06 | 11 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-06 | 12 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-06 | 13 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-06 | 14 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-06 | 15 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-06 | 16 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-06 | 17 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-06 | 18 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-06 | 19 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER ATACAMA CC2-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-06 | 20 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-06 | 21 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-06 | 22 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-06 | 23 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-06 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-06 | 10 | TER COCHRANE U1 | 100% | 25% | 25% | 0%
2020-10-06 | 11 | TER COCHRANE U1 | No Participó | 0% | 0% | 0%
2020-10-06 | 12 | TER COCHRANE U1 | No Participó | 0% | 0% | 0%
2020-10-06 | 13 | TER COCHRANE U1 | 100% | 78.33% | 78.33% | 78.33%
2020-10-06 | 14 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-06 | 15 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-06 | 16 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-06 | 17 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-06 | 18 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-06 | 19 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-06 | 10 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-06 | 11 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-06 | 12 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-06 | 13 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-06 | 14 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-06 | 15 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-06 | 16 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-06 | 17 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-06 | 18 | TER COCHRANE U2 | 100% | 100% | 100% | 100%
2020-10-06 | 19 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-06 | 2 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-06 | 3 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-06 | 7 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-06 | 8 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-06 | 9 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-06 | 10 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-06 | 19 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-06 | 20 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-06 | 21 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-06 | 23 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-06 | 0 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-06 | 2 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-06 | 3 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-06 | 4 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-06 | 5 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-06 | 6 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-06 | 7 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-06 | 8 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-06 | 9 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-06 | 10 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-06 | 19 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-06 | 20 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-06 | 21 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 6 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 9 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 10 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 11 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 12 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 13 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 14 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 15 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 16 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 17 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 18 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 21 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 22 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 23 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-06 | 0 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-06 | 2 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-06 | 3 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-06 | 4 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-06 | 5 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-06 | 6 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-06 | 7 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-06 | 8 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-06 | 9 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-06 | 10 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-06 | 11 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-06 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-06 | 20 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-06 | 21 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-06 | 2 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-06 | 4 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-06 | 10 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-06 | 11 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-06 | 12 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-06 | 13 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-06 | 14 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-06 | 15 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-06 | 16 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-06 | 18 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-06 | 19 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-06 | 20 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-06 | 21 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER KELAR TV | 94.23% | 100% | 94.23% | 94.23%
2020-10-06 | 1 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-06 | 2 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-06 | 3 | TER KELAR TV | 97.44% | 100% | 97.44% | 100%
2020-10-06 | 4 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-06 | 5 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-06 | 6 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-06 | 7 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-06 | 8 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-06 | 9 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-06 | 10 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-06 | 11 | TER KELAR TV | 100% | 100% | 100% | 100%
2020-10-06 | 12 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-06 | 1 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-06 | 2 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-06 | 3 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-06 | 4 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-06 | 5 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-06 | 6 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-06 | 7 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-06 | 20 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-06 | 21 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-06 | 22 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-06 | 23 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-06 | 0 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 1 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 2 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 3 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 4 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 5 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 6 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 7 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 8 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 9 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 10 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 11 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 12 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 13 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 14 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 15 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 16 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 17 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 18 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 19 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 20 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 21 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 22 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 23 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-06 | 0 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER SAN ISIDRO CC1-TV | 98.65% | 100% | 98.65% | 100%
2020-10-06 | 21 | TER SAN ISIDRO CC1-TV | 100% | 100% | 100% | 100%
2020-10-06 | 22 | TER SAN ISIDRO CC1-TV | 100% | 100% | 100% | 100%
2020-10-06 | 23 | TER SAN ISIDRO CC1-TV | 100% | 100% | 100% | 100%
2020-10-06 | 0 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-06 | 1 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER SAN ISIDRO II CC1-TV | 68.42% | 100% | 68.42% | 0%
2020-10-06 | 8 | TER SAN ISIDRO II CC1-TV | 97.44% | 100% | 97.44% | 100%
2020-10-06 | 9 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-06 | 10 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-06 | 11 | TER SAN ISIDRO II CC1-TV | 98.22% | 100% | 98.22% | 100%
2020-10-06 | 12 | TER SAN ISIDRO II CC1-TV | 97.67% | 100% | 97.67% | 100%
2020-10-06 | 13 | TER SAN ISIDRO II CC1-TV | 87% | 100% | 87% | 87%
2020-10-06 | 14 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-06 | 15 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-06 | 16 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-06 | 17 | TER SAN ISIDRO II CC1-TV | 95.22% | 100% | 95.22% | 100%
2020-10-06 | 18 | TER SAN ISIDRO II CC1-TV | 93.56% | 100% | 93.56% | 93.56%
2020-10-06 | 19 | TER SAN ISIDRO II CC1-TV | 97.33% | 100% | 97.33% | 100%
2020-10-06 | 20 | TER SAN ISIDRO II CC1-TV | 69.11% | 100% | 69.11% | 0%
2020-10-06 | 21 | TER SAN ISIDRO II CC1-TV | 53.44% | 100% | 53.44% | 0%
2020-10-06 | 22 | TER SAN ISIDRO II CC1-TV | 86.67% | 100% | 86.67% | 86.67%
2020-10-06 | 23 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-06 | 0 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 1 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 2 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 3 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 4 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 5 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 6 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 7 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 8 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 9 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 10 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 11 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 12 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 13 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 14 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 15 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 16 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 17 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 18 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 19 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 20 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 21 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 22 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 23 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-06 | 0 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 1 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 2 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 3 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 4 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 5 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 6 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 7 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 8 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 9 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 10 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 11 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 12 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 13 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 14 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 15 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 16 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 17 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 18 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 19 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 20 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 21 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 22 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 23 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-06 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-06 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-06 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 0 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-07 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-07 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-07 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-07 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-07 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-07 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-07 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-07 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-07 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-07 | 11 | HE CANUTILLAR U1 | 99.56% | 100% | 99.56% | 100%
2020-10-07 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-07 | 13 | HE CANUTILLAR U1 | 65.73% | 100% | 65.73% | 0%
2020-10-07 | 14 | HE CANUTILLAR U1 | 80.5% | 100% | 80.5% | 80.5%
2020-10-07 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-07 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-07 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-07 | 18 | HE CANUTILLAR U1 | 99.67% | 100% | 99.67% | 100%
2020-10-07 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-07 | 20 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-07 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-07 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-07 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-07 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-07 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-07 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-07 | 8 | HE CANUTILLAR U2 | 98.89% | 100% | 98.89% | 100%
2020-10-07 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-07 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-07 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-07 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-07 | 13 | HE CANUTILLAR U2 | 94.01% | 100% | 94.01% | 94.01%
2020-10-07 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-07 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-07 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-07 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-07 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-07 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-07 | 20 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-07 | 11 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-07 | 12 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-07 | 13 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-07 | 14 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-07 | 15 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-07 | 16 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-07 | 17 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-07 | 18 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-07 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-07 | 2 | HE COLBÚN U1 | 98.44% | 100% | 98.44% | 100%
2020-10-07 | 3 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-07 | 4 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-07 | 5 | HE COLBÚN U1 | 98.11% | 100% | 98.11% | 100%
2020-10-07 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-07 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-07 | 8 | HE COLBÚN U1 | 97.22% | 100% | 97.22% | 100%
2020-10-07 | 9 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-07 | 10 | HE COLBÚN U1 | 99.89% | 100% | 99.89% | 100%
2020-10-07 | 11 | HE COLBÚN U1 | 99% | 100% | 99% | 100%
2020-10-07 | 12 | HE COLBÚN U1 | 89.22% | 100% | 89.22% | 89.22%
2020-10-07 | 13 | HE COLBÚN U1 | 83.22% | 100% | 83.22% | 83.22%
2020-10-07 | 14 | HE COLBÚN U1 | 98.33% | 100% | 98.33% | 100%
2020-10-07 | 15 | HE COLBÚN U1 | 99.67% | 100% | 99.67% | 100%
2020-10-07 | 16 | HE COLBÚN U1 | 96.89% | 100% | 96.89% | 100%
2020-10-07 | 17 | HE COLBÚN U1 | 99.56% | 100% | 99.56% | 100%
2020-10-07 | 18 | HE COLBÚN U1 | 99.44% | 100% | 99.44% | 100%
2020-10-07 | 19 | HE COLBÚN U1 | 98.44% | 100% | 98.44% | 100%
2020-10-07 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-07 | 21 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-07 | 23 | HE COLBÚN U1 | 99.44% | 100% | 99.44% | 100%
2020-10-07 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 3 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 4 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 5 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 6 | HE COLBÚN U2 | 99% | 100% | 99% | 100%
2020-10-07 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 8 | HE COLBÚN U2 | 99.78% | 100% | 99.78% | 100%
2020-10-07 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 11 | HE COLBÚN U2 | 99.89% | 100% | 99.89% | 100%
2020-10-07 | 12 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 13 | HE COLBÚN U2 | 98.73% | 100% | 98.73% | 100%
2020-10-07 | 14 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 16 | HE COLBÚN U2 | 99.25% | 100% | 99.25% | 100%
2020-10-07 | 17 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 18 | HE COLBÚN U2 | 99.89% | 100% | 99.89% | 100%
2020-10-07 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-07 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 0 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 1 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 2 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 3 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 4 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 5 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 6 | HE PEHUENCHE U1 | 96.11% | 100% | 96.11% | 100%
2020-10-07 | 7 | HE PEHUENCHE U1 | 98.89% | 100% | 98.89% | 100%
2020-10-07 | 8 | HE PEHUENCHE U1 | 92.11% | 100% | 92.11% | 92.11%
2020-10-07 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 10 | HE PEHUENCHE U1 | 90.78% | 100% | 90.78% | 90.78%
2020-10-07 | 11 | HE PEHUENCHE U1 | 91.11% | 100% | 91.11% | 91.11%
2020-10-07 | 12 | HE PEHUENCHE U1 | 97.11% | 100% | 97.11% | 100%
2020-10-07 | 13 | HE PEHUENCHE U1 | 88.67% | 100% | 88.67% | 88.67%
2020-10-07 | 14 | HE PEHUENCHE U1 | 99.67% | 100% | 99.67% | 100%
2020-10-07 | 15 | HE PEHUENCHE U1 | 95.11% | 100% | 95.11% | 100%
2020-10-07 | 16 | HE PEHUENCHE U1 | 91.56% | 100% | 91.56% | 91.56%
2020-10-07 | 17 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 18 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 19 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 20 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 21 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 22 | HE PEHUENCHE U1 | 98.22% | 100% | 98.22% | 100%
2020-10-07 | 23 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 0 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-07 | 9 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-07 | 10 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-07 | 11 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-07 | 12 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-07 | 13 | HE PEHUENCHE U2 | 99.44% | 100% | 99.44% | 100%
2020-10-07 | 14 | HE PEHUENCHE U2 | 98.11% | 100% | 98.11% | 100%
2020-10-07 | 15 | HE PEHUENCHE U2 | 97.89% | 100% | 97.89% | 100%
2020-10-07 | 16 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-07 | 17 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-07 | 18 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-07 | 19 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-07 | 20 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-07 | 21 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-07 | 22 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-07 | 23 | HE PEHUENCHE U2 | 98.44% | 100% | 98.44% | 100%
2020-10-07 | 0 | HE RALCO U1 | 78.56% | 100% | 78.56% | 78.56%
2020-10-07 | 1 | HE RALCO U1 | 100% | 100% | 100% | 100%
2020-10-07 | 2 | HE RALCO U1 | 96.44% | 100% | 96.44% | 100%
2020-10-07 | 3 | HE RALCO U1 | 90.67% | 100% | 90.67% | 90.67%
2020-10-07 | 4 | HE RALCO U1 | 93.56% | 100% | 93.56% | 93.56%
2020-10-07 | 5 | HE RALCO U1 | 77.89% | 100% | 77.89% | 77.89%
2020-10-07 | 6 | HE RALCO U1 | 90.22% | 100% | 90.22% | 90.22%
2020-10-07 | 7 | HE RALCO U1 | 99.89% | 100% | 99.89% | 100%
2020-10-07 | 8 | HE RALCO U1 | 81.22% | 100% | 81.22% | 81.22%
2020-10-07 | 9 | HE RALCO U1 | 100% | 100% | 100% | 100%
2020-10-07 | 10 | HE RALCO U1 | 90.67% | 100% | 90.67% | 90.67%
2020-10-07 | 11 | HE RALCO U1 | 92.44% | 100% | 92.44% | 92.44%
2020-10-07 | 12 | HE RALCO U1 | 85.56% | 100% | 85.56% | 85.56%
2020-10-07 | 13 | HE RALCO U1 | 73% | 100% | 73% | 0%
2020-10-07 | 14 | HE RALCO U1 | 92.22% | 100% | 92.22% | 92.22%
2020-10-07 | 15 | HE RALCO U1 | 78.67% | 100% | 78.67% | 78.67%
2020-10-07 | 16 | HE RALCO U1 | 81.67% | 100% | 81.67% | 81.67%
2020-10-07 | 17 | HE RALCO U1 | 95.33% | 100% | 95.33% | 100%
2020-10-07 | 18 | HE RALCO U1 | 97.89% | 100% | 97.89% | 100%
2020-10-07 | 19 | HE RALCO U1 | 94.89% | 100% | 94.89% | 94.89%
2020-10-07 | 20 | HE RALCO U1 | 95.44% | 100% | 95.44% | 100%
2020-10-07 | 21 | HE RALCO U1 | 90.89% | 100% | 90.89% | 90.89%
2020-10-07 | 22 | HE RALCO U1 | 94.44% | 100% | 94.44% | 94.44%
2020-10-07 | 23 | HE RALCO U1 | 91.44% | 100% | 91.44% | 91.44%
2020-10-07 | 0 | HE RALCO U2 | 73.11% | 100% | 73.11% | 0%
2020-10-07 | 1 | HE RALCO U2 | 98.44% | 100% | 98.44% | 100%
2020-10-07 | 2 | HE RALCO U2 | 93.44% | 100% | 93.44% | 93.44%
2020-10-07 | 3 | HE RALCO U2 | 87.56% | 100% | 87.56% | 87.56%
2020-10-07 | 4 | HE RALCO U2 | 96.78% | 100% | 96.78% | 100%
2020-10-07 | 5 | HE RALCO U2 | 70.56% | 100% | 70.56% | 0%
2020-10-07 | 6 | HE RALCO U2 | 94.22% | 100% | 94.22% | 94.22%
2020-10-07 | 7 | HE RALCO U2 | 96.89% | 100% | 96.89% | 100%
2020-10-07 | 8 | HE RALCO U2 | 81% | 100% | 81% | 81%
2020-10-07 | 9 | HE RALCO U2 | 99.11% | 100% | 99.11% | 100%
2020-10-07 | 10 | HE RALCO U2 | 90.67% | 100% | 90.67% | 90.67%
2020-10-07 | 11 | HE RALCO U2 | 92.44% | 100% | 92.44% | 92.44%
2020-10-07 | 12 | HE RALCO U2 | 78.22% | 100% | 78.22% | 78.22%
2020-10-07 | 13 | HE RALCO U2 | 71.33% | 100% | 71.33% | 0%
2020-10-07 | 14 | HE RALCO U2 | 92.44% | 100% | 92.44% | 92.44%
2020-10-07 | 15 | HE RALCO U2 | 75.56% | 100% | 75.56% | 75.56%
2020-10-07 | 16 | HE RALCO U2 | 78.56% | 100% | 78.56% | 78.56%
2020-10-07 | 17 | HE RALCO U2 | 95.67% | 100% | 95.67% | 100%
2020-10-07 | 18 | HE RALCO U2 | 96.44% | 100% | 96.44% | 100%
2020-10-07 | 19 | HE RALCO U2 | 92.89% | 100% | 92.89% | 92.89%
2020-10-07 | 20 | HE RALCO U2 | 81.88% | 100% | 81.88% | 81.88%
2020-10-07 | 21 | HE RALCO U2 | 90.44% | 100% | 90.44% | 90.44%
2020-10-07 | 22 | HE RALCO U2 | 96% | 100% | 96% | 100%
2020-10-07 | 23 | HE RALCO U2 | 94.56% | 100% | 94.56% | 94.56%
2020-10-07 | 0 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | HE RAPEL U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | HE RAPEL U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | HE RAPEL U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | HE RAPEL U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | HE RAPEL U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 1 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 2 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 3 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 4 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 5 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 6 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 7 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 8 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 9 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 10 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 11 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 12 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 13 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 14 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 15 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 16 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 17 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 18 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 19 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 20 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 21 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 22 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 23 | PFV LUZ DEL NORTE | No Participó | 0% | 0% | 0%
2020-10-07 | 0 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER ANGAMOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-07 | 10 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-07 | 11 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-07 | 12 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-07 | 13 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-07 | 14 | TER ANGAMOS U2 | 99% | 100% | 99% | 100%
2020-10-07 | 15 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-07 | 16 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-07 | 17 | TER ANGAMOS U2 | 95.78% | 100% | 95.78% | 100%
2020-10-07 | 18 | TER ANGAMOS U2 | 100% | 100% | 100% | 100%
2020-10-07 | 19 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER ANGAMOS U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER ANTILHUE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER ANTILHUE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER ATACAMA CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER ATACAMA CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER ATACAMA CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER ATACAMA CC2-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER ATACAMA CC2-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 1 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 2 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 3 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 4 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 5 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 6 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 7 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 8 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 9 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 10 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 11 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 12 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 13 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 14 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 15 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 16 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 17 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 18 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 19 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 20 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 21 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 22 | TER ATACAMA CC2-TV | 100% | 100% | 100% | 100%
2020-10-07 | 23 | TER ATACAMA CC2-TV | 99.03% | 100% | 99.03% | 100%
2020-10-07 | 0 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER CANDELARIA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER CANDELARIA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 9 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 10 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 11 | TER COCHRANE U1 | 99.33% | 100% | 99.33% | 100%
2020-10-07 | 12 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 13 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 14 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 15 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 16 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 17 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 18 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 19 | TER COCHRANE U1 | 100% | 100% | 100% | 100%
2020-10-07 | 20 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER COCHRANE U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER COCHRANE U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER COCHRANE U2 | No Participó | 21.67% | 21.67% | 0%
2020-10-07 | 9 | TER COCHRANE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 10 | TER COCHRANE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 11 | TER COCHRANE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 12 | TER COCHRANE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 13 | TER COCHRANE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 14 | TER COCHRANE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 15 | TER COCHRANE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 16 | TER COCHRANE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 17 | TER COCHRANE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 18 | TER COCHRANE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 19 | TER COCHRANE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 20 | TER COCHRANE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 21 | TER COCHRANE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 22 | TER COCHRANE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 23 | TER COCHRANE U2 | No Participó | 0% | 0% | 0%
2020-10-07 | 0 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-07 | 1 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-07 | 2 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-07 | 3 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-07 | 4 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-07 | 5 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-07 | 6 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-07 | 7 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-07 | 8 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-07 | 9 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-07 | 10 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-07 | 19 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-07 | 20 | TER GUACOLDA U1 | 100% | 100% | 100% | 100%
2020-10-07 | 21 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER GUACOLDA U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-07 | 9 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-07 | 10 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-07 | 20 | TER GUACOLDA U2 | 100% | 100% | 100% | 100%
2020-10-07 | 21 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER GUACOLDA U2 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-07 | 1 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-07 | 2 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-07 | 3 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-07 | 4 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-07 | 5 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-07 | 6 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-07 | 7 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-07 | 8 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER GUACOLDA U3 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-07 | 20 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-07 | 21 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-07 | 22 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-07 | 23 | TER GUACOLDA U3 | 100% | 100% | 100% | 100%
2020-10-07 | 0 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-07 | 9 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-07 | 10 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-07 | 11 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-07 | 12 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-07 | 19 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-07 | 20 | TER GUACOLDA U4 | 100% | 100% | 100% | 100%
2020-10-07 | 21 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER GUACOLDA U4 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER GUACOLDA U5 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-07 | 10 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-07 | 11 | TER GUACOLDA U5 | 96.27% | 100% | 96.27% | 100%
2020-10-07 | 12 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-07 | 13 | TER GUACOLDA U5 | 97.56% | 100% | 97.56% | 100%
2020-10-07 | 14 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-07 | 15 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-07 | 16 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-07 | 17 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-07 | 18 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-07 | 19 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-07 | 20 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-07 | 21 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-07 | 22 | TER GUACOLDA U5 | 100% | 100% | 100% | 100%
2020-10-07 | 23 | TER GUACOLDA U5 | 98.56% | 100% | 98.56% | 100%
2020-10-07 | 0 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER KELAR CC1-TG1 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER KELAR CC1-TG2 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER KELAR TV | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER LOS VIENTOS U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER MEJILLONES CTM3-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-07 | 1 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-07 | 2 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-07 | 3 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-07 | 4 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-07 | 5 | TER MEJILLONES CTM3-TV | 98.67% | 100% | 98.67% | 100%
2020-10-07 | 6 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-07 | 7 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER MEJILLONES CTM3-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER MEJILLONES CTM3-TV | 75.22% | 100% | 75.22% | 75.22%
2020-10-07 | 22 | TER MEJILLONES CTM3-TV | 80.89% | 100% | 80.89% | 80.89%
2020-10-07 | 23 | TER MEJILLONES CTM3-TV | 100% | 100% | 100% | 100%
2020-10-07 | 0 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER NEHUENCO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER NEHUENCO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 1 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 2 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 3 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 4 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 5 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 6 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 7 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 8 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 9 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 10 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 11 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 12 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 13 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 14 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 15 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 16 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 17 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 18 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 19 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 20 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 21 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 22 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 23 | TER NUEVA RENCA CC1-TG | No Participó | 0% | 0% | 0%
2020-10-07 | 0 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER SAN ISIDRO CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER SAN ISIDRO CC1-TV | 100% | 100% | 100% | 100%
2020-10-07 | 1 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER SAN ISIDRO CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER SAN ISIDRO CC1-TV | 100% | 100% | 100% | 100%
2020-10-07 | 21 | TER SAN ISIDRO CC1-TV | 100% | 100% | 100% | 100%
2020-10-07 | 22 | TER SAN ISIDRO CC1-TV | 100% | 100% | 100% | 100%
2020-10-07 | 23 | TER SAN ISIDRO CC1-TV | 100% | 100% | 100% | 100%
2020-10-07 | 0 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER SAN ISIDRO II CC1-TG | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-07 | 1 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-07 | 7 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-07 | 8 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-07 | 9 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-07 | 10 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-07 | 11 | TER SAN ISIDRO II CC1-TV | 89.78% | 100% | 89.78% | 89.78%
2020-10-07 | 12 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-07 | 13 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER SAN ISIDRO II CC1-TV | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-07 | 17 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-07 | 18 | TER SAN ISIDRO II CC1-TV | 91.3% | 100% | 91.3% | 91.3%
2020-10-07 | 19 | TER SAN ISIDRO II CC1-TV | 100% | 100% | 100% | 100%
2020-10-07 | 20 | TER SAN ISIDRO II CC1-TV | 68.22% | 100% | 68.22% | 0%
2020-10-07 | 21 | TER SAN ISIDRO II CC1-TV | 51.33% | 100% | 51.33% | 0%
2020-10-07 | 22 | TER SAN ISIDRO II CC1-TV | 98.11% | 100% | 98.11% | 100%
2020-10-07 | 23 | TER SAN ISIDRO II CC1-TV | 91% | 100% | 91% | 91%
2020-10-07 | 0 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 1 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 2 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 3 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 4 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 5 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 6 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 7 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 8 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 9 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 10 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 11 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 12 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 13 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 14 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 15 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 16 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 17 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 18 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 19 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 20 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 21 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 22 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 23 | TER TER NEHUENCO 9B U1 | No Participó | 100% | 100% | 100%
2020-10-07 | 0 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 1 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 2 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 3 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 4 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 5 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 6 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 7 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 8 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 9 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 10 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 11 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 12 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 13 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 14 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 15 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 16 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 17 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 18 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 19 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 20 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 21 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 22 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 23 | TER TOCOPILLA TG3 | No Participó | 0% | 0% | 0%
2020-10-07 | 0 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 1 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 2 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 3 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 4 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 5 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 6 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 7 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 8 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 9 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 10 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 11 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 12 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 13 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 14 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 15 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 16 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 17 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 18 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 19 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 20 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 21 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 22 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 23 | TER TOCOPILLA U14 | No Participó | 0% | 0% | 0%
2020-10-07 | 0 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 1 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 2 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 3 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 4 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 5 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 6 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 7 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 8 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 9 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 10 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 11 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 12 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 13 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 14 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 15 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 16 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 17 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 18 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 19 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 20 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 21 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 22 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-07 | 23 | TER TOCOPILLA U16-TG-TV | No Participó | 0% | 0% | 0%
2020-10-08 | 0 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 1 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 2 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 3 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 4 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 5 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 6 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 7 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 8 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 9 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 10 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 11 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 12 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 13 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 14 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 15 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 16 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 17 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 18 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 19 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 20 | HE CANUTILLAR U1 | 100% | 100% | 100% | 100%
2020-10-08 | 21 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 22 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 23 | HE CANUTILLAR U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 0 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 1 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 2 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 3 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 4 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 5 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 6 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 7 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 8 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 9 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 10 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 11 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 12 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 13 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 14 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 15 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 16 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 17 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 18 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 19 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 20 | HE CANUTILLAR U2 | 100% | 100% | 100% | 100%
2020-10-08 | 21 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 22 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 23 | HE CANUTILLAR U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 0 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 1 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 2 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 3 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-08 | 4 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-08 | 5 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-08 | 6 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-08 | 7 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 8 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 9 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-08 | 10 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-08 | 11 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-08 | 12 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-08 | 13 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-08 | 14 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-08 | 15 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-08 | 16 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-08 | 17 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-08 | 18 | HE CIPRESES U1 | 100% | 100% | 100% | 100%
2020-10-08 | 19 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 20 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 21 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 22 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 23 | HE CIPRESES U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 0 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 1 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 2 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 3 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 4 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 5 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 6 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 7 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 8 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 9 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 10 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 11 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 12 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 13 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 14 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 15 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 16 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 17 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 18 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 19 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 20 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 21 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 22 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 23 | HE CIPRESES U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 0 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 1 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 2 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 3 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-08 | 4 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-08 | 5 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-08 | 6 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-08 | 7 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-08 | 8 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-08 | 9 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-08 | 10 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-08 | 11 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-08 | 12 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-08 | 13 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-08 | 14 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-08 | 15 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-08 | 16 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-08 | 17 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-08 | 18 | HE CIPRESES U3 | 100% | 100% | 100% | 100%
2020-10-08 | 19 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 20 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 21 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 22 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 23 | HE CIPRESES U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 0 | HE COLBÚN U1 | 99.33% | 100% | 99.33% | 100%
2020-10-08 | 1 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-08 | 2 | HE COLBÚN U1 | 99.77% | 100% | 99.77% | 100%
2020-10-08 | 3 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 4 | HE COLBÚN U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 5 | HE COLBÚN U1 | 98.95% | 100% | 98.95% | 100%
2020-10-08 | 6 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-08 | 7 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-08 | 8 | HE COLBÚN U1 | 99.33% | 100% | 99.33% | 100%
2020-10-08 | 9 | HE COLBÚN U1 | 98.44% | 100% | 98.44% | 100%
2020-10-08 | 10 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-08 | 11 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-08 | 12 | HE COLBÚN U1 | 99.33% | 100% | 99.33% | 100%
2020-10-08 | 13 | HE COLBÚN U1 | 99.89% | 100% | 99.89% | 100%
2020-10-08 | 14 | HE COLBÚN U1 | 98.11% | 100% | 98.11% | 100%
2020-10-08 | 15 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-08 | 16 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-08 | 17 | HE COLBÚN U1 | 99.78% | 100% | 99.78% | 100%
2020-10-08 | 18 | HE COLBÚN U1 | 99.11% | 100% | 99.11% | 100%
2020-10-08 | 19 | HE COLBÚN U1 | 98.78% | 100% | 98.78% | 100%
2020-10-08 | 20 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-08 | 21 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-08 | 22 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-08 | 23 | HE COLBÚN U1 | 100% | 100% | 100% | 100%
2020-10-08 | 0 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-08 | 1 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-08 | 2 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-08 | 3 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 4 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 5 | HE COLBÚN U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 6 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-08 | 7 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-08 | 8 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-08 | 9 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-08 | 10 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-08 | 11 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-08 | 12 | HE COLBÚN U2 | 99.89% | 100% | 99.89% | 100%
2020-10-08 | 13 | HE COLBÚN U2 | 99.78% | 100% | 99.78% | 100%
2020-10-08 | 14 | HE COLBÚN U2 | 98.11% | 100% | 98.11% | 100%
2020-10-08 | 15 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-08 | 16 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-08 | 17 | HE COLBÚN U2 | 99.78% | 100% | 99.78% | 100%
2020-10-08 | 18 | HE COLBÚN U2 | 99.11% | 100% | 99.11% | 100%
2020-10-08 | 19 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-08 | 20 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-08 | 21 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-08 | 22 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-08 | 23 | HE COLBÚN U2 | 100% | 100% | 100% | 100%
2020-10-08 | 0 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 1 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 2 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 3 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 4 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 5 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 6 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 7 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 8 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 9 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 10 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 11 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 12 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 13 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 14 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 15 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 16 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 17 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 18 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 19 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 20 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 21 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 22 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 23 | HE EL TORO U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 0 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 1 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 2 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 3 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 4 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 5 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 6 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 7 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 8 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 9 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 10 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 11 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 12 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 13 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 14 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 15 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 16 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 17 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 18 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 19 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 20 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 21 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 22 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 23 | HE EL TORO U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 0 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 1 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 2 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 3 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 4 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 5 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 6 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 7 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 8 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 9 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 10 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 11 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 12 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 13 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 14 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 15 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 16 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 17 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 18 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 19 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 20 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 21 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 22 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 23 | HE EL TORO U3 | No Participó | 100% | 100% | 100%
2020-10-08 | 0 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 1 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 2 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 3 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 4 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 5 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 6 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 7 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 8 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 9 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 10 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 11 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 12 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 13 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 14 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 15 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 16 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 17 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 18 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 19 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 20 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 21 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 22 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 23 | HE EL TORO U4 | No Participó | 100% | 100% | 100%
2020-10-08 | 0 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 1 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 2 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 3 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 4 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 5 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 6 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 7 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 8 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 9 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 10 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 11 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 12 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 13 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 14 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 15 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 16 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 17 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 18 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 19 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 20 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 21 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 22 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 23 | HE PANGUE U1 | No Participó | 100% | 100% | 100%
2020-10-08 | 0 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 1 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 2 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 3 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 4 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 5 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 6 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 7 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 8 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 9 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 10 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 11 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 12 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 13 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 14 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 15 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 16 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 17 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 18 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 19 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 20 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 21 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 22 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 23 | HE PANGUE U2 | No Participó | 0% | 0% | 0%
2020-10-08 | 0 | HE PEHUENCHE U1 | 95.89% | 100% | 95.89% | 100%
2020-10-08 | 1 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-08 | 2 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-08 | 3 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-08 | 4 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-08 | 5 | HE PEHUENCHE U1 | 99.56% | 100% | 99.56% | 100%
2020-10-08 | 6 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-08 | 7 | HE PEHUENCHE U1 | 98.22% | 100% | 98.22% | 100%
2020-10-08 | 8 | HE PEHUENCHE U1 | 92.89% | 100% | 92.89% | 92.89%
2020-10-08 | 9 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-08 | 10 | HE PEHUENCHE U1 | 97.67% | 100% | 97.67% | 100%
2020-10-08 | 11 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-08 | 12 | HE PEHUENCHE U1 | 95.22% | 100% | 95.22% | 100%
2020-10-08 | 13 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-08 | 14 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-08 | 15 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-08 | 16 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-08 | 17 | HE PEHUENCHE U1 | 99.11% | 100% | 99.11% | 100%
2020-10-08 | 18 | HE PEHUENCHE U1 | 98% | 100% | 98% | 100%
2020-10-08 | 19 | HE PEHUENCHE U1 | 89.89% | 100% | 89.89% | 89.89%
2020-10-08 | 20 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-08 | 21 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-08 | 22 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-08 | 23 | HE PEHUENCHE U1 | 100% | 100% | 100% | 100%
2020-10-08 | 0 | HE PEHUENCHE U2 | 96.78% | 100% | 96.78% | 100%
2020-10-08 | 1 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-08 | 2 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-08 | 3 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-08 | 4 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-08 | 5 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-08 | 6 | HE PEHUENCHE U2 | No Participó | 100% | 100% | 100%
2020-10-08 | 7 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-08 | 8 | HE PEHUENCHE U2 | 87.33% | 100% | 87.33% | 87.33%
2020-10-08 | 9 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-08 | 10 | HE PEHUENCHE U2 | 98.33% | 100% | 98.33% | 100%
2020-10-08 | 11 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-08 | 12 | HE PEHUENCHE U2 | 93.78% | 100% | 93.78% | 93.78%
2020-10-08 | 13 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-08 | 14 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-08 | 15 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-08 | 16 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-08 | 17 | HE PEHUENCHE U2 | 99.56% | 100% | 99.56% | 100%
2020-10-08 | 18 | HE PEHUENCHE U2 | 99.67% | 100% | 99.67% | 100%
2020-10-08 | 19 | HE PEHUENCHE U2 | 86.33% | 100% | 86.33% | 86.33%
2020-10-08 | 20 | HE PEHUENCHE U2 | 100% | 100% | 100% | 100%
2020-10-08 | 21 | HE PEHUENCHE U2 | 99.78% | 100% | 99.78% | 100%
2020-10-08 | 22 | HE PEHUENCHE U2 | 99.33% | 100% | 99.33% | 100%